Hydro & Water

Duvha Power Station Water Use License Application

Ref. no: SWPS/037/03

AUTHOR:		    _________________________

NALINI NAIDOO

STRATEGIC WATER PLANNING CHEMIST

SUPPORTED BY:  ________________________

Heine Hoffman

Strategic Water Planning Manager

# CONTENTS

## PART 1	BACKGROUND INFORMATION

  - General information								3

  - Description of Project								4

## PART 2	DESCRIPTION OF THE WATER ENVIRONMENT

(Information by Professor Frank Hodgson from the F S University IGWS)

  - Climate									11

  - Topography									16

  - Geology									17

  - Surface Water									18

  - Groundwater									19

## PART 3	WATER MANAGEMENT

  - Industrial water use and process description					26

  - Groundwater management							53

- References									74

- Appendix:

A:   Groundwater Report							75

B:   Ash Dam Report								76

C:  Scenario Planning using Saltman Spreadsheet				77

D:  Water Use License Application Forms					86

### PART 1:	BACKGROUND INFORMATION

  - General Information

1.1.1 Holding Authority	:	Eskom	(PTY) LTD		P.O. Box 1091

Megawatt Park	Johannesburg

Maxwell Drive	2000

Sunninghill

Contact person:	Heine Hoffman

(011) 800 3713

Applicant		:	Duvha Power Station

Contact Person	:	Johan Prinsloo

(013) 6900240

Site 			:	Duvha Power Station

    - Magisterial district & authority:

Witbank, Emahleni Town Council

    - Nearest Towns:

Witbank – 20 km north west of the power station

Middelburg – 25km north east of the power station

    - Surface Infrastructure:

Duvha Power Station is situated approximately 20 kilometres south east of the town Witbank in the province Mpumalanga on the farm originally known as Speekfontein.

    - Latitude & longitude:

25,9°S & 29,3°E

    - Ownership of land:

Duvha Power Station is located on the farm Speekfontein 336JS with approximately 581 ha currently developed by Eskom. Title deed number CCT10033/1978.

    - Ownership of adjacent (potentially impacted) land:

| Property Name | Property Number | Owner |
| --- | --- | --- |
| Farmers: |  |  |
| Neels Van Dyk | Remainder of Portion 3, Rhenosterfontein No. 318-JS | Neels Van Dyk |
|  | Portion 11, Rhenosterfontein No. 318-JS | Neels Van Dyk |
|  | Portion 2 Speekfontein No. 336-JS | Duvha Power Station |
| Nico Gouws | Portion 1 Duvha Power Station No. 337-JS | Nico Gouws |
|  | Portion 15,16 Speekfontein No. 336-JS | Nico Gouws |
|  | Portion 9,10 Driefontein No. 338-JS | Nico Gouws |
| Industry: |  |  |
| Corobrik | Portion 3, Duvha Power Station No. 337-JS | Corobrik |
| Middelburg Mine South | Portion 1, Driefontein No. 338-JS | Middelburg Mine South |
|  | Portion 2, Duvha Power Station No. 337-JS | Middelburg Mine South |
|  | Remainder Portion 4,12, 13. Portion 29,30,7 Speekfontein No. 336-JS | Middelburg Mine South |

    - Land zoning

Apart from the power station is the area mainly agricultural land and mining  area.

    - River catchment:

Duvha Power Station is situated in the Olifants River Catchment  upstream of the Witbank Dam.

1.2	Description of project

1.2.1	Type of industry and products produced:

Duvha Power Station is a coal-fired power station, producing electricity into the national grid.

    - Amount of electricity produced annually:

Nominal capacity – 21 383 GWh planned for 2003.

    - Raw materials:

Coal consumption: Planned for 2003 – 10 073 000t per annum

Water consumption: Projected raw water demand for 2003 – 49 235 Ml

1.2.4	Water intensive processes:

a)	Water purification plant

Duvha Power Station’s raw water requirement can be met from either of two sources.  First, water can be pumped from the Vygeboom and Nooitgedacht dams in the eastern part of the Mpumalanga, which are fed by the Komati River.  These dams can also be supplied with water from the Usutu system.  Secondly, water can be obtained from the Witbank Dam in the upper reaches of the Olifants River and supplemented with water from the Grootdraai Dam in the Vaal River near Standerton.

The raw water is pumped into the raw water reservoirs which then splits into three major lines: the cooling water south system, the cooling water north system and the water treatment plant (to the raw water clarifiers).  The clarified water is then used for demineralisation and potable water production.

Potable water is produced to satisfy the station and third party needs.  The third parties are Ikageng, Duvha Opencast Mine and Sannieshof single accommodation facility.  This means that the power station is classified as a Water Services Provider in terms of the Water Services Act (Act No. 108 of 1997).  Disinfecting with chlorine, caustic soda (NaOH) for pH adjusting.

Demineralised water is produced using the Ion Exchange technique.  The plant consists of three sets of ion exchangers with each set comprising a cation, weak base anion, strong base anion and mixed bed unit.  The demin plant is designed to produce 200 m3 per unit.  The resins used in the demineralisation plant are regenerated upon exhaustion.  This is only done when required.

b)	Steam and water cycle to generate electricity

Six turbo-generators, which are steam driven, are used to generate electricity at Duvha Power Station.  The steam is produced in the six boilers which are of the Benson type, which depends on forced circulation and has no steam drum.  The feedwater, which is highly purified and demineralised, makes one continuous and uninterrupted circuit through the boiler, the turbine, and the condenser and again through the boiler.  On its path through the boiler, the feedwater evaporated and as more heat is absorbed, the steam becomes superheated to a temperature of 540 oC and a pressure of 17,1 mPa.

A feature of the steam pipework is a high-pressure system that allows the superheated steam to bypass the high-pressure turbine when necessary, to flow directly into the reheat pipework.  From there it bypasses the intermediate-pressure and low-pressure turbines and flows into the main condenser.  This system means that the boiler can be operated independently of the turbine and the correct steam temperature and pressure can be obtained before the generator is started up.  Also, if a turbine trips, the system allows the boiler to be operated at roughly 40 per cent of its maximum load, it can be run at a low load while the boiler is maintained at a higher load.  In both instances, the bypass system prevents, within the limits of its capacity, sudden pressure rises from exceeding the settings of the safety valves in the reheater.

Each boiler is fitted with twenty-four burners, arranged in twelve rows of two-six rows in the front wall of the furnace and six rows in its rear wall.  Each coal mill supplies four burners – two in the front wall and two in the rear wall.  Mounted in the centre of each burner is an oil burner and these are used for starting up and for stabilising the combustion coal at low loads.

Forced-draught fans supply secondary air to the burner wind boxes while primary-air fans transport pulverised coals from the mills to the burners.  Combustion gases are drawn from the furnace by two induced-draught fans, over the surfaces of the steam superheaters, the reheaters, and the economiser and air preheaters, through the electrostatic precipitators and into the chimney.

Each boiler has a capacity of 507 kg/s of steam and the feedwater is supplied, at a pressure of 22 Mpa, by two electric pumps rated at 13 MW each, or by one steam-driven pump.  At maximum continuous rating the efficiency of the boilers is 93,9 percent.

c)	Main cooling water system

The main cooling system condenses the Low-Pressure exhaust steam into the condenser.  This clean condensate gets circulated back to the boiler.

The condensate temperature in the condenser hotwell is about 37 oC.  In order to obtain maximum system efficiency it is necessary to reheat the condensate before returning it to the boiler.  To achieve this, the condensate is passed through numerous heaters before feeding it into the boiler.  All the heaters are of the surface type in which the water flows through tube nests.  Steam extracted from different stages of the turbine heats the water by conduction through the tube metal.

A deaerator situated between the low-pressure and high-pressure heaters removes entrained oxygen in the condensates and heats the water through direct contact with steam extracted from the turbines.  The condensate is pumped from the condenser to the deaerator through low-pressure heaters by means of the main condensate extraction pumps.

The condensate is then pumped from the deaerator feedwater tank to the boiler through the high-pressure heaters by the boiler feed pumps.  The final feedwater temperature at 600 MW is 247 oC.

The condensers are of the dual-pressure surface type.  The vacuum inside the condensers is established by steam-jet air ejectors and maintained in normal operation by water-jet air ejectors.  The steam exhausted from the low-pressure cylinder condenses over 22 552 brass tubes, which have a surface area totalling 23 400 m2.  Each boiler-turbine set has a condenser with a heat exchange capacity of approximately 400 MW.

The six cooling towers at Duvha are designed for a total thermal load of nearly 19 000 GJ/h.  The three large towers are 149m high and 114m in diameter at the base and the minimum shell thickness is 180 mm.  At full load the evaporation from one-tower amounts to 30 Ml a day.

Cooling water treatment and specific the option employed to de-alkalinise the cooling water is an important decision if Zero Liquid Effluent Discharge (ZLED) is to be maintained at all times. Alkalinity control with acid is a neutralisation process and contributes to the salt load of the cooling water. Lime alkalinity control is a precipitation process and very little inorganic contamination of the cooling water takes place during the process.

Lime alkalinity control is therefore the preferred option of cooling water

treatment and these lime systems are managed such as to maintain it as close 			as possible to  100% availability.

d)	Ash plant and ash dams

At full load each boiler produces 250 tons of coarse ash and 1400 tons of fly ash every day.  The coarse ash and the material rejected from the mills are crushed and fed into sumps, from where it is pumped to the ash dam.  The fly ash sluiced from the precipitator hoppers is pumped separately to the ash dam, where it is used to build ash dam walls.

Water from the dam, which covers an area of 450 ha, is decanted and reused in the ash system in a closed loop.

The concentration of the hydroxides in the ash water is of crucial importance if the ash water sulphate concentration is to be substantially lowered in the ash dump. High concentrations of hydroxides in the ash water will increase the solubility of aluminium from the ash, this will lead to the formation of aluminium hydroxide, as the solubility of Al (OH)3 increases with increase in pH (hydroxides). This causes an insoluble salt known as ettringite (3CaO.3CaSO4.Al2O3.31H2O) to precipitate, thereby removing some calcium and sulphate from the solution.  The stoichiometry is given by the following reaction.

6Ca2+ + 3SO42- + 2Al(OH)3 + 37H2O (  3CaO.3CaSO4.Al2O3.31H2O + 6H3O+

The formation of ettringite is pH dependant, the optimum [OH-] Concentrate lying between 600 and 1200. Sodium could depress the solubility of ettringite but sulphates could generally be lowered to approximately 450 mgkg-1 as SO4. The result of this is that this water is then suitable for reuse in the cooling water system.

e).  Station drains complex

All drains are diverted to this system.  These drains collect water from following systems:

- cooling water systems

- storm water within the station and terrace

- drainage of boilers and condensers

The oil separation system is a tilted weir separation system. Any spilled oil is retained in the oil ponds. An overflow weir system allows for the cascading of contaminated drains to the oil separation system.  Oil absorbent pillows and booms are kept as a stock item in the stores.

The water quality is therefore always equal or better than the cooling water systems quality requirement and the water is then recovered back into the main cooling water system.

g)	Sewage treatment

There were two sewage plants, one at Ikageng Quarters and the other at Sannieshof single accommodation, which were integrated in December 2001 with a pipeline. The plant was contracted out to a contractor in November 1999.

The sewage is treated using an activated sludge process.  Treated Sewage will conform to the stipulated requirements for Phosphate, Nitrate and Chemical Oxygen Demand.  Sewage is recovered from the following Parties:

- The Power Station

- Ikageng Quarters

This sewage will be treated and recovered from Ikageng to the high-level ash dam system within the station.

h).  Mine Water Recovery

The Komati Water Scheme is currently under stress to supply the required demand of water to the power stations.  The situations lends itself to the controlled usage of polluted mine water for ashing purposes at Duvha Power Station.

i.  Recovery and treatment

Should any parameter in the mine water exceed the specified threshold for cooling water then the mine water will be treated as a separate stream. Evaluation of the mine water chemistry should also include permanent hardness and specific permanent hardness following lime treatment.

The preconditions for recovery of mine water are:

- That the mine water must not be acidic

- The mine water must be introduced into the ashing system

- Must be a controlled process, which will ensure sufficient freeboard in

the ashing system in the case of a storm.

Lime softening must be the only option for cooling water alkalinity control in order to maximise mine water utilisation.  The chemical dynamics within the ash water system are such that the sulphates from the mine water will be lowered through the natural precipitation of sulphate as ettringite.  This will render the mine water i.e. controlled volumes, suitable for recovery to the cooling water system.

ii.  Identification of environmental impacts

Resource saving

Using polluted mine water for power generation makes pristine river water available for human consumption. It further prevents this polluted water from entering the water environment.

Salt load to the disposed ash

Eskom even though exceeding the demand at this stage regards power station ash as a resource. The disposal of excessive volumes of high salinity brine can compromise the resource value of the ash. Ground water quality could be compromised if the field capacity of the ash is exceeded

The possible pollution of the ground water with the so-called ash variables is a reality. A strategically placed ground water monitoring borehole is monitored for telltale parameters.  Results are managed in accordance with the Department of Water Affairs and Forestry minimum requirements for ground water monitoring and are available in the C:\Wish database.

    - Details of existing permits

Duvha Power Station is currently operating under Permit 596N, which was issued in terms of the Water Act, 1956 (Act 54 of 1956). This permit allows for the use of 53 837.5 Megalitres (Ml) of water per year. This water is supplied by the Department of Water Affairs from the Komati-Usutu Rivers Link System Government Water Scheme.

PART 2:	DESCRIPTION OF WATER ENVIRONMENT

  - Climate

2.1.1	Regional climate

Duvha power station is situated on the Highveld in the Central part of Mpumalanga province, on the escarpment, at an average height of 1 550 m above sea level. The winters are generally dry and cold with frost and intermittent light rain. The summers are mild with most of the rainfall, frequently in form of thundershowers, occurring during the summer.

- Temperature

The following annual average temperatures are reported by The South African Weather Services for the Witbank Centre. Monthly specific data is presented in table 2.1.3.

| Maximum | Minimum | Average |
| --- | --- | --- |
| 23.4 oC | 10.7 oC | 17.0 oC |

- Relative humidity

The following annual relative humidity readings are reported by The South African Weather Services for the Witbank Centre.

| 0800 | 1400 | 2000 | Maximum | Minimum |
| --- | --- | --- | --- | --- |
| 68% | 39% | 57% | 88% | 22% |

- Wind

Winds are generally light to moderate except during thunderstorms when North-East winds predominate, with a mean wind speed of 6.4 km/hr over

    - Rainfall data

Duvha Power Station is situated in the quaternary catchment B11G. According to WRC Report No. 298/2.1/94 is the rainfall as presented in Table 2.1.2 a) and b).

Table 2.1.2 a) Mean annual rainfall for Duvha Power Station

| Weather Bureau Gauge No. | Station Name | Record Used | No. of years | MAP (mm) |
| --- | --- | --- | --- | --- |
| 0478546 | Vandyksdrift | 1928 - 1989 | 62 | 696 |
| 0515412 | Witbank Municipality | 1956 - 1989 | 34 | 716 |
| 0515386 | Landau | 1950 - 1989 | 40 | 689 |
| Adopted MAP for Duvha Power Station | 700 mm |

Duvha Power Station is in an area of mean annual precipitation (MAP) of 700 mm per annum.

Table 2.1.2 b) Rainfall distribution

| Month | Percentage Distribution | Monthly Rain (mm) |
| --- | --- | --- |
| October | 11.37 | 79.6 |
| November | 16.35 | 114.5 |
| December | 14.37 | 100.6 |
| January | 18.67 | 130.7 |
| February | 12.58 | 88.1 |
| March | 11.57 | 80.9 |
| April | 6.56 | 45.9 |
| May | 1.81 | 12.6 |
| June | 1.09 | 7.6 |
| July | 0.81 | 5.7 |
| August | 1.03 | 7.2 |
| September | 3.79 | 26.6 |
| Total | 100% | 700.1 |

Table 2.1 2 c) Design rainfall depths mm during 24 hour duration

| Station | 2 years | 5 years | 10 years | 20 years | 50 years | 100 years | 200 years |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Vandyksdrift | 54 | 72 | 85 | 99 | 117 | 132 | 148 |
| Witbank Municipality | 51 | 69 | 82 | 95 | 113 | 127 | 142 |
| Witbank (POW) | 48 | 64 | 76 | 88 | 105 | 118 | 132 |

Reference Natal University CCWR

Table 2.1.2 d) Design rainfall depths mm during a 7 day duration

| Station | 2 years | 5 years | 10 years | 20 years | 50 years | 100 years | 200 years |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Vandyksdrift | 102 | 132 | 152 | 171 | 197 | 216 | 235 |
| Witbank Municipality | 98 | 127 | 146 | 165 | 190 | 208 | 227 |
| Witbank (POW) | 95 | 123 | 142 | 160 | 184 | 202 | 220 |

Reference source WRC Report No. 298/2.1/94.

Table 2.1.2e) Op Ten Noord formula storm duration

| Storm duration |  |  | Recurrence interval (Years) |  |
| --- | --- | --- | --- | --- |
| Hours | 2 | 5 | 10 | 25 | 50 | 100 |
| 2 | 18mm | 23mm | 29mm | 38mm | 46mm | 57mm |
| 4 | 10mm | 13mm | 16mm | 21mm | 26mm | 32mm |
| 6 | 7mm | 9mm | 11mm | 15mm | 19mm | 23mm |
| 8 | 6mm | 7mm | 9mm | 12mm | 15mm | 18mm |
| 10 | 5mm | 6mm | 7mm | 10mm | 12mm | 15mm |
| 12 | 4mm | 5mm | 6mm | 8mm | 10mm | 13mm |
| 14 | 3mm | 4mm | 6mm | 7mm | 9mm | 11mm |
| 16 | 3mm | 4mm | 5mm | 6mm | 8mm | 10mm |
| 18 | 3mm | 4mm | 4mm | 6mm | 7mm | 9mm |
| 20 | 2mm | 3mm | 4mm | 5mm | 7mm | 8mm |
| 22 | 2mm | 3mm | 4mm | 5mm | 6mm | 7mm |
| 24 | 2mm | 3mm | 3mm | 5mmm | 6mm | 7mm |
| Op Ten Noord Formula |  |  |  |  |  |

    - Temperature data

Table 2.1.3 (a).  Temperature data for the Witbank area

| Season | Month | Daily mean oC | Daily Max oC | Daily min oC |
| --- | --- | --- | --- | --- |
| Summer | October | 18.3 | 24.8 | 11.7 |
|  | November | 18.9 | 24.6 | 13.2 |
|  | December | 19.8 | 25.1 | 14.5 |
|  | January | 20.6 | 26.2 | 14.9 |
| Autumn | February | 20.5 | 26.0 | 15.0 |
|  | March | 20.2 | 26.1 | 14.2 |
|  | April | 17.5 | 23.9 | 11.2 |
|  | May | 14.5 | 21.3 | 7.7 |
| Winter | June | 12.2 | 19.1 | 5.2 |
|  | July | 11.4 | 18.4 | 4.3 |
|  | August | 14.1 | 21.5 | 6.7 |
|  | September | 16.4 | 23.5 | 9.2 |
| Annual |  | 17.0 | 23.4 | 10.7 |

Daily air temperatures as provided by The South African Weather Service

    - Evaporation data

The average mean annual evaporation (MAE) S Pan value for the quaternary catchment B11G is 1292 mm. Duvha Power Station is situated in Evaporation Zone 4A and thus represents a distribution in accordance with Table 2.1.4 a).  The mean annual evaporation rate MAE for the quaternary catchments B11G was quoted to be 1600mm (A pan) respectively. This figure had to be converted into MAE (Symans Pan) and therefore a mean annual evaporation rate of 1292mm was therefore adopted for Duvha Power Station. Reference source WRC Report No. 298/2.1/94.

Table 2.1.4 a) Distribution of evaporation losses

| Month | % Distribution | Monthly mm |
| --- | --- | --- |
| October | 10.78 | 139.3 |
| November | 10.17 | 131.4 |
| December | 11.20 | 144.7 |
| January | 11.00 | 142.1 |
| February | 9.17 | 118.5 |
| March | 9.05 | 116.9 |
| April | 6.96 | 89.9 |
| May | 5.86 | 75.7 |
| June | 4.76 | 61.5 |
| July | 5.21 | 67.3 |
| August | 6.90 | 89.2 |
| September | 8.94 | 115.5 |
| Annual | 100% | 1292 mm |

Reference source WRC Report No. 298/2.1/94

2.2 Topography

Figure 1. Location of Duvha Power Station in relation to the topography, ash dam, coal stockyard, solid waste

site (W) and Witbank Dam.

Duvha Power Station is located south of the Witbank Dam (Figure 1). At its closest point, the Witbank Dam is 1,5 km from the ash dam. The ashing facility comprises 480 ha. The coal stockyard is located close to the power station, covering an area of 26 ha.

Almost all surface run-off occurs towards the north. A very small portion of the power station terrain and coal stockyard drains to the south. Water from the southern slopes also ends up in the Witbank Dam, though along another route.

A pan exists west of the power station, which serves as an emergency water storage facility. The pan serves as a catchment mainly for rain water and is fed by a natural fountain. An overspill trench leads from the pan to discharge into the ash water system to the north.

2.3 Geology

Water from the power station terrain seeps into the ground, infiltrating the weathered zone. Below this zone, the almost impervious and fresh Karoo sediments deflect the water laterally. As a result, the groundwater table rises. Dwyka tillite is present, this is impermeable to groundwater movement and pollution will not be able to penetrate this layer in the event that the upper aquifer should become polluted.

A geological profile showing the typical geology in the vicinity of the power station is presented in Figure 1.

Figure 2. Geological profile showing typical geology for the power station terrain

2.4  Surface Water

2.4.1 Nearest watercourse

Duvha Power Station including the ash dams is situated in the Olifants River catchment area, which is a tributary of the Olifants River.

2.4.2 Receiving water body

Duvha Power  Station is situated in the B11G (Figure 2) quaternary catchment of the Witbank Dam. The catchment (B11G) surface area is 368 km2  and has a net mean annual runoff (MAR) of 13.2 * 106 cubic meters.

Figure 2. Quaternary catchments

    - Water use in accordance with SA Water Quality Guidelines

The following water uses are identified as possible users within the quaternary catchment and definite users within Witbank Dam area and Olifants catchment :

- Domestic

- Industrial from the Witbank Dam only

- Natural environment

- Recreational

- Agriculture

- Live stock watering

    - Water authority

The water authority for the area is the Department of Water Affairs and Forestry (DWAF) Mpumalanga Region.

    - Wetlands

There are no significant wetlands that can be identified from the 1 in 50 000 topographical maps.

  - Groundwater

Ground Water monitoring has been ongoing at Duvha Power Station since 1989.The boreholes are sampled and analysed 6 monthly and the geological logs and data of each borehole are contained in the Water and Steam Data Management System.  The interpretation of the analytical data can be done with the WISH programme, which was obtained from Professor Frank Hodgson.

a).  Location of the boreholes

Monitoring boreholes B1, B2 and B3 were drilled in the area between the ash dam and Witbank Dam.  These holes monitor the area where previous contamination of groundwater had been reported by  farmers.  Borehole B4 and B5 are located below the dam wall of the ash water returns dams and originates from seepage from the ash water return dam.  Boreholes B6, B7 and B8 are situated between the coal stock yard and the Sannieshof Sewage plant.  Borehole B9 and B10 are situated close to the high levels ash dams.

2.5.1.  Identification and quantification of the affected zone

The affected groundwater zone at Duvha Power Station is mainly limited to the weathered sediments of the area.

Figure 3. Locality plan showing positions of monitoring boreholes.

2.5.2. Water qualities in the monitoring boreholes.

Figure 4. Electrical conductivity graphs of historic water qualities at monitoring boreholes.

Figure 5. pH-graphs of historic water qualities at monitoring boreholes.

Figure 6. Calcium graphs of historic water qualities at monitoring boreholes.

Figure 7. Magnesium graphs of historic water qualities at monitoring boreholes

Figure 8. Sodium graphs of historic water qualities at monitoring boreholes.

Figure 9. Potassium graphs of historic water qualities at monitoring boreholes.

Figure 10. Calcium graphs of historic water qualities at monitoring boreholes.

Figure 11. Sulphate graphs of historic water qualities at monitoring boreholes.

From the figures above the following can be concluded:

- The boreholes in the areas downstream from the ash (B1, B2, B3, B4 & B5) show various degrees of groundwater pollution. Pollution levels and constituents vary according to distances from the ashing facilities.

- Borehole B4, immediately below the ash water returns dam has the highest salinities. The high concentration of sulphate in noticeable with intermediate levels of calcium, magnesium and sodium. The alkalinity in this borehole has generally been rising over the past five years. The pH of the borehole water (7,0) contrasts markedly with that in the ash water return dam (11,25).

- Boreholes B1 – B3, which are in an area known to have been polluted as early as 1989, do no show deterioration in water quality over the past five years. In fact, sulphate levels have decreased to below 30 mg/L. The conclusion is that the trench (Figure 3) which was dug between the ash dump and these boreholes, as well as the eucalyptus trees (Figure 1H) planted in this area have greatly reduced the flux of ash water away from the ash dam.

- Borehole B5, which is located north of the ash dam, shows an increase in sodium and chloride (Figure 9). Concentrations here are, however, still negligible compared to all water standards.

- Boreholes B6 – B8, east of the coal stockyard, are not contaminated. The water quality in these boreholes is still pristine.

# Possible affected users:

| Property Name | Property Number | Owner |
| --- | --- | --- |
| Farmers: |  |  |
| Neels Van Dyk | Remainder of Portion 3, Rhenosterfontein No. 318-JS | Neels Van Dyk |
|  | Portion 11, Rhenosterfontein No. 318-JS | Neels Van Dyk |
|  | Portion 2 Speekfontein No. 336-JS | Duvha Power Station |
| Nico Gouws | Portion 1 Duvha Power Station No. 337-JS | Nico Gouws |
|  | Portion 15,16 Speekfontein No. 336-JS | Nico Gouws |
|  | Portion 9,10 Driefontein No. 338-JS | Nico Gouws |
| Industry: |  |  |
| Corobrik | Portion 3, Duvha Power Station No. 337-JS | Corobrik |
| Middelburg Mine South | Portion 1, Driefontein No. 338-JS | Middelburg Mine South |
|  | Portion 2, Duvha Power Station No. 337-JS | Middelburg Mine South |
|  | Remainder Portion 4,12, 13. Portion 29,30,7 Speekfontein No. 336-JS | Middelburg Mine South |

# PART 3: WATER MANAGEMENT

3.1 Industrial Water Use and Process Description

3.1.1 Water Sources in the Power Station

## Raw water

## Cooling water

Demineralised water

Potable water

Ash water

Water treatment effluents

Dirty Storm water

Treated sewage water

Mine Water Recovery

3.1.1.1 Typical water requirements at Duvha Power Station

## Water consumption depends largely on the load generated. This is mainly as result of the evaporation from the cooling towers during the rejection of the waste heat.

#### Table 3.1.1 (a): Typical water requirements for Duvha Power Station

| Water System | Source | Minimum Demand | Maximum Demand | Base load Demand |
| --- | --- | --- | --- | --- |
| Potable water *1 | Raw water | 5.0 Ml per day | 9.0 Ml per day | 7.5 Ml per day |
| Demineralised water | Raw water | 1.0 Ml per day | 3.0 Ml per day | 2.0 Ml per day |
| Cooling water | Raw water Dirty storm water (*2) | 70 Ml per day | 175 Ml per day | 125 Ml per day |
| Ashing system (Ash water) | Water treatment effluents Dirty storm water (*2) Cooling water blow-downs | 43 Ml per day | 65 Ml per day | 53 Ml per day |

(*1) Excluding third parties

(*2) When available and conforming to the quality requirements of the cascading destination

The Duvha Power Station raw water is supplied from the Komati system augmented by the Usutu system. The current cost for raw water from this system is approximately      R 793.00 per Ml. The cost comprise of the following:

- Raw water tariff

- Catchment Management Fee

- Water Research Commission levy

- Electricity

- Operation and maintenance

- Capital

3.1.2 Production days

Electricity is produced 365 days per year.

3.1.3 Yearly usage pattern

The bulk of the water consumed at Duvha Power Station will be directly proportional to the load send out by the generating sets.

3.1.4 Applicable water rights

None.

3.1.5 Average and maximum water usage applied for

As water is used in the process to generate electricity there is a direct relationship between energy produced and water consumed.  This relationship is expressed as l/USO (i.e. the specific water consumption) and is calculated by dividing water consumption by energy send-out.

Production at Duvha Power Station will be in accordance with the graph below.

Electric power demand will necessitate the operation of Duvha Power Station at high production levels during the coldest periods of the winter months. This represents the production peak, which will necessitate maximum raw water demands.

Figure 13. Raw water use projections

Projected maximum raw water requirements for the next 5 years is expected to be around 130 Ml per day.

The usage application is therefore in accordance with the projected consumption See table 3.1.5 (a) below.

Projected water consumption for Duvha Power Station is based on Eskom’s 5-year Production Plan (14 April 2003). These projections are part of the Eskom water demand projections provided to DWAF on a biannual basis.

Table 3.1.5 (a): Projected raw water demand for Duvha Power Station

| Year | Requirement per Annum | Daily Maximum |
| --- | --- | --- |
|  | Ml per annum | Ml per day |
| 2001 | 45229 | 123.9 |
| 2002 | 47253 | 129.5 |
| 2003 | 43657 | 119.6 |
| 2004 | 46044 | 126.1 |
| 2005 | 48196 | 132.0 |
| 2006 | 48074 | 131.7 |
| 2007 | 47667 | 130.6 |
| 2008 | 48380 | 132.5 |

3.1.6 Processes

Duvha Power Station’s raw water requirement can be met from either of two sources.  First, water can be pumped from the Vygeboom and Nooitgedacht dams in the eastern part of the Mpumalanga, which are fed by the Komati River.  These dams can also be supplied with water from the Usutu system.  Secondly, water can be obtained from the Witbank Dam in the upper reaches of the Olifants River and supplemented with water from the Grootdraai Dam in the Vaal River near Standerton.

- Water treatment plant

Duvha’s raw water requirement is currently from the Komati system but due to an increased growth in population and demand for electricity the system was in jeopardy in 2002.  Duvha’s raw water demand has therefore been augmented from December 2002 from the Usuthu system. The water quality requirement for the potable water production process complies with the National Guidelines and Standards.  Raw water is treated to potable standard by coagulation, clarification, filtration and chlorination.  Potable water is used on the Duvha Power Station for domestic use and some is distributed to third parties (i.e. Ikageng, Duvha Opencast Mine and Sannieshof single accommodation facility).

Some of the potable water is also used in the production of demineralised water for use in the boilers and condensate polishing plant.  Demineralised water is produced using the Ion Exchange Technique.  The susceptibility of the ion exchange resins to deteriorate over time and increases in the effluent volumes emanating from these processes are recognised and are mainly as a result of ageing.  If extended rinse water volume occurs from these processes after regeneration it will act as an indicator to replace resins. The demin plant resins are sampled 6 monthly and all the Condensate Polishing Plant resins annually.  They are sent to Rohm and Haas for analysis. Condensate Polishing Plant (CPP) resins are sampled before and after regeneration and capacities on the resins are done to check the efficiency of the regeneration, especially where units had condenser tube leaks.

Effluents emanating from the process includes spent regenerants, raw water clarification sludge and backwash and rinse water. The high salinity effluent is disposed of in the ash water system in accordance with the Eskom guideline GGM 0970, while low salinity effluent cascades to the cooling water system via the station drains system.

ii) The steam cycle

Six turbo-generators, which are steam driven, are used to generate electricity at Duvha Power Station.  The steam is produced in the six boilers which are of the Benson type, which depends on forced circulation and has no steam drum.  The feedwater, which is highly purified and demineralised, makes one continuous and uninterrupted circuit through the boiler, the turbine, and the condenser and again through the boiler.  On its path through the boiler, the feedwater evaporated and as more heat is absorbed, the steam becomes superheated to a temperature of 540 oC and a pressure of 17,1 mPa.

A feature of the steam pipework is a high-pressure system that allows the superheated steam to bypass the high-pressure turbine when necessary, to flow directly into the reheat pipework.  From there it bypasses the intermediate-pressure and low-pressure turbines and flows into the main condenser.  This system means that the boiler can be operated independently of the turbine and the correct steam temperature and pressure can be obtained before the generator is started up.  Also, if a turbine trips, the system allows the boiler to be operated at roughly 40 per cent of its maximum load, it can be run at a low load while the boiler is maintained at a higher load.  In both instances, the bypass system prevents, within the limits of its capacity, sudden pressure rises from exceeding the settings of the safety valves in the reheater.

Each boiler is fitted with twenty-four burners, arranged in twelve rows of two-six rows in the front wall of the furnace and six rows in its rear wall.  Each coal mill supplies four burners – two in the front wall and two in the rear wall.  Mounted in the centre of each burner is an oil burner and these are used for starting up and for stabilising the combustion coal at low loads.

Forced-draught fans supply secondary air to the burner wind boxes while primary-air fans transport pulverised coals from the mills to the burners.  Combustion gases are drawn from the furnace by two induced-draught fans, over the surfaces of the steam superheaters, the reheaters, and the economiser and air preheaters, through the electrostatic precipitators and into the chimney.

Each boiler has a capacity of 507 kg/s of steam and the feedwater is supplied, at a pressure of 22 Mpa, by two electric pumps rated at 13 MW each, or by one steam-driven pump.  At maximum continuous rating the efficiency of the boilers is 93,9 percent.

- Main cooling water system

The main cooling system condenses the Low-Pressure exhaust steam into the condenser.  This clean condensate gets circulated back to the boiler.

The condensate temperature in the condenser hotwell is about 37 oC.  In order to obtain maximum system efficiency it is necessary to reheat the condensate before returning it to the boiler.  To achieve this, the condensate is passed through numerous heaters before feeding it into the boiler.  All the heaters are of the surface type in which the water flows through tube nests.  Steam extracted from different stages of the turbine heats the water by conduction through the tube metal.

A deaerator situated between the low-pressure and high-pressure heaters removes entrained oxygen in the condensates and heats the water through direct contact with steam extracted from the turbines.  The condensate is pumped from the condenser to the deaerator through low-pressure heaters by means of the main condensate extraction pumps.

The condensate is then pumped from the deaerator feedwater tank to the boiler through the high-pressure heaters by the boiler feed pumps.  The final feedwater temperature at 600 MW is 247 oC.

The condensers are of the dual-pressure surface type.  The vacuum inside the condensers is established by steam-jet air ejectors and maintained in normal operation by water-jet air ejectors.  The steam exhausted from the low-pressure cylinder condenses over 22 552 brass tubes, which have a surface area totalling 23 400 m2.  Each boiler-turbine set has a condenser with a heat exchange capacity of approximately 400 MW.

The six cooling towers at Duvha are designed for a total thermal load of nearly 19 000 GJ/h.  The three large towers are 149m high and 114m in diameter at the base and the minimum shell thickness is 180 mm.  At full load the evaporation from one-tower amounts to 30 Ml a day.

Cooling water treatment and specific the option employed to de-alkalinise the cooling water is an important decision if Zero Liquid Effluent Discharge (ZLED) is to be maintained at all times. Alkalinity control with acid is a neutralisation process and contributes to the salt load of the cooling water. Lime alkalinity control is a precipitation process and very little inorganic contamination of the cooling water takes place during the process.

Lime alkalinity control is therefore the preferred option of cooling water

treatment and these lime systems are managed such as to maintain it as close 			as possible to  100% availability.

- Ash plant and ash dams

At full load each boiler produces 250 tons of coarse ash and 1400 tons of fly ash every day.  The coarse ash and the material rejected from the mills are crushed and fed into sumps, from where it is pumped to the ash dam.  The fly ash sluiced from the precipitator hoppers is pumped separately to the ash dam, where it is used to build ash dam walls.

Water from the dam, which covers an area of 450 ha, is decanted and reused in the ash system in a closed loop.

The concentration of the hydroxides in the ash water is of crucial importance if the ash water sulphate concentration is to be substantially lowered in the ash dump. High concentrations of hydroxides in the ash water will increase the solubility of aluminium from the ash, this will lead to the formation of aluminium hydroxide, as the solubility of Al (OH)3 increases with increase in pH (hydroxides). This causes an insoluble salt known as ettringite (3CaO.3CaSO4.Al2O3.31H2O) to precipitate, thereby removing some calcium and sulphate from the solution.  The stoichiometry is given by the following reaction.

6Ca2+ + 3SO42- + 2Al(OH)3 + 37H2O (  3CaO.3CaSO4.Al2O3.31H2O + 6H3O+

The formation of ettringite is pH dependant, the optimum [OH-] Concentrate lying between 600 and 1200. Sodium could depress the solubility of ettringite but sulphates could generally be lowered to approximately 450 mgkg-1 as SO4. The result of this is that this water is then suitable for reuse in the cooling water system.

Refer to Appendix A: Ash Dam Operating Manual

- Station drains system

All drains are diverted to this system.  These drains collect water from following systems:

- cooling water systems

- storm water within the station and terrace

- drainage of boilers and condensers

The oil separation system is a tilted weir separation system. Any spilled oil is retained in the oil ponds. An overflow weir system allows for the cascading of contaminated drains to the oil separation system.  Oil absorbent pillows and booms are kept as a stock item in the stores.

The water quality is therefore always equal or better than the cooling water systems quality requirement and the water is then recovered back into the main cooling water system.

- Sewage treatment plant

A sewage treatment plant is also operational on the plant.  The sewage treatment plant receives sewage from the station complex, hostel and married quarters.  The sewage is treated using an activated sludge type process.  The purified sewage effluent is returned to the station ashing system.

Table 3.1.6 (a):Typical treated sewage water quality for Duvha Power Station

| Parameter | Units | Average |
| --- | --- | --- |
| pH |  | 9.5 |
| E.C. | (S/cm | 25 |
| M Alk | mg/kg as CaCO3 | 66 |
| Phosphate | mg/kg as PO4 | 3.0 |
| Ammonia | mg/kg as N | 1.0 |
| NO2 + NO3 | mg/kg as N | < 0.1 |
| Cl | mg/kg | 22.7 |
| SO4 | mg/kg | 16.1 |

Table 3.1.6 (b): Typical water usage quantities at Duvha Power Station

| Water system | Average daily quantity Ml | Peak daily quantity |
| --- | --- | --- |
| Total raw water | See table 3.1.5 a | 120 |
| Potable water | 7.5 Ml per day | 9.0 Ml per day |
| Demineralised water for steam cycle | 2.0 Ml per day | 3.0 Ml per day |
| Main cooling system make-up | 125 Ml per day | 170 Ml per day |

*1 Internal circulation thus not an additional raw water requirement

Table 3.1.6 (c): Typical water qualities of water used at Duvha Power Station

| Parameter | Units | Potable water | Demin water | Raw water | Cooling water | Station drains |
| --- | --- | --- | --- | --- | --- | --- |
| PH |  | 8.96 | 7.0 | 7.8 | 8.1- 8.5 | 7.7 |
| Electrical conductivity | µScm-1 | 148.8 | 0.06 | 134 | < 2500 | 272 |
| Calcium as CaCO3 | mgkg-1 | 25.4 | Nil | 27 | 100 - 300 |  |
| Magnesium as CaCO3 | mgkg-1 | 30 | Nil | 29.5 | 80 – 220 |  |
| P Alkalinity as CaCO3 | mgkg-1 | 5.4 | Nil | Nil | 0 - 7 |  |
| M Alkalinity as CaCO3 | mgkg-1 | 57 | Nil | 50.6 | 80 - 120 |  |
| CaCO3 PP @ 25o C | mgkg-1 | -14.3 | Negative | - 6.3 | 1 - 7 |  |
| Sodium | mgkg-1 | 7.96 | < 0.002 | 5.6 | 30 – 80 | 46.4 |
| Potassium | mgkg-1 | 1.12 | < 0.001 | 1.04 | 40 - 80 |  |
| Chloride | mgkg-1 | 5.5 | < 0.001 | 3.5 | 20 - 50 |  |
| Sulphate | mgkg-1 | 7.45 | < 0.001 | 8.21 | < 750 |  |
| Silica as SiO2 | mgkg-1 | 0.33 | <0.003 | 7.3 | < 150 |  |

3.1.7 Re-use of water

Duvha Power Station has adopted a cascading hierarchy based on the quality of the water. This entails the controlled cascading of water from the one system to another as soon as the water no longer meets the quality requirement of the current system.

All leaks, drains and on terrace storm water cascades to the Low Level Dams. Upstream from the Low Level Dams are oil and grit removal systems to prevent oil contamination and silting of the dam. The water quality and the water level of the ashing system determine the reuse destination of this water. The water quality from this system is always better then that of the cooling water system and recovery to the cooling water system ensures compliance with the ZLED policy.

The water collected in the station drains is recovered to the cooling water where the water is concentrated to the specified thresholds for cooling water. If it is not possible to facilitate further concentration of the station drains through recovery to the cooling water systems the station drains are pumped to the ashing system.

The ash water is reused several times to remove the coarse and fly ash from the respective systems. Water is “lost” from the ashing system as result of natural evaporation, seepage and interstitial hold. Due to the fact that Duvha Power Station will be operated as a Zero Liquid Effluent Discharge facility (when not considering seepage losses), reuse in terms of the wet cooled power generation process is almost 100%.

3.1.8 Reduction of water in the production processes

3.1.8 a) The open evaporative cooling water system

Duvha Power Station will be operated with raw water from the Komati system, which are very low in salinity thus allowing the operation of the cooling water systems at high cycles of concentration. Operation of cooling water systems at high cycles of concentration means that relatively small volumes of water must be removed (blow down) from these systems to maintain the systems water quality requirements. Cooling tower blow-downs are used to supplement consumptive use within the ashing cycle.

Evaporation from open evaporative cooling towers is dependent on the efficiency of the energy conversion process. Chemical energy from the coal is converted into electrical energy. During the process is waste heat rejected through cooling which drives the evaporation of water. The term waste heat does not imply that the conversion process is wasteful but rather refer to a large amount of heat available at low temperature. Logistics and the South African climate is the main reason why this heat cant be used sensibly.

Evaporation from the cooling towers is proportional to the load generated and is normally reported against the load sent out by the power station.  The efficiency of the energy conversion process is consistently monitored and optimised by Performance Monitoring and Optimisation Department at the power station. It must be noted that poor efficiency not only manifests in the form of additional water losses but also coal losses. Coal is the most expensive raw material used in the process and monetary savings on coal exceed that on water by far.

Table 3.1.8. a) below represents the specified thresholds at which blow downs must be opened. The objective is not to do intermittent blow downs but rather continuos controlled blow downs. It must also be noted that the volumetric water requirements of the wet ash disposal system will dictate the maximum cycles of concentration.

Table 3.1.8. a) The specifications for cooling water are:

| Parameter | Limit or range | Frequency of analysis |
| --- | --- | --- |
| Turbidity | As low as cost effectively possible but < 100 FTU | Daily |
| Conductivity | Conforms to the cycles of concentration being used but generally < 4000 (Scm(1 | Daily |
| Condenser temperatures T1, T2 and Δ T | Indicative of condenser problems that will lead to increased water consumption. Must be incorporated in the chemistry data sets. | Daily |
| pH | 8,1 to 8,6 @ 25 °C | Daily |
| “P” alkalinity | < 7,5 mgkg(1 as CaCO3 | Daily |
| “M” alkalinity Guideline limits only and will not constitute an out of specification condition provided that the CCPP conforms to the specified limits | 80 to 120 mgkg(1 as CaCO3 without a crystal modifier dosing programme. (Depending on CCPP) 120 to 160 mgkg-1 as CaCO3 with a crystal modifier dosing programme. | 3 ( Daily |
| Calcium | 200 to 500 mgkg(1 as CaCO3 | Daily |
| Silica | < 150 mgkg(1 as SiO2 While also taking cognisance of Mg ( SiO2 limitation | Daily |
| Magnesium | Mg (as CaCO3) ( SiO2 < 25 000 | Daily |
| Calcium carbonate precipitation potential (CCPP) at 38o C | Stasoft version 4.0 Without crystal modifier dosing: < 30 mgkg-1 as CaCO3 With crystal modifier dosing: < 45 mgkg-1 as CaCO3 | * 3 X Week |
| Sulphate | Poor quality concrete <1000 mgkg-1 if Na+ < 250mgkg-1 <750 mgkg-1 if Na+ > 250 mgkg-1 High quality concrete < 1500 mgkg-1 if Na+ < 500 mgkg-1 < 1000 mgkg-1 if Na+ >500 mgkg-1 Note: Mg++ to be <150 mgkg-1 as CaCO3 | * 1 X Week |

* Depending on the risk of exceeding the specification. If the risk of exceeding the specified limit is high the surveillance shall be increased to at least three times per week.

Table 3.1.8. (a).  Cooling water specification continued:

| Parameter | Limit or range | Frequency of analysis |
| --- | --- | --- |
| Phosphate | < 0,5 mgkg(1 as PO4 | Weekly |
| OA and COD or TOC | As low as economically possible through the application of suitable flocculants. | Weekly |
| Chloride | < 400 mgkg(1 as Cl | * Weekly |
| Nitrate and nitrite | Not specified | Weekly |
| Sodium | < 600 mgkg(1 as Na if SO4= < 750 mgkg-1 < 500 mgkg-1 as Na if SO4= >750 mgkg-1 | * Weekly |
| Potassium | Not specified | Weekly |
| Copper, Zinc and Iron. | Not specified | Monthly |
| Ammonia | < 40 mgkg-1 as NH4 | Weekly |

3.1.8 b) The ash disposal system

Wet Ash Disposal systems requires more water for the operation of the system. Wet systems further are simple to operate and is of relative low cost when compared to Dry Ash Disposal systems. Consumptive uses in the ashing cycle are mainly as result of:

- Interstitial hold (Absorption on the ash)

- Evaporation from the wet ash on the ash dam (dump)

- Evaporation from the water pool on top of the ash dam (dump) which is used to separate the water from the ash in order to allow for effective reuse of the water.

4. Evaporation during the quenching of bottom (coarse) ash following combustion to

facilitate safe removal.

- Evaporation from the Low Level Ash Water Dam

Table  3.1.8. b): Evaporative water losses for Duvha Power Station

| Area | Water loss through Evaporation |
| --- | --- |
| Evaporation from raw water reservoirs (15.3 ha) | 131.64 Ml/yr. |
| Evaporation from ash water ( Water phase) | 1411.53 Ml/yr. |
| Evaporation from wetted ash phase | 2628.00 Ml/yr. |
| Evaporation from the Low Level Ash Water Return Dam (6.6 ha) | 12.658 Ml/yr. |
| Evaporation from the Emergency Pan (24.7 ha) | 471.913 Ml/yr. |
| Evaporation from the active ash disposal dump (240 ha) | 105.120 Ml/yr. |
| Evaporation during bottom ash quenching | 0.536 Ml/yr. |
| Evaporation of demineralised water as steam | 1.320 Ml/yr. |
| Evaporation from sewage maturation pond (0.5 ha) | 9.537 Ml/yr. |

3.1.9 Methods to minimise liquid waste loads

It must be noted that Duvha Power Station will be operated in compliance with the Eskom ZLED policy. This implies that effluent volumes are less than the available effluent sink. See table 3.1.8-(e) Effluent concentration by employing techniques such as membrane desalination are therefore not required. All chemicals used in the water treatment process are expensive and continuo optimisation is standard practice for all Eskom Power Stations. A reduction in chemicals employed in the power generation process implies that the salt load will be reduced which ultimately will have to be disposed on the ash.

3.1.9 a) Coal conveyer belt washing

Coal dust posses hazards with respect to Alpha Quartz and Silicoses and also coal dust explosions. Dry-cleaning are therefore not considered to be safe and is wet cleaning the only safe option available.

High pressure washing systems will be used for conveyer washing at Duvha Power Station; this will eliminate excessive liquid wastes produced from the washing of these systems.

3.1.9 b) Ion exchange resins

The selection of ion exchange resins will be such as to maximise the volume and quality of the demineralised water. This means that more demineralised water and of a better quality will be produced for the same mass of regenerants used. The improved quality means that less water will have to be removed (blown down) from the boilers (drum type boilers) thus reducing the demineralised water consumption which will further reduce the regeneration chemical requirements. Demineralised water with Ion Exchange is the only technology, which produces demineralised water suitable for high-pressure boilers, and thus complies with the BATNEEC principle.

3.1.9 c) Condensate polishing

Should condensate purification (Condensate Polishing) become a requirement during the two-shift mode of operation will micro filtration be considered. It is anticipated that micro filtration will produce minimal chemical effluents (in comparison to ion exchange) while backwash water will be recovered to the cooling water systems. The low capital cost and the mobility of a micro filtration system further benefits this option in comparison to ion exchange.

3.1.9 d) Recovery of spent caustic regenerant

Anion ion exchange resins are regenerated with a diluted caustic soda and cation ion exchange resins with sulphuric acid. This implies that the effluent once mixed in the effluent sump is a solution of sodium sulphate with low concentrations of calcium and magnesium sulphate and sodium chloride.

In theory will the elimination of the caustic from the effluent stream change the effluent composition to calcium sulphate following the neutralisation of the spent acid regenerants with calcium hydroxide from the ash water. This will imply that the sulphate from the cation regeneration process is now converted into lowly mobile calcium sulphate through the following chemical reaction.

H2SO4   +   Ca(OH)2 (in the ash water)   (   CaSO4   +   2H2O

This implies that the calcium sulphate can be eliminated as ettringite from the environment through the same phenomenon as described in section 3.5.5 b. There are therefore no economic or environmental justification to recover the spend acid regenerants.

The economic viability and technical reliability of the technology to eliminate the caustic effluents are frequently evaluated by Eskom. The technology to recover and purify and reuse caustic soda spent regenerants will be employed by Eskom if the technology becomes technically reliable and economically viable.

The main limitations of the current technology for caustic recovery are:

- No suitable RO membrane material for the pH of the application >14

- Ion exchange process requires high purity regenerants

- Severe fouling of the membranes with silica and organic compounds

Note: The Koch AlkaSave® System employs nano filtration membranes and would therefore not remove soluble sodium species of sulphate and chloride. This technique is only viable for removing heavy metal precipitates and colloidal matter from caustic solutions.

3.1.10.  Effluent Management:

(a).  Disposal priority of effluents:

The cascading hierarchy of effluents to a suitable section of the effluent sink is an important aspect of the management of effluents.

The priority of disposing effluents is as follow:

- regenerants

- Sludge from the clarification processes

- Brine effluent

4.           Concentrated cooling water

(b). Cascading destination:

The objective with effluent disposal should always be to permanently sideline the salts (effluent) from the water circuits. Aspects such as the blow-down of cooling water to a system from which water is recovered back to the cooling water system only meant that the salts contained in the cooling water were temporarily sidelined.

The disposal of high salinity regeneration effluents to the ash sumps using ash sluiceways will compromise the integrity of the concrete as result of the high level of sodium sulphate. Neutrality (pH) of the spent regenerants is crucial importance in order not to jeopardise the integrity of the concrete. High sulphate and specifically in the form of sodium sulphate will compromise the integrity of the concrete if it is not sulphate resistant concrete.

The only acceptable cascading destination for high salinity regeneration effluents is the fly-ash conditioning system. The continuous use of cooling water and or ash water at these systems will result in the formation of calcium carbonate and calcium sulphate scale receptively. The application of a crystal modifier / anti-scalant is regarded as the only solution for scaling problems on these components.

(c). Effluent concentration:

Effluent concentration becomes a requirement when the total effluents produced exceed the available effluent sink. The “Saltman” spreadsheet programme has the facility to predict this situation and is therefore used in the pre-emptive approach of ensuring the process plant long-term health.

(d). Waste minimisation:

Minimisation of effluents is a continual process and best evidence of this is illustrated by:

The utilisation of low rinse water volume resins in the ion exchange processes.

CCW Clarifier sludge

- The station drains

3.1.11.   Raw materials and waste volumes

The following raw materials are used in the energy conversion process (chemical energy from coal into electrical energy):

- Coal at 463 tons  per GW hour sent out

- Raw water  2.01 Ml per GW hr at 75 %  station load factor

- Fuel oil

- Sulphuric acid

- Caustic Soda

- Lubricating oils

- Aluminium sulphate

- Calcium chloride

- Soda ash

- Chlorine

3.1.11.1.  (a) Coal

Middelburg Mine will supply coal to Duvha Power Station South.

Coal is stored in the coal staithes or in the open on the coal stockyard.  The coal stock yard will be lined with a clay liner suitable to prevent the migration of significant volumes of polluted water to the ground water system. Oxidation of pyrites will take place and will be washed from the coal. This polluted runoff will be collected in a suitably lined stockyard pollution control dam. All the water collected in this dam will be used for dust suppression on the coal stockyard.

Coal is stored on site to ensure the uninterrupted supply of electricity during labour disputes or any other possible coal supply disruption.

3.1.11.1.  (b) Raw water

Duvha Power Station will use raw water from the Komati Government Water Scheme. Water from Grootdraai Dam will be transferred to the raw water reservoirs at Duvha Power Station.

Raw water is stored in reservoirs. Raw water is fed directly from the reservoirs to the water treatment plant and cooling towers.

Water borne salts represents a significant fraction of the salts that must be disposed to the ash. This section will quantify the salt load contained in the raw water without taking cognisance of any chemical addition. A typical quality of Usutu water is used for the quantification purpose.

3.1.11.2.  Fuel Oil

Fuel oil is received in bulk tankers and is stored in bulk tanks on site. These tanks are within bunded areas, which will retain spills. Any oil spillage outside the bunded areas will flow towards the station drains interception. Any oil on the station drains will be retained at the oil and grit separation plant prior to Low Level Dams.

Fuel oil is consumed during the start-up of generating sets and is therefore not proportional to load as other raw materials. Fuel oil consumption is more a function of the number of start-ups and the technical difficulties experienced during start-up.

Oil combustion produces no solid wastes and there would thus be no impact from the combustion of oil during the start-up process of the generating sets.

3.1.11.3.  Sulphuric acid

Sulphuric acid is received in 30-ton bulk tankers and is off loaded into bunded bulk storage tanks. The off loading area is designed to retain any spillage that might occur during the off loading process.

Sulphuric acid is used for the neutralisation of the incoming alkalinity in the cooling water and for the regeneration of cation exchangers in the ion exchange process for demineralised water production.

Sulphuric acid used for the demineralised water production process (cation regeneration) will be disposed following neutralisation with caustic soda (anion regeneration). This implies that almost all the acid used for demineralised water  production will be as sodium sulphate in the end state.

Sulphuric acid used for the control of alkalinity in the cooling water systems react in accordance with the equations below:

Ca (HCO3)2  +  H2SO4     (    CaSO4  +  2CO2  +  2H2O

Mg(HCO3)2  +  H2SO4    (   MgSO4 +  2CO2  +  2H2O

Mg SO4   +    Ca(OH)2 (ash water)     (    Mg(OH)2 (  +  CaSO4

This implies that the end state for all the calcium and magnesium alkalinity species will be calcium sulphate. Section 2.5.4.1 refers to the synergistic effects of the ash water chemistry, which result in the removal of calcium sulphate from the ash water as ettringite.

3.1.11.4.  Caustic soda

Caustic soda is received in 30-ton bulk tankers and is off loaded into bunded bulk storage tanks. The off loading area is designed to retain any spillage that might occur during the off loading process.

Caustic soda is used for the regeneration of anion exchangers in the ion exchange process for demineralised water production.

Caustic soda used for the demineralised water production process (anion regeneration) will be disposed following neutralisation with sulphuric acid (cation regeneration). This implies that almost all the caustic used for demineralised water production will be as sodium sulphate in the end state.

3.1.11.5.  Lubricating oils

Lubricating oils are received in drums / mini containers and bulk tankers. The oil is either stored in the bunded bulk storage tanks or under roof in the Oil Store.

Used or dirty oils will be stored in and area of suitable construction in order to prevent the contamination of soil. All used / dirty lubricating oil will be recycled through a reputable recycling contractor.

3.1.11.6.  Calcium chloride

Calcium chloride is received in 50kg bags and stored under roof in the water treatment plant chemical storage area.

Water from the Komati system is under saturated with respect to calcium carbonate and will thus corrode all galvanised steel, steel or asbestos cement pipe work. Stabilisation is done with a sufficiently soluble calcium salt in order to simplify the application process.

Almost all potable water produced at Duvha Power Station returns to the power station, which implies that the salts added during the potable production process, will be ultimately disposed off on the ash.  In the end state calcium chloride will maintain its composition as such.

3.1.11.7.  Liquid chlorine

Liquid chlorine is received in 907 kg cylinders and stored under roof in a suitably ventilated area. The chlorine cylinders are secured in accordance with the relevant safety requirements.

Chlorine is used to sterilise the potable water prior to reticulation. Treated sewage is also sterilised with chlorine prior to cascading to the station drains interception system.

Almost all the potable water produced at Duvha Power Station returns to the power station, which implies that the salts added during the potable production process will be ultimately disposed off on the ash. The end state of the chlorine used in the process are as an un-quantifiable group of salts which could include sodium chloride, magnesium chloride, halogenated methane’s and chloro-amines.

3.1.12 Water balance

Table 3 1.12 a) Basis for calculation

| Parameter | Value | Unit |
| --- | --- | --- |
| Load factor * | 75 | % |
| Thermal Efficiency | 35 | % |
| Ash Content of Coal (as received basis) | 27 | % |
| Coal burn rate | 463 | T/GW Sent Out |
| Moisture content of ash (% wet basis) | 58 | % |
| Moisture content of ash(% dry basis) | 38 | % |
| Average ash dump pool size | 100 | ha |
| Active ash disposal area | 245.69 | ha |
| Ash dump runoff area (catchment) | 481.6 | ha |
| Runoff factor for Ash Dump area | 20 | % |
| Average annual precipitation | 680 | mm |
| Pond Evaporation | 1292 | mm per annum |
| Mean annual evaporation from ash phase | 1034 | mm per annum |
| Cold lime softening process availability | 100 | % |

3.1.12 (b) Description / discussion of the water balance (including ‘Saltman’

spreadsheet:

The water balance for Duvha Power Station was developed as a live spreadsheet model that can provide real time balance for any possible scenario. The balances included in the report reflect outcomes bases on the annual average climatic conditions with rainfall and load factors as the only variables.

For the development of the water balance, the following aspects were included as variable inputs:

- Historical data as recorded in the STEP (thermal performance) reports

- Storm water gains and evaporation losses in accordance with WRC data for weather stations in the close proximity of Duvha Power Station

- Evaporation losses from coal and ash were adjusted in line with Eskom experience

- The current worst quality raw water from the Komati system

- Cooling water alkalinity control with sulphuric acid and lime treatment

- Maximum recycling

- Management of the station drains in order to eliminate spent regenerants thus allowing recovery of drains to the cooling water systems

- All effluents cascade to the ash water system and are consumed through evaporation and interstitial hold while a small volume might migrate to the ground water system.

- All station drains cascade to the station drains interception and recovery systems and are recovered to the east cooling water system

The impacts of any obvious or expected variation in Water Management variables are evaluated by employing the purposely-compiled “Saltman” computer spreadsheet programme. Findings from this modelling and the “Occurrence Reporting and Investigation System” database drive the Technical Planning Process (Budgeting) for the Water Management section. Typical aspects of water management that can be modelled using this tool are:

- Effluent sink capacity for any given operating condition such as load factor and

coal quality variations.

- Cooling system effluent volumes (Blow-downs) generated for any given

operating condition and raw water quality variation.

- Theoretical water balances for any specified window period while taking

cognisance of storm water gains in clean and dirty drainage areas as well as

load, coal and water quality variations.

- Verification of the accuracy flow metering equipment by predicting a

theoretical water consumption rate.

- Speciation to aid in the interpretation of the chemistry of the different streams

of water recovered to the cooling water systems.

- Salt loads on the ash for any given water quality, coal quality and power station

load variation.

- Quantification of tower evaporation, drift and windage losses. These flows can

normally not be quantified through metering due to a magnitude of other losses

from the cooling systems.

- Where applicable can cost adding the necessary inputs generates outputs.

- Desalination requirements and soda ash dosing needs can also be calculated by

following the instructions provided in the applicable cells.

3.1.12 (c).  Water flow Diagrams:

i.  Raw Water Intake, Storage and reticulation:

ii. Demineralised water production and reticulation process diagram:

- Potable water production and reticulation process diagram:

- Station Potable and Demineralised water reticulation system diagram

- Cooling water systems diagram:

- Waste Disposal System:

- Sewage Works:

3.1.13.  Mine Water Recovery:

Duvha Power Station is one of Eskom’s large power stations employing fossil fuel for combustion and wet cooling to dissipate the waste heat.  Duvha Power Station evaporates approximately 129Ml of water per day water at maximum production capacity. This water is supplied from the Komati Government Water Scheme. The Komati system is currently under pressure to supply all the users relying on the scheme. This is essentially due to the pollution of the Witbank Dam that could have elevated the stress.

Duvha Power Station imports approximately 7350kg / day of alkalinity (as CaCO3) to the cooling water systems. (129Ml X 45mgk-1 as CaCO3). This alkalinity was previously neutralised with sulphuric acid which represented a sulphate load of approximately 6900 kg / day of sulphate which ultimately had to be disposed of on the ash. This together with HOH (H+ Cation and OH- Anion) operation of the Condensate Polishing Plant, sulphate from the Boiler Make-up Plant regeneration and natural sulphate in the raw water represents the total sulphate load to the ash dams (dumps).

Improvements in water treatment processes over the last couple of years have eliminated the disposal of approximately 1000kg per day of soluble sulphates (Na2SO4) in the form of spent regenerants. Employing new technology ion exchange resins, which allowed Eskom to reduce the chemicals used in the regeneration process while operation of the Condensate Polishing resins in the Ammonex cycle, did this. These optimisation activities have lowered effluent volumes and mobile sulphates (Na2SO4) by as much as 75%, while low mobility sulphate (CaSO4) was reduced by approximately 70% by the introduction of the cold lime softening process for cooling water treatment. Incoming bicarbonates are precipitated as calcium carbonate and magnesium hydroxide in the cold lime softening process. Both these precipitates will remain sparingly soluble in the ash water as result of the hydroxide concentration (alkaline conditions) of the ash water.

All these optimisation activities have reduced the effluent volume and the concentration of sulphates in the effluent stream disposed of on the ash.

3.1.11. (a)  Rationale with respect to the cooling water and ash water chemistry

Duvha Power Station is fed with coal from the Middelburg Mining Services. Following the combustion, the ash from the mentioned coal contains:

| Silica as SiO2 | Calcium as CaO | Aluminium as Al2O3 |
| --- | --- | --- |
| 52.7% | 4.4% | 28.6% |

The maximum coal burned per day is approximately 38300 tons producing 10350 tons of ash per day with a theoretical CaO yield of approximately 450 tons per day. The calcium oxide (CaO) hydrolyse following contact with water in accordance with the following equation:

CaO   +   H2O   (   Ca(OH)2

The lime that forms in this reaction provides the alkaline conditions that dissolves aluminium as Al(OH)3. In contrast with other metals the solubility of the Aluminium hydroxide increases with increase in pH and at a pH of 11.6 to 12.0 conditions are favourable for the precipitation of Ettringite.

The lime further provides the alkaline conditions, which allows for the precipitation of the magnesium associated with sulphate in accordance with the following reaction:

MgSO4   +   Ca(OH)2   (   Mg(OH)2   +   CaSO4

This reaction further benefits the precipitation of Ettringite and Calcium sulphate as can be seen by the following:

6Ca2+ + 3SO42- + 2Al(OH)3 + 37H2O ( 3CaO.3CaSO4.Al2O3.31H2O + 6H3O+

The salinity of the water emanating from the Middelburg mines is mainly as result of sulphates of calcium and magnesium and could therefore be used for ash disposal provided that the recovery to the power station is a controlled process.

The normal upper limit for calcium and sulphate concentration in the absence of an inhibitor is expressed by:

[Ca2+] X [SO42-] = 500 000

This upper limit will be exceeded by approximately 2.6 times following the introduction of the mine water and calcium sulphate will also precipitate (as CaSO4) within the ash, thus further lowering the main contaminant of the mine water. Both calcium sulphate and Ettringite will remain sparingly soluble within the ash provided that the prerequisites spelled out below are maintained. The stability / solubility of these two precipitates beyond closure of the ash dump will be ensured by the pozzalanic properties of the ash and the low water penetration of the ash following rehabilitation (topsoil and vegetation) of the ash dam (dump).

The only prerequisites for recovering this water to the ash water systems is that:

- The mine water will always be neutralised with lime prior to recovery to the power station.

- The pH of the ash water system will not be allowed to drop below 11.6.

Introduction of the ash water will be in the ash distribution box to allow for the precipitation to take place in the ash rather than in dams, pumps or pipe work.

3.1.13.1.  An Evaluation on the need for the use of mine water from Middelburg South

Mine:

Duvha Power Station with the change to lime treatment and improved reuse of water has created a situation where it has a deficit over the effluent sink i.e. it can introduce water of a poorer quality into its water management to serve the needs of the ashing system and it’s ancillary systems.  The scope of this investigation included an assessment into the use of mine water from the nearby tied colliery (Middelburg South).  The mine water is of poor quality and is essentially contaminated with sulphates of magnesium and calcium. These salts could be precipitated in the ash dams through a natural ettringite process provided that the introduction of the mine water is at the ash dams and is controlled by maintaining a high pH in the ash water.

The Saltman Water Management Model was used to model a few likely scenarios calculating the shortfall in the effluent sink. This shortfall would then be supplemented with mine water.  An average raw water quality was used with different annual precipitation rates to model the expected shortfalls in the effluent sink.

The following scenarios were considered when determining the amount of mine water to be recovered:

- i.  Using average climatic and water quality (mean annual precipitation of 700 mm)

conditions and Komati water only;

ii. Using an annual precipitation of 1000 mm and average raw water quality conditions

and use of Komati water only;

iii. Using an annual precipitation of 400 mm and average raw water quality conditions

and use of Komati water only;

- iv. Using average climatic and water quality (mean annual precipitation of 700 mm)

conditions and using Komati water as well as Witbank Dam Water as well;

Table 3.1.13. (a):

| Scenario | Ml per annum shortfall |
| --- | --- |
| i | 2314 |
| ii | 1127 |
| iii | 3501 |
| iv | 1538 |

Table 3.1.13 (b): Typical water qualities:

| Parameter | Units | Raw water | Witbank Dam Water | Mine Water |
| --- | --- | --- | --- | --- |
| PH |  | 7.8 | 8.0 | 7.8 |
| Electrical conductivity | µScm-1 | 134 | 742 | 221 |
| Calcium as CaCO3 | mgkg-1 | 27 | 142.5 | 320 |
| Magnesium as CaCO3 | mgkg-1 | 29.5 | 150.2 | 244 |
| P Alkalinity as CaCO3 | mgkg-1 | Nil |  | 3.1 |
| M Alkalinity as CaCO3 | mgkg-1 | 50.6 | 105 | 71.4 |
| CaCO3 PP @ 25o C | mgkg-1 | - 19.3 | -21.5 | -7.2 |
| Sodium | mgkg-1 | 5.6 | 40.8 | 53.4 |
| Potassium | mgkg-1 | 1.04 | 7.8 | 13.0 |
| Chloride | mgkg-1 | 3.5 | 23.7 | 20.0 |
| Sulphate | mgkg-1 | 8.21 | 377.8 | 1366.2 |
| Silica as SiO2 | mgkg-1 | 7.3 |  | 0.44 |

3.2. Ground water management

Duvha Power Station is one of Eskom’s newer power stations and commenced power generation in 1981.  A groundwater monitoring system was installed in 1989. Since then, several reports have summarised findings on groundwater quality.

Waste facilities that exist at Duvha Power Station, which could potentially pollute groundwater resources, are:

- Ash disposal.

- Coal stockpiling.

- Solid water disposal.

- Sewage works.

Of these, ash disposal and the coal stockyard have, in view of the scale of operations, the greatest potential to pollute groundwater.

For the past eight years, monitoring has been of a quantitative nature. No predictive capability was available to predict possible migration of groundwater pollution plumes. At the older power stations, it has been found that, after a number of years, groundwater resources inevitably become polluted. It has therefore become necessary to re-evaluate the monitoring facilities at Duvha Power Station and to provide a predictive capability in terms of groundwater pollution migration. The currently investigation is therefore intended to:

- Process all existing information on groundwater quality at Duvha Power Station.

- Establish a geographic information system through which this information can be accessed in future.

- Investigate past trends and anomalies.

- Correct historic information where necessary.

- Conduct in-situ measurement of water quality within monitoring holes.

- Model potential pollution plume migration through ground and rock.

- Implement the geographic information system at the power station for future data entry and processing.

- Methodologies applied

This investigation (Hodgson) leans heavily on historic groundwater quality information at the power station. Eight years’ data are currently available which was used to calibrate the pollution migration model for the power station.

To supplement this information, several field and laboratory investigations were also conducted. Of these, the most important are in-situ measurements of the water chemistry in monitoring boreholes. This is the first time that measurements of this kind have been performed at Duvha Power Station.

Leaching tests on ash from the ash dam and ash from the power station, as well as coal from the stockyard were also conducted.

b) Locality and physiography

Figure 14: Duvha Power Station is located south-east of Witbank

Duvha Power Station is located south of the Witbank Dam,  at its closest point, the Witbank Dam is 1,5 km from the ash dam. The ashing facility comprises 480 ha. The coal stockyard is located close to the power station, covering an area of 26 ha. In the past, limited amounts of solid waste have been disposed of in the area (W) north of the power station.

In the event that the groundwater beneath the coal stockyard does become polluted, modelling has shown that most of the contaminated groundwater will migrate towards the pan, east of the stockyard. This pan has already been contaminated by the disposal of power station effluent in it. Migration of pollution groundwater from the coal stockyard is also possible to the west and east. Modelling shows that this movement will be very slow and will have no impact on existing water users.

c).  Historic monitoring and results

Groundwater monitoring has been conducted by the power station since the installation of the boreholes in 1989. Localities of monitoring boreholes are shown in Figure 3. Time series plots of the main constituents are provided in Figures 4 – 12.

Figure 3. Locality plan showing positions of monitoring boreholes.

d).  In-situ ground water qualities

In-situ groundwater quality in the monitoring boreholes was measured as part of this investigation. The advantages of doing this rather than water sampling are:

- The exact water chemistry, as it occurs in the ground, is measured.

- A complete record of the vertical variation in water chemistry is obtained.

The results from these measurements are show in Figures 15 – 21.

Figure 15. Geology and in-situ water chemistry at Borehole B1

The following conclusions are drawn from Figure 14 and the water chemistry for this borehole:

- The shallow water table suggests a water source that recharges the groundwater. This can only be from the ash dam.

- The electical conductivity of historic water samples ranges from 18 – 45 mS/m. The range of values for the specific conductance graphs is  28 – 44 mS/m. The latter indicates stratification in water quality. In view of the stratified nature of groundwater at this borehole, sampling here should consistently be from the same depth.  It is suggested that sampling should always be from from a depth of 13 m, which corresponds to the major water intersection in this borehole.

- The lower electrical conductivity in the top portion of the borehole is ascribed to recharge from rain water.

- It is known that high pH-values from ashing operations do not propagate through groundwater and high pH-values have not been expected at this borehole. The pH-values here range from 5,8 – 6,5. These are normal for groundwater in the area and also for this rock type, namely felsite.

- The rapid decrease in the dissolved oxygen content from 2,3 mg/L to almost zero at a depth of 7 m, suggests recharge from surface water and thus dilution.

Figure 16. Geology and in-situ water chemistry at Borehole B2

The following conclusions are drawn from Figure 15 and the water chemistry for this borehole:

- The effect of dilution from rain water manifests clearly in the top portion of the specific conductance curve, down to a depth of  6 m.

- Conditions are reducing, which could be the result of the mashy nature of the soil around the borehole. The low oxygen content in the water confirms this.

- The felsite is deeply weathered at this locality and flow of groundwater is possible down to a depth of 19 m.

- Historic electrical conductivity has been rising steadily from around 12 mS/m to slightly above 30 mS/m over the last eight years. This correlates well with the specific conductance (electrical conductivity at 25oC) of 37 mS/m measured in the field for the deeper portion of the aquifer.

- It is recommended that future sampling should be done at a delth of 13 m, where the transition between the very weathered and weathered felsite takes place.

- There is no doubt that the deeper water within this borehole also derives from the ashing operations. The relatively low salt content of the water in this borehole demonstrates the extent to which the weathered felsite and soil is capable of filtering particularly the bi-valent ions from the water.

Figure 17. Geology and in-situ water chemistry at Borehole B4

This borehole is located immediately below the dam wall of the ash water return dam. The following conclusions are drawn from Figure 16 and the water chemistry for this borehole:

- The specific conductance down the borehole is relatively constant at a value of 84 – 88 mS/m. This corresponds well with the historic values of around 80 mS/m measured since 1995.

- Sulphate levels in particular are elevated. Most other macro constituents are also slightly elevated.

- Although water was first intersected in the borehole at a depth of 3 m, groundwater is capable of seeping through the weathered dolerite down to a depth of 10 m.

- The dissolved oxygen content is low and conditions within the borehole are reducing.

- The pH of the groundwater ranges from 6,7 – 7,0. This demonstrates that the high pH of the ash water (>11,0) is not transferred through the aquifer and that the ash dam poses no threat in terms of pH to the environment beyond the dam.

- The ideal sampling depth for this borehole is 8 m, just below the casing and on the contact between the weathered and slightly weathered dolerite.

Figure 18. Geology and in-situ water chemistry at Borehole B5

The following conclusions are drawn from Figure 17 and the water chemistry for this borehole:

- The borehole has been drilled in felsite. Weathering extends down to 8,5 m.

- Pollution at this borehole is minimal, but a slow rise in specific constituents has been observed over the past few years.

- The specific conductance of the water in the borehole is very constant, ranging from 33 – 34 mS/m. This supports historic information from laboratory measurements during the period 1994 – 1997.

- The pH-values range between 7,4 – 6,8, decreasing down the hole. This again confirms that the high pH-values normally found in ash water do not propagate through the aquifer.

- The increase in dissolved oxygen from a depth of 7m cannot currently be explained. The redox curve shows a similar trend, switching from reducing conditions at surface to oxidising conditions deeper down. There seems to be a correlation between the depth of casing and response of the oxygen and redow probes.

- It is recommended that future sampling should be done just below the casing, at a depth of 8,5 m.

Figure 19. Geology and in-situ water chemistry at Borehole B6

The following conclusions are drawn from Figure 18 and the water chemistry for this borehole:

- The geology at this location is totally different from that at the ash dam. Karoo rocks are present over the whole depth of the borehole. Weathering extends down to 8 m. From deeper than 20 m, Dwyka tillite is present. The latter is totally impermeable to groundwater movement and pollution will not be able to penetrate this layer in the event that the upper aquifer should become polluted.

- Water was intersected in this borehole at the transition between the weathered material and the upper Karoo shale. The specific conductance of the water in the borehole is very low, decreasing from 9,5 – 8,1 mS/m from top to bottom. This corresponds well with the electrical conductivity historically measured for water samples.

- The water occurs under reducing conditions and the oxygen content is low. This suggests that no active recharge from rain water occurs in this area.

- The pH ranges from 6,9 down to 6,6, which is typical for natural groundwater occuring in aquifers of this area.

- Sampling at this locality should be done at 8,0 metres below surface, which is at the transition from weathered sediments to the shale.

Figure 20. Geology and in-situ water chemistry at Borehole B7

The following conclusions are drawn from Figure 20 and the water chemistry for this borehole:

- Two distinct horizons of water quality are present in this borehole. This is confirmed by the specific conductance, redox potential and the dissolve oxygen profiles. These horisons correlate well with the geology.

- Historic electrical conductivities are similar to that measured in the upper portion of the borehole. This is the zone in which pollution should be noticed first. The conclusion is that this borehole is still unpolluted. The increase in salinity in the deeper portion of the borehole seems to correlate with the Dwyka tillite. It is suggested that the increase in salinity is due to stagnation of the borehole water within this horizon and not due to pollution from the coal stockyard.

- Sampling of water in this borehole should be at 19 m. This depth is below the casing and in the coal seam, where water was intersected during the drilling of the borehole.

Figure 21. Geology and in-situ water chemistry at Borehole B8

The following conclusions are drawn from Figure 21 and the water chemistry for this borehole:

- The water quality in this borehole is exceptionally pure with a specific conductance ranging from 3 – 7. This corresponds well with historic values over the last two years, as measured in the laboratory.

- The relatively low pH of 5,1 – 5,4, coupled with an oxidation potential between 170 – 200 is typical of natural groundwater within weathered sandstones. The oxygen potential of 6 mg/L, decreasing to 2 mg/L at a depth of 10 m suggests that active recharge from rain water is occurring. The thin soil cover of a sandy nature is probably the main contributing factor for this recharge.

- Sampling of water from this borehole should continue at a depth of 13 m, which is below the casing and corresponds to the depth at which water was intersected in the borehole.

In-situ groundwater quality in the monitoring boreholes was measured as part of this investigation. The advantages of doing this, rather than water sampling, are:

- The exact water chemistry, as it occurs in the ground, is measured.

- A complete record of the vertical variation in water chemistry is obtained.

# 3.2.1.  Groundwater modelling pollution transport

# Introduction to groundwater pollution modelling

The model for simulating groundwater pollution transport at Duvha Power Station has been based on the finite element method.

The first step in constructing such a model is the subdivision of the area to be modelled into blocks (elements) where the characteristics are similar. Considerations for subdivision of the Duvha area were typically:

- The surface geometry, such as topography, streams and positions of waste management facilities.

- The hydraulic characteristics of the underlying aquifer.

- Current groundwater quality distribution.

The simulated area constitutes an area of 6 000 x 9 000 m. It covers all the waste disposal facilities, as well as the streams, north and south of the complex. The area was subdivided into 6565 elements, as shown in Figure 22.

As can be seen from the finite element network, a greater density of elements has been introduced in areas where more detailed answers are required. Typically, these areas are around waste management facilities. This includes the ash dam, coal stockyard, ash water return dam and pans.

## 3.2.1.2. Governing equations for modelling pollution transport

To predict pollution movement across the area in question, several sets of equations are to be solved. These are for instance:

- The interpolation of groundwater levels across the whole of the area using Bayesian interpolation (Figure 22).

Figures 22. Finite element network (left) and groundwater level contours (right) used for pollution plume modelling at Duvha Power Station.

- The solution of the groundwater flow equation, which is a second order partial differential equation for the whole of the area, thus determining groundwater gradients, seepage velocity and the response of the aquifer due to external influences such as pumpage and recharge from rainfall. This equation may be written as follows:

T(2h/x2)  +  T(2h/y2)  +  T(2h/z2)  =  Sh/t  -  Q

where

S 	= 	Storage coefficient

h/t	= 	Change in hydraulic head with time (m/d)

T	= 	Transmissivity (m2/d)

(2h/x2), (2h/y2), (2h/z2) 	= Flux directions

Q	= 	Abstraction/Recharge (m3/d)

This equation describes the three-dimensional flow of groundwater through the substrata, calculating the water-table response. The equation may be solved analytically for simple problems, though for the power station problem, piece-wise approximation of the equation is usually obtained through the finite element method, because of the complexity of the problem.

Once the water-level distribution is available over the whole of the area in question, seepage velocity and directions can be calculated, using the following equation:

v 	= 	k(h/l)/n

where

v		=	Seepage velocity (m/d)

k		=	Hydraulic conductivity (m/d)

n		=	Effective porosity (%)

h/l		=	Groundwater gradient (m/m)

On the basis of the hydraulic gradients and flow velocities, movement of pollutants through the aquifer may be calculated next. The mass transport equation is of the following type in its one-dimensional form:

Dx(2c/x2)  - Vx(c/x)  =  R(c/t)

where

Dx		=	Dispersion coefficient in the x-direction (m2/d)

2c/x2		=	Flux direction

Vx		=	Seepage velocity (m/d)

c/x		=	Change in concentration with distance

R		=	Retardation coefficient

c/t		=	Change in concentration with time (decay)

This equation may be expanded into two or three dimensions, depending on requirements.

It is clear from the above that coupling of the mass transport equation with the flow equation becomes rather complex in the real life situation, because of the additional variables present. The dispersive properties of the soil and aquifer, degree of convection in these systems, as well as chemical reactions that take place, must be known before the mass transport equation can be applied successfully.

Certain simplifying assumptions may be made with respect to the problem to be modelled, without jeopardising the value of the model. Examples are:

The vertical dimension in the equations may be eliminated. Most of the flow takes place within the weathered upper 10 - 15 m. Laterally, the aquifer at Duvha Power Station extends over several kilometres, up to the nearest streams and beyond. The vertical dimension is therefore very small in comparison to the lateral dimensions. The time for the pollutant to travel vertically into the aquifer is therefore negligibly small in comparison to the time for the pollutant to disperse regionally. Elimination of the vertical dimension in the problem will therefore have no effect on the arrival time for the pollutant at some distant point. Elimination of the vertical dimension from the simulation considerably reduces the complexity and computational effort.

For modelling purposes, chemical constituents in the ashing environment may be grouped into various categories, depending on their reactivity, attenuation and decay properties. As an example, calcium in ash water will precipitate as calcium carbonate when carbon dioxide enters into the water. In terms of mass transport modelling, constituents that precipitate need not be modelled, because they will not be available for transport. Monitoring has also shown that alkalinity does not move. A typical constituent that is likely to persist within a power station ashing environment is sodium. Sodium is introduced into the fly ash through effluent from the demineralisation plant. At modern power stations, about 300 kg sodium is used daily and the effluent is disposed of in the ashing system. In theory, sodium is therefore a convenient constituent to study the movement of pollution from an ash dam, because:

- Sodium is readily soluble and will not precipitate in the ashing system or the aquifer.

- Sodium does not adsorb readily onto clay particles in the soil or the aquifer.

- Sodium does not decay with time.

In the Duvha situation, all of the monitoring boreholes have sodium concentrations that are less than the recommended RSA drinking-water standards. It has, however, been rising steadily in the area below the ash dam and ash water return dam over the past four years. If sodium concentrations are to be modelled, they should be modelled without any attenuation.

Apart from sodium, sulphate may also be considered. It is introduced into the system either through oxidation of sulphides in the coal stockyard, or though demineralisation effluent which is disposed of in the ashing system. Sulphate usually has an attenuation factor in the order of 10, which should be considered during modelling.

Most heavy metals (except manganese) will not mobilise because of the high pH of the ash water and the general neutral pH-character of the groundwater in the power station area.

The complexity of the problem to simulate mass transport through the groundwater system has therefore, through logical reasoning, been reduced significantly. It should, however, be emphasised that even in its simplest form, mass transport simulation is still complicated, because of the many other hydraulic variables that partake in the solution. Some of these aspects need to be discussed before the results from this modelling exercise are demonstrated.

## 3.2.1.3.  Hydraulic variables and constraints

Variables and constraints that act upon the movement of pollutants through an aquifer are typically:

- The transmissivity and hydraulic conductivity of the underlying strata.

- The storativity and effective porosity of the underlying strata.

- The hydraulic gradient, dispersion and convection characteristics of the aquifer.

- Boundaries such as dolerite dykes, catchment and surface.

- Other sources of water in the area such as streams, pans, dams and lakes.

Sinks within the area where groundwater is abstracted or naturally emanates on surface in the form of fountains.

### 3.2.1.4. Transmissivity and Hydraulic Conductivity

No pumping tests have been performed at the monitoring boreholes. The borehole logs, however, indicate low-yielding characteristics for the aquifer. Records show that the average blowout yield is in the order of 0,5 L/sec, which translates into a hydraulic conductivity of 0,2 - 0,01 m/d, with an average value of 0,1 m/d.

### Storativity and Effective Porosity

Pumping test methods has tested the storage coefficient of aquifers Witbank/Highveld Coalfields, and an average value of 10-3 can be assumed for the fractured aquifer. The reason for this relatively low storativity values lies in the fact that only a small proportion of the pores and fractures in the fresh aquifer partake in water flow. In the upper, weathered aquifer the effective porosity is an order higher and a value of 10-2 can be achieved. This higher value is due to the fact that almost all the calcium that normally binds the sedimentary grains together, has been leached from this horizon. Water can therefore permeate through the weathered matrix.

### Regional Water-table Gradient, Dispersion and Convection

As a start, for the determination of the regional water-table gradient, measurement of static water levels in the monitoring boreholes is necessary. Since the regional water-table gradient within the Arnot area is controlled by the surface topography, the latter may be used as a controlling factor in a Bayesian estimation model to infer groundwater levels in areas where monitoring boreholes are not available. This provides a well-defined distribution of water tables, which, in turn, is essential for calculating groundwater flow directions and velocities.

### Boundaries

Groundwater boundaries exist in various forms in nature and have to be accounted for in models. Typical boundaries are dolerite dykes and sills, which may act as impermeable barriers in the transverse direction or as conductive zones along intrusive contacts. Close to surface, dolerite weathers and water permeates easily through it. Other boundaries are, for instance, catchment boundaries, where a change in the direction of the water-table gradient may occur. Surface boundaries, above which the groundwater level cannot rise without decanting, should also be considered. Boundaries of these types can be accommodated in flow and mass transport models, with the prerequisite that knowledge about these boundaries must be available for the areas in question.

### Sources of Water

Sources of water may be incorporated in groundwater computer models. They may be in the form of constant or specified flux sources. A good example of such a source in the modelling exercise to follow, is the constant water supply at the ash dam. Another source is the rainfall that recharges the aquifer.

### Sinks

Points where water is taken from the system, such as boreholes, drains or fountains, are referred to as sinks. The finite element model to be used in this exercise can accommodate sinks at any position in the model and the effect of water abstraction or water loss at these points can be simulated. This facility may be used to predict the response of a pollution plume during groundwater abstraction. Currently, there are no users of groundwater in the area that could impact on the movement of pollutants through the aquifer.

## 3.2.2.  Results from finite element simulation

### Groundwater contours

The calculation of the distribution of groundwater levels in the area was carried out by using existing information at boreholes and waste management facilities, and relating this information to surface topographic information by using the Bayesian technique. The result is a contour map (Figure 22), showing groundwater gradients in the direction of the streams. Seeing that groundwater flow occurs from areas of higher potential to lower potential, it can be inferred from the contours that pollution from the power station area will be able to disperse to the northeast, west, south and southwest of the station.

### Flow vectors

Using the contour information as input, groundwater flow directions and seepage velocities have been calculated next. This is done for each of the elements in the finite element network. The results of these calculations have been plotted in Figure 22, using arrows to indicate the directions and velocity of flow. The lengths of the arrows are proportional to the seepage velocity at each point. It is clear, for instance, that seepage velocity away from the ash dam has the potential to be high, because of the significant water-level differences between the water in the dam and the groundwater northeast of the dam. It is furthermore clear that the groundwater seepage velocity in the area underneath the power plant and coal stockyard is relatively low. Any pollution in this area will take a long time to migrate away from these facilities. The greater density of arrows in specific areas, such as for instance in the area around the ash dam is due to the greater detail of the finite element network in this area and it does not signify more concentrated or faster seepage.

### Initial concentrations

The concentrations of pollution are indicated in Figure 23 as 100 mg/L at all sites where pollution of groundwater may occur. These values should be read as percentages. In other words, 100% concentration will be different for each of the sites. By indicating concentrations in this way, rather than absolute values, any concentration can be accommodated.

Figure 23. Locations of potential pollution sources in relation to the Witbank Dam.

### Local and regional impact

Simulation of the pollution movement from these localities was the next step. It has been assumed in the simulation that the power station will continue to operate for another 30 years. Thereafter, the power station terrain will be rehabilitated, removing all sources of groundwater pollution except for the ash dam. The ash dam will continue to leach because of rainfall on top of the dam. Simulations were done for a total period of 100 years. The results, not allowing for attenuation, are displayed in Figures 24 - 28. Simulation times are 5, 10, 30, 60 and 100 years. The conclusions for the operative phase of the power station follow:

- Pollution plume propagation rates indicated are without attenuation. This would be valid for sodium and chloride. Sulphate is attenuated by a factor of 10- and therefore the 10-year contour diagram (Figure 26) depicts a 100-year simulation for sulphate.

- It has been assumed that the aquifer below the ash dam, coal stockyard and pan has already been contaminated. This is not necessarily the case, as pointed out earlier in this report. The predictions are therefore only valid from the date when pollution is first present in the aquifer. At the ash dam, this has been the case since the inception of the facility. At the coal stockyard, the boreholes between the stockyard and the pan are still unpolluted. No information is available on groundwater quality below the stockyard itself.

Figure 24. Flow vectors (left) and pollution plume percentages 5 years after the pollution has entered into the aquifer.

Figure 25. Flow vectors (left) and pollution plume percentages 10 years after the pollution has entered into the aquifer.

Figure 26. Flow vectors (left) and pollution plume percentages 30 years after the pollution has entered into the aquifer.

Figure 27. Flow vectors (left) and pollution plume percentages 60 years after the pollution has entered into the aquifer. The coal stockyard and pan have now been rehabilitated for 30 years.

Figure 28. Flow vectors (left) and pollution plume percentages 100 years after the pollution has entered into the aquifer. The coal stockyard and pan have now been rehabilitated for 60 years

- The movement of pollution in the aquifer at Duvha Power Station is very slow. Movement occurs dominantly to the northwest, west and south of the power station.

- At the ash dam, the trench along a portion of the northern perimeter of the dam effectively intercepts seepage from the dam by locally reversing the hydraulic gradient. Further to the northwest along the same portion of the dam, seepage propagates to the northwest and west, in the absence of the trench in these parts. It should, however, be emphasised that this propagation is, at least for the foreseeable future, optimistic since the ash dam has not reached its final height in these parts. In real life, propagation of the pollution plume to the west will be negligible until the ash dam has reached its full height.

- Propagation of the pollution plume at the coal stockyard occurs in all directions because of the topographic high on which the coal stockyard is located. It is currently not certain whether or not pollution from the stockyard has, in fact, reached the aquifer. At older power stations, such as Arnot and Hendrina, contamination of the aquifer has in fact occurred. Usually this took something in the order of 20 - 25 years for acidification and migration of sulphate across the unsaturated zone underneath the older facilities. At the newer facilities, the floor on which the coal has been deposited has been compacted very well and no information of seepage rate across this barrier is available. The pollution plume shown for the coal stockyard should therefore only be taken as indicative in terms of the directions of flow and also the relative concentrations in the various directions. In the event that pollution does reach the aquifer, most of the pollution, if any, is expected to migrate towards the pan. The latter is already contaminated by power station process water.

- Propagation of pollution from the pan next to the coal stockyard is also slow. The pan drains to the north into a vlei area. Significant pollution is not expected in the second pan because of the proven attenuation of sulphate within weathered strata of the Witbank Coalfields. If pollution does reach the second pan, this will surface and evaporate from here.

- The conclusion is drawn that the outputs from these simulations depict the worst case scenarios. Even so, no significant impact on the Witbank Dam or surrounding groundwater resources is shown. Monitoring should continue and only if deviations from that predicted by the model occur, should the model be updated.

# 3.2.3.  CONCLUSIONS

The following conclusions are drawn from this investigation:

- The waste management facilities at Duvha Power Station have now been equipped with groundwater monitoring facilities for eight years. During this time, no significant deterioration of groundwater or surface water resources has occurred from activities by the power station.

Ashing facilities

- Historically, the area north of the ash dam has been polluted, primarily by an increase in salinity and sulphate.

- To combat the spread of this pollution, the power station has installed a cut-off trench and planted eucalyptus trees.

- This has been successful and a marked improvement in the water quality of the upper aquifer has been noticed during the past five years.

- Modelling shows that pollution is unlikely to propagate significantly beyond the trench and trees.

- Water quality profiling within monitoring boreholes in this area suggests that deeper underflow of water from the ash dam may be present but until this has been proven and its potential impact quantified, no counteraction by the power station is necessary.

- The neutral pH-levels of groundwater within areas historically impacted upon by ash water are of significance. It is concluded that there is no danger of the pH of groundwater rising to uncontrollable levels. Even within 50 m of the ash water return dam, the pH of groundwater is between 6,7 – 7,0.

- It is expected that sodium levels will gradually increase in the area between the ash dam and the Witbank Dam. Sodium is mainly derived from demineralisation effluent that is disposed within the ash. Although a rise in the sodium concentrations in water is generally considered as undesirable, levels of sodium within the groundwater are currently still low (40 – 90 mg/L). Even so, the latter compares unfavourably with the original sodium levels of 2 – 15 mg/L within the aquifer. A close watch on future sodium concentrations is suggested.

- Chloride levels show similar elevated levels. Current values range between 30 – 70 mg/L.

Coal stockyard

- No pollution of groundwater resources has been detected in any of the five boreholes at this facility.

- It was therefore difficult to calibrate the model for the coal stockyard.

- For calibration purposes, pollution of the aquifer at some stage in the future had to be assumed.

- The model therefore predicts movement of contaminated groundwater from the coal stockyard after pollution has occurred. Based on information at older power stations, pollution at coal stockyards normally does not occur in less than 20 years.

- In the event that the groundwater beneath the coal stockyard does become polluted, modelling has shown that most of the contaminated groundwater will migrate towards the pan, east of the stockyard. This pan has already been contaminated by the disposal of power station effluent in it. Migration of pollution groundwater from the coal stockyard is also possible to the west and east. Modelling shows that this movement will be very slow and will have no impact on existing water users.

- Sulphate pollution from the coal stockyard will only really become a problem when the pH of the leachate drops. This is not likely to happen at a well-managed coal stockyard because the natural base potential of the coal will have to be depleted before this could occur. At Duvha Power Station, the average base potential of the coal is 15 kg/t, whereas the acid potential is 25 kg/t. In the event that the base potential becomes exhausted due to pyrite oxidation, the coal on the stockyard can be replaced systematically.

The complete groundwater quality and pollution plume modelling reports is attached as appendix A.

- References

1.  Hanekom, DJ. Naidoo, N. 2002. An evaluation of a need for the use of mine water from

Middelburg South Mine by Duvha Power Station.

- Lazik, D. Janovsky, A. Schreiter, P.  2000.  Germany.  Geochemical and Hydraulic

behaviour of ash posts for mechanical stabilisation of acid mine dumps.

3.  Van Blerk, P.  2002.  Duvha Power Station Water Management Plan.

4.   Hodgson, F. March 1998. Groundwater Quality and Pollution Plume Modelling at

Duvha Power Station.

5.  Jones & Wagener, Consulting Civil Engineers.  Report No. UC13/99/6106. July 1999.

Middelburg Mine Services (PTY) LTD Driefontein Dam Operations and Maintenance

Manual.

6.  ECosoft (PTY) LTD. August 2002.  Report 08/02/0023.DUVHA POWER STATION

# ASH DAMOPERATIONS AND MAINTENANCE MANUAL.

7.  Midgley, D.C. Pitman, W.V, Middleton, B.J. WRC Report No.: 298/1.1/94.  Water

Research Commission Surface Water Resources of South Africa, Volume 1, 1st Edition,

1994.

8. Midgley, D.C. Pitman, W.V, Middleton, B.J. WRC Report No.: 298/1.2/94.  Water

Research Commission Surface Water Resources of South Africa, Volume 1, 1st Edition,

1994.

- Hanekom, D.J. September 2003.  Eskom – Chemistry Standard for Cooling Water.

- Van Blerk, P. 2002. Duvha Power Station. Personal Communications and data required.

- South African Weather Services.

Appendix A

Appendix B

Appendix C

Mine Water Recovery Scenarios

- i.  Using average climatic and water quality (mean annual precipitation of 700 mm)

conditions and Komati water only.

| CALCULATED WATER BALANCE WITH LIME TREATMENT |  |  |
| --- | --- | --- |
| Window period | Days | 365 |
| Effluent sink |  |  |
| Absorption on ash | Ml | 1870.136 |
| Evaporation during coarse ash quenching | Ml | 192.681 |
| Evaporation from ashing system | Ml | 4030.615 |
| Ash water recovered to cooling water system | Ml | 0.000 |
| Seepage to ground water from dirty areas | Ml | 142.350 |
| Total sink capacity | Ml | 6235.781 |
| Effluents |  |  |
| Cooling water blow downs lime alkalinity control | Ml | 691.350 |
| Additional blow-downs to control calcium sulphate | Ml | 209.400 |
| Cooling water sludge (Included in calculated cooling water blowdowns) | Ml |  |
| Rain water ingress into ash system | Ml | 2768.070 |
| Regeneration effluents | Ml | 84.844 |
| Ash system gland sealing water (other than ash water and CCW) | Ml | 0.000 |
| Treated sewage to ash water system | Ml | 167.791 |
| Total effluents | Ml | 3921.455 |
| Effluent excess over sink | Ml | -2314.327 |
| Desalination requirement | Ml | 0.000 |
| Desalination plant brine | Ml | 0.000 |
| Cooling water cycles of concentration |  | 40.7 |
| Basis for calculation |  |  |
| Station load factor |  | 0.750 |
| Raw water supply from Witbank Dam | Ml for the period | 0.000 |
| Raw water supply from Grootdraai Dam | Ml for the period | 35427.740 |
| Rain fall | mm per annum | 700 |
| Pond / dam evaporation rate | mm per day | 4.820 |
| Cooling tower evaporation rate | Ml / GWh so | 1.563 |
| As received ash content of coal | % | 27.00 |
| Coal burn rate | T / Gwh so | 463 |
| Cooling water calcium specification as CaCO3 | mgkg-1 | 400 |
| Cooling water sulphate specification | mgkg-1 | 1000 |
| Cooling water alkalinity specification as CaCO3 | mgkg-1 | 120 |
| Average demineralised water consumption | m3 / Gwh so | 40.00 |

ii.  Using an annual precipitation of 1000 mm and average raw water quality conditions

and use of Komati water only;

| CALCULATED WATER BALANCE WITH LIME TREATMENT |  |  |
| --- | --- | --- |
| Window period | Days | 365 |
| Effluent sink |  |  |
| Absorption on ash | Ml | 1870.136 |
| Evaporation during coarse ash quenching | Ml | 192.681 |
| Evaporation from ashing system | Ml | 4030.615 |
| Ash water recovered to cooling water system | Ml | 0.000 |
| Seepage to ground water from dirty areas | Ml | 142.350 |
| Total sink capacity | Ml | 6235.781 |
| Effluents |  |  |
| Cooling water blow downs lime alkalinity control | Ml | 691.350 |
| Additional blow-downs to control calcium sulphate | Ml | 209.400 |
| Cooling water sludge (Included in calculated cooling water blowdowns) | Ml |  |
| Rain water ingress into ash system | Ml | 3955.004 |
| Regeneration effluents | Ml | 84.844 |
| Ash system gland sealing water (other than ash water and CCW) | Ml | 0.000 |
| Treated sewage to ash water system | Ml | 167.791 |
| Total effluents | Ml | 5108.389 |
| Effluent excess over sink | Ml | -1127.392 |
| Desalination requirement | Ml | 0.000 |
| Desalination plant brine | Ml | 0.000 |
| Cooling water cycles of concentration |  | 40.7 |
| Basis for calculation |  |  |
| Station load factor |  | 0.750 |
| Raw water supply from Witbank Dam | Ml for the period | 0.000 |
| Raw water supply from Grootdraai Dam | Ml for the period | 35427.740 |
| Rain fall | mm per annum | 1000 |
| Pond / dam evaporation rate | mm per day | 4.820 |
| Cooling tower evaporation rate | Ml / GWh so | 1.563 |
| As received ash content of coal | % | 27.00 |
| Coal burn rate | T / GWh so | 463 |
| Cooling water calcium specification as CaCO3 | mgkg-1 | 400 |
| Cooling water sulphate specification | mgkg-1 | 1000 |
| Cooling water alkalinity specification as CaCO3 | mgkg-1 | 120 |
| Average demineralised water consumption | m3 / GWh so | 40.00 |

iii. Using an annual precipitation of 400 mm and average raw water quality conditions

and use of Komati water only;

| CALCULATED WATER BALANCE WITH LIME TREATMENT |  |  |
| --- | --- | --- |
| Window period | Days | 365 |
| Effluent sink |  |  |
| Absorption on ash | Ml | 1870.136 |
| Evaporation during coarse ash quenching | Ml | 192.681 |
| Evaporation from ashing system | Ml | 4030.615 |
| Ash water recovered to cooling water system | Ml | 0.000 |
| Seepage to ground water from dirty areas | Ml | 142.350 |
| Total sink capacity | Ml | 6235.781 |
| Effluents |  |  |
| Cooling water blow downs lime alkalinity control | Ml | 691.350 |
| Additional blow-downs to control calcium sulphate | Ml | 209.400 |
| Cooling water sludge (Included in calculated cooling water blowdowns) | Ml |  |
| Rain water ingress into ash system | Ml | 1581.135 |
| Regeneration effluents | Ml | 84.844 |
| Ash system gland sealing water (other than ash water and CCW) | Ml | 0.000 |
| Treated sewage to ash water system | Ml | 167.791 |
| Total effluents | Ml | 2734.520 |
| Effluent excess over sink | Ml | -3501.261 |
| Desalination requirement | Ml | 0.000 |
| Desalination plant brine | Ml | 0.000 |
| Cooling water cycles of concentration |  | 40.7 |
| Basis for calculation |  |  |
| Station load factor |  | 0.750 |
| Raw water supply from Witbank Dam | Ml for the period | 0.000 |
| Raw water supply from Grootdraai Dam | Ml for the period | 35427.740 |
| Rain fall | mm per annum | 400 |
| Pond / dam evaporation rate | mm per day | 4.820 |
| Cooling tower evaporation rate | Ml / GWh so | 1.563 |
| As received ash content of coal | % | 27.00 |
| Coal burn rate | T / GWh so | 463 |
| Cooling water calcium specification as CaCO3 | mgkg-1 | 400 |
| Cooling water sulphate specification | mgkg-1 | 1000 |
| Cooling water alkalinity specification as CaCO3 | mgkg-1 | 120 |
| Average demineralised water consumption | m3 / GWh so | 40.00 |

- iv. Using average climatic and water quality (mean annual precipitation of 700 mm)

conditions and using Komati water as well as Witbank Dam Water as well;

| CALCULATED WATER BALANCE WITH LIME TREATMENT |  |  |
| --- | --- | --- |
| Window period | Days | 365 |
| Effluent sink |  |  |
| Absorption on ash | Ml | 1870.136 |
| Evaporation during coarse ash quenching | Ml | 192.681 |
| Evaporation from ashing system | Ml | 4030.615 |
| Ash water recovered to cooling water system | Ml | 0.000 |
| Seepage to ground water from dirty areas | Ml | 142.350 |
| Total sink capacity | Ml | 6235.781 |
| Effluents |  |  |
| Cooling water blow downs lime alkalinity control | Ml | 923.437 |
| Additional blow-downs to control calcium sulphate | Ml | 753.663 |
| Cooling water sludge (Included in calculated cooling water blowdowns) | Ml |  |
| Rain water ingress into ash system | Ml | 2768.070 |
| Regeneration effluents | Ml | 84.844 |
| Ash system gland sealing water (other than ash water and CCW) | Ml | 0.000 |
| Treated sewage to ash water system | Ml | 167.791 |
| Total effluents | Ml | 4697.805 |
| Effluent excess over sink | Ml | -1537.976 |
| Desalination requirement | Ml | 0.000 |
| Desalination plant brine | Ml | 0.000 |
| Cooling water cycles of concentration |  | 22.0 |
| Basis for calculation |  |  |
| Station load factor |  | 0.750 |
| Raw water supply from Witbank Dam | Ml for the period | 2007.500 |
| Raw water supply from Grootdraai Dam | Ml for the period | 33420.240 |
| Rain fall | mm per annum | 700 |
| Pond / dam evaporation rate | mm per day | 4.820 |
| Cooling tower evaporation rate | Ml / Gwh so | 1.563 |
| As received ash content of coal | % | 27.00 |
| Coal burn rate | T / Gwh so | 463 |
| Cooling water calcium specification as CaCO3 | mgkg-1 | 400 |
| Cooling water sulphate specification | mgkg-1 | 1000 |
| Cooling water alkalinity specification as CaCO3 | mgkg-1 | 120 |
| Average demineralised water consumption | m3 / Gwh so | 40.00 |

Appendix D

Water Use License Application Forms

# Text boxes

Elevation

mamsl

Duvha P.S.

Witbank Dam

Rainfall

Pan

Coal Stockyard

Ash Dam

- Witbank Dam

Pan

Coal Stockyard

Ash Dam

Komati System

Naupoort System

Raw Water

Resevoir

Cooling Water North

Raw water Reticulation

Cooling Water South

South Irrigation

Overflow

Evaporation

North Irrigation

Demin Sand Filters

Demin + CPP

Plant

Demin Storage

Clarified Water

Demin to WTP

Backwash Water

Backwash Water

LP Demin Range

HP Demin Range

Dirty Effluent

Medium Effluent

Clean Effluent

Clarifier

Potable Water Sand Filters

Potable Water Storage

Raw water

Back wash water

Compressor Cooling

Demin Production

Backwash Water

Fire Range

Power Station

Colliery

Hostels

Contractor Yards

CCW Treatment

Compressor Cooling

Raw Water Sludge

# Power

Station

Potable to Station

Potable to Fire Range

HP Demin to station

LP Demin to station

Evaporation

Irrigation

Sewage Plant

Station drains (clean)

Mix Temp pit rec

Power Station

Cooling

System

Lime

Softening

Emergency Pan

Compressor Cooling

Mixed Temp pit rec

Raw Water

CPP transfer rec

Potable water

Ash Dump recovery

Sand Filter Backwash

Tower Evaporation

Drift & Windage

CW blow-down

Leakage to drains

CW sludge

Rainfall

Station drains

Emergency Pan

WTP effluents

Cooling Water

CCW Sludge

Maturation Pond

Mine Water

Evaporation

Adsorption on Ash

Seepage to GW

Cooling water system

Evaporation

Low Level Dams

High Level Dams

Bottom Ash Quenching

Ash

Plant

Ash Dumps

Sewage

Works

Maturation

Pond

Raw Sewage from station

Raw sewage from hostel

Raw sewage from mine

Evaporation

Public Stream

Ash Dump

Cooling System