9 | DSL | 9DSLB0003 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 75 | 79 | 79 | 9LLM001TR | 9DSLA03CR | A 01 9L3385B1 9L310 A 01 9L3385B1 9L310 A 01 9L3385B1 9L312 A 02 9L3385C1 9L310 A 03 9L3385D1 9L310 A 04 9L3385E1 9L310 A 05 9L3385F1 9L310 A 06 2L3312A1 2L346 A 07 2L3319C1 2L346 A 08 2L3318B1 2L346 A 09 2L3324A1 2L346 A 10 2L3324B1 2L346 A 11 2L33JMA3 2L346 A 12 2L22JMA3 2L244 A 13 2L11JMA3 2L149 A 14 2L1125E1 2L149 A 15 2L1119E3 2L149 A 16 2L1119D3 2L149 A 17 2L1119C3 2L149 A 18 2L1119B3 2L149 A 19 2L1119A3 2L149 A 20 9L1119A3 9L115 |  | 6
9 | DSN | 9DSNB0001 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 57 | 80 | 80 | 9DSN001AR | 9DSNA01CR | A 01 9N2200D2 9N2C34 A 01 9N2200D2 9N2C34 A 02 9N2221B3 9N2C47 A 03 9N2221C3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221E3 9N2C45 A 06 9N2221F3 9N2C45 A 07 9N2221G3 9N2C45 A 08 9N2221H3 9N2C45 A 09 9N2221J3 9N2C45 A 10 9N2221K3 9N2C45 A 11 9N2221L3 9N2C45 |  | 6
9 | DSN | 9DSNB0002 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 20 | 40 | 40 | 9DSN001AR | 9DSNB02CR | IND (SITE RUN) |  | 6
9 | DSN | 9DSNB0003 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 87 | 99 | 99 | 9DSN001AR | 9DSNC03CR | A 01 9N2200D2 9N2C34 A 01 9N2200D2 9N2C34 A 02 9N2200C2 9N2C34 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N33A8A2 9N395 A 10 9N3342B1 9N395 A 11 9N3342A1 9N395 A 12 9N33A2A1 9N3A81 A 13 9N33A2B1 9N3A81 A 14 9N3330A2 9N3A81 A 15 9N3330B2 9N3A81 A 15 9N3330B2 9N3B27 A 16 9N3313C1 9N3B27 A 17 9N3313D1 9N3B27 A 18 9N3313E1 9N3B27 A 19 9N3313F1 9N3B80 A 20 9N3313G1 9N3B80 A 21 9N3313H1 9N3B80 |  | 6
9 | DSN | 9DSNB0004 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 87 | 122 | 122 | 9DSN001AR | 9DSND04CR | A 01 9N2200D2 9N2C34 A 01 9N2200D2 9N2C34 A 02 9N2200C2 9N2C34 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N33A8A2 9N395 A 10 9N3342B1 9N395 A 11 9N3342A1 9N395 A 12 9N33A2A1 9N3A81 A 13 9N33A2B1 9N3A81 A 14 9N3330A2 9N3A81 A 15 9N3330B2 9N3A81 A 15 9N3330B2 9N3B27 A 16 9N3313C1 9N3B27 A 17 9N3313D1 9N3B27 A 18 9N3313E1 9N3B27 A 19 9N3313F1 9N3B80 A 20 9N3313G1 9N3B80 A 21 9N3313H1 9N3B80 A 22 9N3313J1 9N3B80 |  | 6
9 | DSN | 9DSNB0005 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 40 | 62 | 62 | 9DSN001AR | 9DSNE05CR | A 01 9N2200D2 9N2C34 A 01 9N2200D2 9N2C34 A 02 9N2222A1 9N2C47 A 03 9N22C0A3 9N2C47 A 04 1N33C0A1 1N3C76 A 05 1N33C0B1 1N3C76 A 06 1N44C0A1 1N4C76 A 07 1N44C0B1 1N4C76 A 08 1N55C0A1 1N5C76 A 09 1N5500A1 1N5C76 |  | 6
9 | DSN | 9DSNB0006 | OUT | OUT | OUT | NO | 4 | 95 | A | [5 empty] | NO |  |  | 56 | 101 | 101 | 9LLM001TR | 9DSN001AR | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 A 02 9L3362B2 9L310 A 02 9L3362B2 9L312 A 03 9L3362C2 9L312 A 04 9N3340A2 9N395 A 05 9N3340B2 9N395 A 06 9N3340C2 9N395 A 07 9N33A3A2 9N395 A 08 9N22A3A2 9N2A34 A 09 9N2200A2 9N2A34 A 10 9N2200B2 9N2A34 A 10 9N2200B2 9N2C34 A 11 9N2200C2 9N2C34 A 12 9N2200D2 9N2C34 |  | 95
9 | DTV | 9DTVB1401 | OUT | OUT | OUT | NO | 4 | 10 | A | [5 empty] | NO |  |  | 82 | 112 | 112 | 9LLM001TR | 9DTVE01AR | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 A 02 9L3330U3 9L310 A 03 9L3330T3 9L310 A 03 9L3330T3 9L312 A 04 1L3330T3 1L306 A 05 1L3335L1 1L306 A 06 1L3335K1 1L306 A 07 1L3335J1 1L306 A 08 1L3335H1 1L306 A 09 1L3335G1 1L306 A 10 1L3335F1 1L304 A 10 1L3335F1 1L306 A 11 1L3335E1 1L304 A 12 1L33JNB1 1L304 A 13 1L44JNA1 1L404 A 14 1L55JNA1 1L506 A 15 1L66JNA1 1L605 A 16 1L6640D2 1L605 A 17 1L6640C2 1L601 A 18 1L6640B2 1L601 A 19 1L6640A2 1L601 |  | 10
9 | DVM | 9DVMB0001 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 59 | 74 | 74 | 9LKK0402 | 9DVM009CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A8 1M2? |  | 2.5
9 | DVM | 9DVMB0002 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 119 | 151 | 151 | 9LKK0403 | 9DVM004CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | DVM | 9DVMB0003 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 96 | 109 | 109 | 9LKK0404 | 9DVM012CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 16
9 | DVM | 9DVMB0004 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 20 | 10 | 21 | 9DVM012CR | 9DVM014CR | IND (SITE RUN) |  | 16
9 | DVM | 9DVMB0005 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 234 | 82 | 82 | 9DVM004CR | 9DVM012ZV | A 01 1M1112C4 1M1? A 01 1M1112C4 1M1? A 02 0G1107A3 0G1D A 03 0G1107B3 0G1D |  | 2.5
9 | DVM | 9DVMB0006 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 37 | 37 | 9DVM009CR | 9DVM018ZV | IND (SITE RUN) |  | 2.5
9 | DVM | 9DVMB0007 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 36 | 36 | 9DVM012CR | 9DVM014CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0001 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 52 | 53 | 53 | 9LKI0209 | 9DVN002BX | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2224A1 9N2C47 A 07 9N22C0A3 9N2C47 A 08 1N33C0A3 1N3C76 A 09 1N33C0B3 1N3C76 A 10 1N44C0A3 1N4C76 A 11 1N44C0B3 1N4C76 A 12 1N55C0A3 1N5C76 A 13 1N5501A1 1N5C76 A 14 9N5501A1 9N5A01 A 15 9N5507A1 9N5A45 A 16 9N5507B1 9N5A49 A 16 9N5507B1 9N5A50 |  | 150
9 | DVN | 9DVNB0002 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 52 | 52 | 52 | 9LKI0209 | 9DVN002BX | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2224A1 9N2C47 A 07 9N22C0A3 9N2C47 A 08 1N33C0A3 1N3C76 A 09 1N33C0B3 1N3C76 A 10 1N44C0A3 1N4C76 A 11 1N44C0B3 1N4C76 A 12 1N55C0A3 1N5C76 A 13 1N5501A1 1N5C76 A 14 9N5501A1 9N5A01 A 15 9N5507A1 9N5A45 A 16 9N5507B1 9N5A49 A 16 9N5507B1 9N5A50 |  | 150
9 | DVN | 9DVNB0003 | OUT | OUT | OUT | NO | 3 | 185 | A | [5 empty] | NO |  |  | 63 | 70 | 70 | 9LKI0205 | 9DVN005BX | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2224A1 9N2C47 A 07 9N22C0A3 9N2C47 A 08 1N33C0A3 1N3C76 A 09 1N33C0B3 1N3C76 A 10 1N44C0A3 1N4C76 A 11 1N44C0B3 1N4C76 A 12 1N55C0A3 1N5C76 A 13 1N5500A1 1N5C76 A 14 9N5500A1 9N5A01 A 15 9N5500B1 9N5A01 A 16 9N5500C1 9N5A01 A 17 9N5500D1 9N5A01 A 18 9N5508A1 9N5B60 A 19 9N5508B1 9N5B55 A 19 9N5508B1 9N5B56 |  | 185
9 | DVN | 9DVNB0004 | OUT | OUT | OUT | NO | 3 | 185 | A | [5 empty] | NO |  |  | 63 | 62 | 62 | 9LKI0205 | 9DVN005BX | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2224A1 9N2C47 A 07 9N22C0A3 9N2C47 A 08 1N33C0A3 1N3C76 A 09 1N33C0B3 1N3C76 A 10 1N44C0A3 1N4C76 A 11 1N44C0B3 1N4C76 A 12 1N55C0A3 1N5C76 A 13 1N5500A1 1N5C76 A 14 9N5500A1 9N5A01 A 15 9N5500B1 9N5A01 A 16 9N5500C1 9N5A01 A 17 9N5500D1 9N5A01 A 18 9N5508A1 9N5B60 A 19 9N5508B1 9N5B55 A 19 9N5508B1 9N5B56 |  | 185
9 | DVN | 9DVNB0005 | OUT | OUT | OUT | YES | 3 | 185 | A | [5 empty] | NO |  |  | 20 | 4 | 4 | 9DVN002BX | 9DVN002ZV | IND (SITE RUN) |  | 185
9 | DVN | 9DVNB0006 | IN | IN | OUT | YES | 3 | 185 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 7 | 7 | 9DVN005BX | 9DVN005ZV | K9DVN B0006 A IN 03 185 A 9N5B56 N5B56 60T 9DVN 005BX 9N5B56 N5B56 60T 9DVN 005ZV 7 |  | 3 x 185mm2
9 | DVN | 9DVNB0007 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 134 | 76 | 76 | 9DNN001AR | 9DVN015CR | A 01 9N2222D1 9N2C45 A 01 9N2222D1 9N2C45 A 02 9N2222C1 9N2C45 A 03 9N2222B1 9N2C47 A 04 9N2200D2 9N2C34 A 05 9N2200E2 9N2C34 A 06 9N2200F2 9N2C34 A 07 9N2200G2 9N2C34 A 08 9N22C4A3 9N2C34 A 09 9N33D6A1 9N3D51 A 10 9N3332D1 9N3C02 A 11 9N3332C1 9N3C02 A 12 9N3332B1 9N3C02 A 13 9N3332A1 9N3C02 A 14 1N33C2A1 1N3C14 A 15 1N3303A1 1N3C14 A 16 1N3303B1 1N3C14 A 17 9N3318A2 9N3C70 A 18 1N3310A2 1N3C76 A 19 1N33C0B3 1N3C76 A 20 1N44C0A3 1N4C76 A 21 1N44C0B3 1N4C76 A 22 1N55C0A3 1N5C76 A 23 1N5501A1 1N5C76 A 24 9N5501A1 9N5A01 A 25 9N5501B1 9N5A01 A 26 9N5503A1 9N5A01 |  | 6
9 | DVN | 9DVNB0008 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 20 | 12 | 12 | 9DVN015CR | 9DVN016CR | IND (SITE RUN) |  | 6
9 | DVN | 9DVNB0009 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 20 | 16 | 16 | 9DVN016CR | 9DVN017CR | IND (SITE RUN) |  | 6
9 | DVN | 9DVNB0010 | OUT | OUT | OUT | NO | 4 | 6 | A | [5 empty] | NO |  |  | 20 | 14 | 14 | 9DVN017CR | 9DVN018CR | IND (SITE RUN) |  | 6
9 | DVN | 9DVNB0011 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 19 | 19 | 9DVN015CR | 9DVN015FI | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0012 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 20 | 9DVN016CR | 9DVN016FI | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0013 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 20 | 9DVN017CR | 9DVN017FI | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0014 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 24 | 24 | 9DVN018CR | 9DVN018FI | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0020 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 21 | 21 | 9DVN015CR | 9DVN014CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0021 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 23 | 23 | 9DVN015CR | 9DVN014CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0022 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 11 | 11 | 9DVN015CR | 9DVN016CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0023 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 13 | 13 | 9DVN016CR | 9DVN017CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0024 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 18 | 18 | 9DVN017CR | 9DVN018CR | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0600 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 20 | 9DVN014CR | 9DVN001SM | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0601 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 5 | 20 | 9DVN001SM | 9DVN002SM | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0602 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 8 | 20 | 9DVN002SM | 9DVN003SM | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0603 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 5 | 20 | 9DVN003SM | 9DVN004SM | IND (SITE RUN) |  | 2.5
9 | DVN | 9DVNB0604 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 20 | 9DVN001SM | 9DVN004SM | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0001 | OUT | OUT | OUT | NO | 3 | 185 | A | [5 empty] | NO |  |  | 114 | 135 | 135 | 9LKK0209 | 9DWN001AR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA2 1L306 A 13 1L224JA2 1L204 A 14 1L114JA2 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1L11J5A5 1L101 A 23 1L1100F3 1L101 A 23 1L1100F3 1L113 A 24 1L1100E3 1L101 A 25 1L1100D3 1L101 A 25 1L1100D3 1L102 A 26 1L1100C3 1L102 A 26 1L1100C3 1L103 A 26 1L1100C3 1L104 A 27 1L1103A1 1L104 A 28 1L1102A2 1L104 A 28 1L1102A2 1L114 |  | 185
9 | DWN | 9DWNB0002 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 111 | 128 | 128 | 9LKK0410 | 9DWN010CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA2 1L306 A 13 1L224JA2 1L204 A 14 1L114JA2 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1L11J5A5 1L101 A 23 1L1100F3 1L101 A 23 1L1100F3 1L113 A 24 1L1100E3 1L101 A 25 1L1100D3 1L101 A 25 1L1100D3 1L102 A 26 1L1100C3 1L102 A 26 1L1100C3 1L103 A 26 1L1100C3 1L104 A 27 1L1103A1 1L104 A 28 1L1102A2 1L104 A 28 1L1102A2 1L114 |  | 2.5
9 | DWN | 9DWNB0003 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 110 | 126 | 126 | 9LKK0411 | 9DWN001HU | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA2 1L306 A 13 1L224JA2 1L204 A 14 1L114JA2 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1L11J5A5 1L101 A 23 1L1100F3 1L101 A 23 1L1100F3 1L113 A 24 1L1100E3 1L101 A 25 1L1100D3 1L101 A 25 1L1100D3 1L102 A 26 1L1100C3 1L102 A 26 1L1100C3 1L103 A 26 1L1100C3 1L104 A 27 1L1103A1 1L104 A 28 1L1102A2 1L104 A 28 1L1102A2 1L114 |  | 16
9 | DWN | 9DWNB0010 | OUT | OUT | OUT | NO | 4 | 10 | A | [5 empty] | NO |  |  | 107 | 127 | 127 | 9DNL001AR | 9DWN011CR | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 A 02 9L3356K4 9L310 A 03 9L3356J4 9L310 A 04 9L3356H4 9L310 A 05 9L3356G4 9L312 A 06 1L3356G4 1L306 A 07 1L3356F4 1L306 A 08 1L3356E4 1L306 A 09 1L3356D4 1L306 A 10 1L3356C4 1L306 A 11 1L334JA2 1L306 A 12 1L224JA2 1L204 A 13 1L114JA2 1L109 A 14 1L1112E1 1L109 A 15 1L1112D1 1L109 A 16 1L1112C1 1L105 A 16 1L1112C1 1L109 A 17 1L1114A1 1L105 A 18 1L1110G3 1L105 A 19 1L1110F3 1L105 A 20 1L1110E3 1L101 A 20 1L1110E3 1L113 A 21 1L11J5A5 1L101 A 22 1L1100F3 1L101 A 22 1L1100F3 1L113 A 23 1L1100E3 1L101 A 24 1L1100D3 1L101 A 24 1L1100D3 1L102 A 25 1L1100C3 1L102 A 25 1L1100C3 1L103 A 25 1L1100C3 1L104 A 26 1L1103A1 1L104 A 27 1L1102A2 1L104 A 27 1L1102A2 1L114 |  | 10
9 | DWN | 9DWNB0011 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 23 | 23 | 9DWN011CR | 9DWN001FI | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0012 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 145 | 130 | 184 | 9LKZ0101 | 9DWN001CR | A 01 1L1112C5 1L105 A 01 1L1112C5 1L105 A 01 1L1112C5 1L109 A 02 1L1112B5 1L105 A 03 1L1112A5 1L105 A 04 1L1110F5 1L105 A 05 1L1110E5 1L101 A 05 1L1110E5 1L113 A 06 1L1110D5 1L101 A 07 1L1110C5 1L101 A 08 1L1103A1 1L104 A 09 1L1102A2 1L104 A 09 1L1102A2 1L114 |  | 150
9 | DWN | 9DWNB0020 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 18 | 18 | 9DWN011CR | 9DWN013CR | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0021 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 18 | 18 | 9DWN011CR | 9DWN013CR | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0022 | OUT | OUT | OUT | NO | 3 | 35 | A | [5 empty] | NO |  |  | 20 | 18 | 18 | 9DWN001CR | 9DWN001GF | IND (SITE RUN) |  | 35
9 | DWN | 9DWNB0023 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 20 | 17 | 17 | 9DWN001CR | 9DWN001PO | IND (SITE RUN) |  | 6
9 | DWN | 9DWNB0024 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 20 | 17 | 17 | 9DWN001CR | 9DWN001PO | IND (SITE RUN) |  | 6
9 | DWN | 9DWNB0025 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 20 | 9DWN011CR | 9DWN001GF | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0026 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 9DWN011CR | 9DWN001CR | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0027 | OUT | OUT | OUT | NO | 2 | 1.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9DWN001CR | 9DWN001BC | IND (SITE RUN) |  | 1.5
9 | DWN | 9DWNB0028 | OUT | OUT | OUT | NO | 2 | 1.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9DWN001BC | 9DWN001BC | IND (SITE RUN) |  | 1.5
9 | DWN | 9DWNB0029 | OUT | OUT | OUT | NO | 2 | 1.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9DWN001BC | 9DWN026VD | IND (SITE RUN) |  | 1.5
9 | DWN | 9DWNB0030 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 135 | 200 | 1 | 9LKZ0510 | 9DWN010TR | A 01 1L1112E1 1L109 A 01 1L1112E1 1L109 A 02 1L115JA1 1L109 A 03 1L225JA1 1L204 A 04 1L335JA1 1L306 A 05 1L3317R2 1L306 A 06 1L3317P2 1L306 A 07 1L3317N2 1L306 A 08 1L3317M2 1L306 A 09 1L3317L2 1L306 A 10 1L3317K2 1L306 A 11 1L3317J2 1L306 A 12 1L3355A2 1L306 A 13 1L3342E3 1L304 A 13 1L3342E3 1L306 A 14 1L3342D3 1L304 A 15 1L3342C3 1L304 A 16 1L3336C3 1L304 A 17 1L3336D3 1L304 A 18 1M2204A4 1M2? A 19 1M22H6A3 1M2? A 20 1M11H6A3 1M1? A 21 1M1106A5 1M1? |  | 16
9 | DWN | 9DWNB0031 | OUT | OUT | OUT | NO | 4 | 16 | A | [5 empty] | NO |  |  | 20 | 5 | 5 | 9DWN010TR | 9DWN010AR | IND (SITE RUN) |  | 16
9 | DWN | 9DWNB0032 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 9LKZ0510 | 9DWN010TR |  |  | 16 | [5 empty] | not in pericles
9 | DWN | 9DWNB0600 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 20 | 30 | 20 | 9DWN001AR | 9DWN001ZV | IND (SITE RUN) |  | 6
9 | DWN | 9DWNB0601 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 20 | 15 | 20 | 9DWN001AR | 9DWN002ZV | IND (SITE RUN) |  | 6
9 | DWN | 9DWNB0602 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 8 | 20 | 9DWN001AR | 9DWN003ZV | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0603 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 45 | 20 | 9DWN001AR | 9DWN004ZV | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0604 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 20 | 30 | 20 | 9DWN001AR | 9DWN001RS | IND (SITE RUN) |  | 70
9 | DWN | 9DWNB0605 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 15 | 20 | 9DWN001AR | 9DWN010CR | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0606 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 15 | 20 | 9DWN001AR | 9DWN010CR | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0607 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 8 | 20 | 9DWN010CR | 9DWN001HU | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0608 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 20 | 9DWN013CR | 9DWN001SM | IND (SITE RUN) |  | 2.5
9 | DWN | 9DWNB0609 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 8 | 20 | 9DWN010CR | 9DWN001HU | IND (SITE RUN) |  | 2.5
9 | DWX | 9DWXB0011 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 30 | 1 | 9LKP0510 | 9DWX011ZV |  |  | 2.5 | [5 empty] | not in pericles
9 | DWX | 9DWXB0012 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 18 | 1 | 9LKP0509 | 9DWX012ZV |  |  | 2.5 | [5 empty] | not in pericles
9 | DWX | 9DWXB0013 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 33 | 1 | 9LKP0507 | 9DWX014ZV |  |  | 2.5 | [5 empty] | not in pericles
9 | DWX | 9DWXB0031 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 31 | 45 | 1 | 9LKN0403 | 9DWX011CR | A 01 9Y2201E1 9Y20Y A 01 9Y2201E1 9Y20Y A 02 9Y2201F1 9Y20Y A 03 9Y2201G1 9Y20Y A 04 9Y2201H1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y |  | 2.5
9 | DWX | 9DWXB0032 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 31 | 36 | 36 | 9LKN0401 | 9DWX002CR | A 01 9Y2201E1 9Y20Y A 01 9Y2201E1 9Y20Y A 02 9Y2201F1 9Y20Y A 03 9Y2201G1 9Y20Y A 04 9Y2201H1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y |  | 2.5
9 | DWX | 9DWXB0033 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 13 | 25 | 18 | 9LKP0509 | 9DWX005CR | A 01 9H2200E2 9H2? A 01 9H2200E2 9H2? A 02 9H2200D2 9H2? A 03 9H2202A1 9H2? A 04 9H2203H2 9H2? A 05 9H2203J2 9H2? |  | 2.5
9 | DWX | 9DWXB0034 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 18 | 6 | 6 | 0LLL0101 | 9DWX009CR | A 01 0G1109A1 0G1D A 01 0G1109A1 0G1D |  | 6
9 | DWX | 9DWXB0035 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 27 | 24 | 24 | 9LKM0210 | 9DWX010CR | A 01 0G1193A2 0G1B A 01 0G1193A2 0G1B |  | 2.5
9 | DWX | 9DWXB0036 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 56 | 110 | 110 | 9DWX002CR | 9DWX001ZV | A 01 9Y2220A1 9Y20Y A 01 9Y2220A1 9Y20Y A 02 9Y2226C3 9Y20Y A 03 9Y2226B3 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y22Z2A2 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2201H1 9Y20Y A 08 9Y2201G1 9Y20Y A 09 9Y2201F1 9Y20Y A 10 9Y2201E1 9Y20Y A 11 9Y2201D1 9Y20Y A 12 9Y2201C1 9Y20Y A 13 9Y2201B1 9Y20Y A 14 9Y2201A1 9Y20Y A 15 9Y2200A2 9Y20Y |  | 2.5
9 | DWX | 9DWXB0037 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 44 | 74 | 74 | 9LKN0402 | 9DWX002ZV | A 01 9Y2201C1 9Y20Y A 01 9Y2201C1 9Y20Y A 02 9Y2201B1 9Y20Y A 03 9Y2201A1 9Y20Y A 04 9Y2200A2 9Y20Y |  | 2.5
9 | DWX | 9DWXB0038 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 15 | 20 | 9DWX010CR | 9DWX003ZV | IND (SITE RUN) |  | 2.5
9 | DWX | 9DWXB0039 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 15 | 9DWX009CR | 9DWX004ZV | IND (SITE RUN) |  | 2.5
9 | DWX | 9DWXB0040 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 20 | 13 | 9DWX009CR | 9DWX005ZV | IND (SITE RUN) |  | 2.5
9 | DWX | 9DWXB0041 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 24 | 38 | 38 | 9DWX005CR | 9DWX011ZV | A 01 9H2203J2 9H2? A 01 9H2203J2 9H2? A 02 9H2203H2 9H2? A 03 9H2203G2 9H2? A 04 9H2203F2 9H2? A 05 9H2203E2 9H2? A 06 9H2203D2 9H2? A 07 9H2203C2 9H2? A 08 9H2203B2 9H2? |  | 2.5
9 | DWX | 9DWXB0042 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 17 | 35 | 35 | 9DWX005CR | 9DWX012ZV | A 01 9H2203J2 9H2? A 01 9H2203J2 9H2? A 02 9H2203H2 9H2? A 03 9H2203G2 9H2? A 04 9H2203F2 9H2? A 05 9H2203E2 9H2? A 06 9H2203D2 9H2? |  | 2.5
9 | DWX | 9DWXB0043 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 4 | 15 | 30 | 9LKP0510 | 9DWX014ZV | A 01 9H2200E2 9H2? A 01 9H2200E2 9H2? A 02 9H2200D2 9H2? A 03 9H2200C2 9H2? |  | 2.5
9 | DWX | 9DWXB0044 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 61 | 115 | 115 | 9DWX002CR | 9DWX026ZV | A 01 9Y2220A1 9Y20Y A 01 9Y2220A1 9Y20Y A 02 9Y2226C3 9Y20Y A 03 9Y2226B3 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y22Z2A2 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2201H1 9Y20Y A 08 9Y2201G1 9Y20Y A 09 9Y2201F1 9Y20Y A 10 9Y2201E1 9Y20Y A 11 9Y2201D1 9Y20Y A 12 9Y2201C1 9Y20Y A 13 9Y2201B1 9Y20Y A 14 9Y2201A1 9Y20Y A 15 9Y2200A2 9Y20Y |  | 2.5
9 | DWX | 9DWXB0045 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 0LLL0101 | 9DWX009CR |  |  | 2.5 | [5 empty] | not in pericles
9 | DWX | 9DWXB0046 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9DWX011CR | 9DWX001CO | IND (SITE RUN) |  | 2.5
9 | DWX | 9DWXB0047 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 24 | 45 | 1 | 9LKP0410 | 9DWX101RS | A 01 9H2200D2 9H2? A 01 9H2200D2 9H2? A 02 9H2202A1 9H2? A 03 9H2203H2 9H2? A 04 9H2203J2 9H2? A 05 9H2203K2 9H2? A 06 9H2203L2 9H2? A 07 9H2203M2 9H2? A 08 9H2203N2 9H2? |  | 16
9 | DWX | 9DWXB0048 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 24 | 41 | 41 | 9LKP0411 | 9DWX101ZV | A 01 9H2200D2 9H2? A 01 9H2200D2 9H2? A 02 9H2202A1 9H2? A 03 9H2203H2 9H2? A 04 9H2203J2 9H2? A 05 9H2203K2 9H2? A 06 9H2203L2 9H2? A 07 9H2203M2 9H2? A 08 9H2203N2 9H2? |  | 2.5
9 | GRV | 9GRVB0001 | OUT | OUT | OUT | YES | 3 | 70 | A | [5 empty] | NO |  |  | 258 | 269 | 269 | 9LKZ0201 | 9GRV001RE | A 01 9L0002C1 9L035 A 01 9L0002C1 9L035 A 02 9L0002D1 9L035 A 03 9L00Z8A1 9L035 A 04 2L11Z8A1 2L141 A 05 2L1113A3 2L141 A 05 2L1113A3 2L142 A 06 2L1122F2 2L141 A 07 2L1122E2 2L141 A 08 2L1122D2 2L141 A 08 2L1122D2 2L153 A 09 2L1122C2 2L145 A 10 2L1122B2 2L145 A 10 2L1122B2 2L149 A 11 2L11JMA4 2L149 A 12 2L22JMA4 2L244 A 13 2L33JMA4 2L346 A 14 2L3325C1 2L344 A 14 2L3325C1 2L346 A 15 2L3325D1 2L344 A 16 2L3325E1 2L344 A 17 2L3325F1 2L341 A 17 2L3325F1 2L344 A 18 2M3300A1 2M3? A 19 2M22HAA1 2M2? A 20 2M2203A1 2M2? A 21 2M220HA2 2M2? A 22 2M110HA2 2M1? A 23 2M1121A2 2M1? A 24 2M1121B2 2M1? A 25 0G1108C3 0G1D A 26 0G1108B3 0G1D |  | 70
9 | JPD | 9JPDB0001 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 191 | 226 | 226 | 9LKK0508 | 9JPD001PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB1 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3318C2 1L301 A 22 1L3318B2 1L301 A 23 1L3308C4 1L301 A 24 1L3308D4 1L301 A 25 1L3308E4 1L301 A 26 1L33J5A6 1L301 A 27 1L22J5A6 1L201 A 28 1L11J5A6 1L101 A 29 1L1100F3 1L101 A 29 1L1100F3 1L113 A 30 1L1100E3 1L101 A 31 1L1100D3 1L101 A 31 1L1100D3 1L102 A 32 1L1100C3 1L102 A 32 1L1100C3 1L103 A 32 1L1100C3 1L104 A 33 1L1100B3 1L104 A 34 1W1100B3 1W130 A 35 1W1100A3 1W130 A 36 1W1107A1 1W130 A 37 1W11M0A1 1W131 A 38 1W00M0A1 1W031 A 39 1W0000A1 1W031 A 39 1W0000A1 1W032 A 39 1W0000A1 1W035 A 39 1W0000A1 1W037 A 39 1W0000A1 1W038 |  | 3 x 35mm2
9 | JPD | 9JPDB0003 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 191 | 226 | 226 | 9LKK0503 | 9JPD002PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB1 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3318C2 1L301 A 22 1L3318B2 1L301 A 23 1L3308C4 1L301 A 24 1L3308D4 1L301 A 25 1L3308E4 1L301 A 26 1L33J5A6 1L301 A 27 1L22J5A6 1L201 A 28 1L11J5A6 1L101 A 29 1L1100F3 1L101 A 29 1L1100F3 1L113 A 30 1L1100E3 1L101 A 31 1L1100D3 1L101 A 31 1L1100D3 1L102 A 32 1L1100C3 1L102 A 32 1L1100C3 1L103 A 32 1L1100C3 1L104 A 33 1L1100B3 1L104 A 34 1W1100B3 1W130 A 35 1W1100A3 1W130 A 36 1W1107A1 1W130 A 37 1W11M0A1 1W131 A 38 1W00M0A1 1W031 A 39 1W0000A1 1W031 A 39 1W0000A1 1W032 A 39 1W0000A1 1W035 A 39 1W0000A1 1W037 A 39 1W0000A1 1W038 |  | 3 x 35mm2
9 | JST | 9DSNB0008 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9DSN041CR | 9DSN141ES |  |  | 3 x 6mm2 Armoured | [5 empty] | not in pericles
9 | KBS | 9JDTB0920 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9LNH012JA | 9JDT400CR | E9JDT B0920 A IN 03 2.5 A 9H2? 9LNH 012JA 9LNH 012JA 1C2A 9JDT 400CR 9JDT 400CR 0 |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | KBS | 9JDTB0921 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9LNF550CR | 9JDT300CR | E9JDT B0921 A IN 03 2.5 A 9N2C45 9LNF 550CR 9LNF 550CR 9N2C34 9JDT 300CR 9JDT 300CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KBS | 9JDTB0922 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9LNF550CR | 9JDT350CR |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | KIR | 9JDTB0923 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9LNF550CR | 9JDT375CR | E9JDT B0923 A IN 03 2.5 A 9N2C45 9LNF 550CR 9LNF 550CR 2K256 9JDT 375CR 9JDT 375CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0928 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 1LNE500CR | PN1L319 | E9JDT B0928 A IN 03 2.5 A 1W401 1LNE 500CR 1LNE 500CR 1W330 PN1 L319 PN1 L319 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0929 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 1LMA500CR | PN1L316 | E9JDT B0929 A IN 03 2.5 A 1W431 1LMA 500CR 1LMA 500CR 1W330 PN1 L316 PN1 L316 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0930 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 1LMA500CR | 9JDT010CR | E9JDT B0930 A IN 03 2.5 A 1W431 1LMA 500CR 1LMA 500CR 9N4C15 9JDT-010CR 9JDT-010CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0931 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 1LNE500CR | 9JDT100AR | E9JDT B0931 A IN 03 2.5 A 1W401 1LNE 500CR 1LNE 500CR 1L609 9JDT 100AR 9JDT 100AR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0932 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | PN1L319 | 9JDT001CR | E9JDT B0932 A IN 03 2.5 A 1W330 PN1 L319 PN1 L319 1W330 PN1 L319 PN1 L319 0 |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | KIR | 9JDTB0933 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | PN1L316 | 9JDT006CR | E9JDT B0933 A IN 03 2.5 A 1W330 PN1 L316 PN1 L316 1W330 PN1 L316 PN1 L316 0 |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | KIR | 9JDTB0963 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT100AR | 9JDT201AR | E9JDT B0963 A IN 03 2.5 A 1L609 9JDT 100AR 9JDT 100AR 9L711 9JDT 201AR 9JDT 201AR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0965 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT201AR | 9JDT100AR | E9JDT B0965 A IN 03 2.5 A 9L711 9JDT 201AR 9JDT 201AR 1L609 9JDT 100AR 9JDT 100AR 0 |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | KIR | 9JDTB0968 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT001CR | 9JDT003CR | E9JDT B0968 A IN 03 2.5 A 1R330 9JDT 001CR 9JDT 001CR 1R320 9JDT 003CR 9JDT 003CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0969 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT003CR | 9JDT005CR | E9JDT B0969 A IN 03 2.5 A 1R320 9JDT 003CR 9JDT 003CR 1R330 9JDT 005CR 9JDT 005CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0970 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT006CR | 9JDT004CR | E9JDT B0970 A IN 03 2.5 A 1R330 9JDT 006CR 9JDT 006CR 9L307 9JDT 004CR 9JDT 004CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0971 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT004CR | 9JDT002CR | E9JDT B0971 A IN 03 2.5 A 9L307 9JDT 004CR 9JDT 004CR 1R330 9JDT 002CR 9JDT 002CR 0 |  | 3c x 2,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0976 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT200CR | 9JDT903AR | E9JDT B0976 A IN 03 2.5 A 2L650 9JDT 200CR 9JDT 200CR 2L650 9JDT 903AR 9JDT 903AR 0 |  | 3c x 1,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0977 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT200CR | 9JDT904AR | E9JDT B0977 A IN 03 2.5 A 2L650 9JDT 200CR 9JDT 200CR 2L650 9JDT 904AR 9JDT 904AR 0 |  | 3c x 1,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0978 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT250CR | 9JDT905AR | E9JDT B0978 A IN 03 2.5 A 2L650 9JDT 250CR 9JDT 250CR 2L650 9JDT 905AR 9JDT 905AR 0 |  | 3c x 1,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0979 | OUT | OUT | OUT | NO | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9JDT250CR | 9JDT906AR | E9JDT B0979 A IN 03 2.5 A 2L650 9JDT 250CR 9JDT 250CR 2L650 9JDT 906AR 9JDT 906AR 0 |  | 3c x 1,5mm2 | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0980 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9JDT200CR | 9JDT920AR |  |  | 3core x 1.5mm2 | [5 empty] | not in pericles
9 | KIR | 9JDTB0990 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9JDT100CR | 1JPH001AN |  |  | 3c x 2,5 mm2 SWA / PVC | [5 empty] | duplicate cable number
9 | KIR | 9JDTB0991 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9JDT150CR | 2JPH001AN |  |  | 3c x 2,5 mm2 SWA / PVC | [5 empty] | duplicate cable number
9 | KIR | 9KIRB0900 | IN: OUT; IN: OUT; OUT: OUT; NO: NO |  |  |  | NO | [5 empty] | 9KIR001AR | 9KIR002HV | [8 empty] | not in pericles
9 | KRT | 9KRTB0023 | IN | IN | OUT | YES | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ABERDARE/AFRICAN CABLES | EMS | 66 |  |  | 9KRT566AR | 9DSNB02CR | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | KRT | 9KRTB0798 | IN | IN | OUT | YES | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ABERDARE/AFRICAN CABLES | EMS | 20 |  |  | 9KRT501AR | 9KRT001TB | IND (SITE RUN)
9 | KRT | 9KRTB1002 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT503CR | IND (SITE RUN) | [7 empty] | not in pericles
9 | KRT | 9KRTB1003 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT503CR | 9KRT502CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1004 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT505CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1005 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT506CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1006 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT507CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1007 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT508CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1008 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT500AR | 9KRT509CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1009 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT510CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1010 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT511CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1011 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT512CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1012 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT513CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1013 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT514CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1014 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT515CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1015 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT516CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1016 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT517CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1017 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT518CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1018 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT519CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1019 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT520CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1020 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT521CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1021 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT522CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1022 | IN | IN | OUT | NO | 3 | 0.6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | LAPP | EMS |  |  |  | 9KRT530CR | 9KRT523CR | IND (SITE RUN) |  | 3 x 0,6mm² | [5 empty] | not in pericles
9 | KRT | 9KRTB1023 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ABERDARE/AFRICAN CABLES | EMS |  |  |  | 9KRT500AR | 9KRT530CR | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LBG | 9LBGB0001 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 22 | 38 | 20 | 9LKK0506 | 9LBG001RD | A 01 9L3356P4 9L310 A 01 9L3356P4 9L310 A 02 9L33KAA2 9L310 A 03 9L44KAA2 9L410 A 04 9L4442F1 9L410 A 05 9L4442E1 9L410 A 06 9L4442D1 9L410 A 07 9L4442C1 9L410 |  | 3 x 35mm2
9 | LBG | 9LBGB0002 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 87 | 90 | 90 | 9LKI0307 | 9LBG002RD | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N3340A2 9N395 A 16 9L3362C2 9L312 A 17 9L3362B2 9L310 A 17 9L3362B2 9L312 A 18 9L3362A2 9L310 A 19 9L3356K4 9L310 A 20 9L3356L4 9L310 A 21 9L3356M4 9L310 A 22 9L3356N4 9L310 A 23 9L3356P4 9L310 A 24 9L33KAA1 9L310 A 25 9L44KAA1 9L410 A 26 9L4442F1 9L410 A 27 9L4442E1 9L410 A 28 9L4442D1 9L410 A 29 9L4442C1 9L410 |  | 3 x 35mm2
9 | LBG | 9LBGB0900 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 130 | 9LBG101CR | 1LLY206JA | IND, 9L4421E, IND, 9L4KA1A, 9L3KA1A, 9L3564P-H, 9L3571C, 1L3303T, 1L3394M-G, 1L3363B-C, 1L3423C-B, 1L3424B-A, 1L3154E-C, IND, 1L3084E-C, IND |  | 3 x 35mm2 | [5 empty] | duplicate cable number with different 'equipment from and to' information
9 | LBG | 9LBGB0901 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 55 | 9LBG102CR | 2LLY206JA | IND, 9L4421D, 4KA1A, 3KA1A, 3564P-M, 3851F, 3152B-A, IND |  | 3 x 35mm2 | [5 empty] | duplicate cable number with different 'equipment from and to' information
9 | LBG | 9LBGB0902 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 10 | 9LBG001RD | 9LBG101CR | IND, 9L4421C-D, IND |  | 3 x 35mm2 | [5 empty] | duplicate cable number with different 'equipment from and to' information
9 | LBG | 9LBGB0903 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 12 | 9LBG002RD | 9LBG102CR | IND, 9L4421C-D, IND |  | 3 x 35mm2 | [5 empty] | duplicate cable number with different 'equipment from and to' information
9 | LBH | 9LBHB0001 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 4 | 14 | 14 | 9LKN0211 | 9LBH001RD | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2207A1 9Y20Y A 03 9Y2201D1 9Y20Y |  | 3 x 50mm2
9 | LBK | 9LBKB0001 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 28 | 38 | 38 | 9LLV0202 | 9LBK001RD | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184B1 9D181 A 06 9D11H0A2 9D181 A 07 9D00H0A2 9D083 A 08 9D0000A2 9D082 A 08 9D0000A2 9D083 |  | 3 x 16mm2
9 | LBK | 9LBKB0012 | OUT | OUT | OUT | NO | 2 | 35 | A | [5 empty] | NO |  |  | 31 | 40 | 1 | 9LBK0253 | 9LLV0109 | A 01 9D0000A2 9D082 A 01 9D0000A2 9D082 A 01 9D0000A2 9D083 A 02 9D00H0A2 9D083 A 03 9D11H0A2 9D181 A 04 9D1184B1 9D181 A 05 9D1181E1 9D181 A 06 9D1181D1 9D181 A 07 9D1181C1 9D181 A 08 9D1181B1 9D181 |  | 35
9 | LBK | 9LBKB0013 | OUT | OUT | OUT | NO | 2 | 35 | A | [5 empty] | NO |  |  | 143 | 0 | 1 | 9LBK0241 | 9LLZ0109 | A 01 9D0000A2 9D082 A 01 9D0000A2 9D082 A 01 9D0000A2 9D083 A 02 1D0000B2 1D042 A 03 1D0000C2 1D042 A 04 2D0000D2 2D022 A 05 2D00W3A2 2D022 A 06 2L11Z0A2 2L142 A 07 2L1110A2 2L142 A 07 2L1110A2 2L146 A 07 2L1110A2 2L150 A 08 9L1110A2 9L115 A 09 9L11JAA3 9L115 A 10 2L22JAA3 2L244 A 11 9L33JAA3 9L307 A 12 9L3358A2 9L307 A 13 9L3358B2 9L307 A 14 9L3358C2 9L307 A 14 9L3358C2 9L312 A 15 9L3380B2 9L312 A 16 9L3380A2 9L312 |  | 35
9 | LBL | 9LBLB0001 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 9 | 19 | 19 | 9LKP0501 | 9LBL001RD | A 01 9H2200E2 9H2? A 01 9H2200E2 9H2? A 02 9H2200F2 9H2? A 03 9H2200G2 9H2? A 04 9H2203E2 9H2? A 05 9H2203F2 9H2? |  | 16
9 | LCD | 9LCDB0001 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 27 | 32 | 26 | 9LKK0505 | 9LCD001RD | A 01 9L3356P4 9L310 A 01 9L3356P4 9L310 A 02 9L33KAA2 9L310 A 03 9L44KAA2 9L410 A 04 9L4442F1 9L410 A 05 9L4442E1 9L410 A 06 9L4442D1 9L410 A 07 9L4442C1 9L410 A 08 9L4442B1 9L410 |  | 3 x 16mm2
9 | LCD | 9LCDB0002 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 92 | 95 | 108 | 9LKI0306 | 9LCD002RD | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N3340A2 9N395 A 16 9L3362C2 9L312 A 17 9L3362B2 9L310 A 17 9L3362B2 9L312 A 18 9L3362A2 9L310 A 19 9L3356K4 9L310 A 20 9L3356L4 9L310 A 21 9L3356M4 9L310 A 22 9L3356N4 9L310 A 23 9L3356P4 9L310 A 24 9L33KAA1 9L310 A 25 9L44KAA1 9L410 A 26 9L4442F1 9L410 A 27 9L4442E1 9L410 A 28 9L4442D1 9L410 A 29 9L4442C1 9L410 A 30 9L4442B1 9L410 |  | 3 x 16mm2
9 | LCD | 9LCDB0900 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 1LLY001TB | 9LCD101CR |  |  | 3 x 16mm2 | [5 empty] | not in pericles
9 | LCD | 9LCDB0901 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 2LLY001TB | 9LCD102CR |  |  | 3 x 16mm2 | [5 empty] | not in pericles
9 | LCD | 9LCDB0902 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LCD101CR | 9LCD001RD |  |  | 3 x 16mm2 | [5 empty] | not in pericles
9 | LCD | 9LCDB0903 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LCD102CR | 9LCD002RD |  |  | 3 x 16mm2 | [5 empty] | not in pericles
9 | LCE | 9LCEB0001 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 5 | 16 | 16 | 9LKN0609 | 9LCE001RD | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2208A1 9Y20Y A 04 9Y2201F1 9Y20Y |  | 16
9 | LCG | 9LCGB0001 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 27 | 36 | 36 | 9LLV0203 | 9LCG001RD | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184B1 9D181 A 06 9D11H0A2 9D181 A 07 9D00H0A2 9D083 A 08 9D0000A2 9D082 A 08 9D0000A2 9D083 |  | 3 x 16mm2
9 | LCH | 9LCHB0001 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 7 | 17 | 17 | 9LKP0502 | 9LCH001RD | A 01 9H2200E2 9H2? A 01 9H2200E2 9H2? A 02 9H2200F2 9H2? A 03 9H2200G2 9H2? A 04 9H2203D2 9H2? |  | 16
9 | LGB | 9LGBA0001 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 176 |  |  | 9LGE0201 | 1LGB0401
9 | LGB | 9LGBA0002 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 177 |  |  | 9LGE0201 | 1LGB0401
9 | LGB | 9LGBA0003 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 179 |  |  | 9LGE0201 | 1LGB0401
9 | LGB | 9LGBA0004 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 180 |  |  | 9LGE0201 | 1LGB0401
9 | LGB | 9LGBA0005 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 181 |  |  | 9LGE0201 | 1LGB0401
9 | LGB | 9LGBA0006 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | [5 empty] | NO |  |  | 180 |  |  | 9LGE0201 | 1LGB0401 |  |  | 1pr x 500mm2 | [5 empty] | not in pericles
9 | LGE | 9LGEA0001 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 14 | 14 | 9LGR001TA | 9LGE0401 | K9LGE A0001 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 14 |  | 500
9 | LGE | 9LGEA0002 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 14 | 14 | 9LGR001TA | 9LGE0401 | K9LGE A0002 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 14 |  | 500
9 | LGE | 9LGEA0003 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 14 | 14 | 9LGR001TA | 9LGE0401 | K9LGE A0003 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 14 |  | 500
9 | LGE | 9LGEA0004 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0004 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0005 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0005 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0006 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 14 | 14 | 9LGR001TA | 9LGE0401 | K9LGE A0006 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 14 |  | 500
9 | LGE | 9LGEA0007 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 14 | 14 | 9LGR001TA | 9LGE0401 | K9LGE A0007 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 14 |  | 500
9 | LGE | 9LGEA0008 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0008 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0009 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0009 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0010 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0010 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0011 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0011 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0012 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR001TA | 9LGE0401 | K9LGE A0012 A IN 01 500 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 0401 9LGE 0401 15 |  | 500
9 | LGE | 9LGEA0013 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 11 | 9LGE0501 | 9LGF0501 | A 01 9J1103B1 9J11J A 01 9J1103B1 9J11J A 02 9J1103A1 9J11J |  | 400
9 | LGE | 9LGEA0014 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 11 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0015 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 11 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0016 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 10 | 9LGE0501 | 9LGF0501 | A 01 9J1103B1 9J11J A 01 9J1103B1 9J11J A 02 9J1103A1 9J11J |  | 400
9 | LGE | 9LGEA0017 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 11 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0018 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 6 | 11 | 11 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0019 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 7 | 11 | 11 | 9LGE0501 | 9LGF0501 | A 01 9J1104B1 9J11J A 01 9J1104B1 9J11J A 02 9J1104A1 9J11J |  | 400
9 | LGE | 9LGEA0020 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 7 | 12 | 12 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0021 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 7 | 11 | 12 | 9LGE0501 | 9LGF0501 |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0022 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 23 | 22 | 22 | 9LGR001TA | 9LGE001TR | A 01 9J1101D3 9J11J A 01 9J1101D3 9J11J A 02 9J1101C3 9J11J A 03 9J1101B3 9J11J |  | 400
9 | LGE | 9LGEA0023 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 23 | 22 | 22 | 9LGR001TA | 9LGE001TR |  |  | 400 | [5 empty] | not in pericles
9 | LGE | 9LGEA0024 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 23 | 22 | 22 | 9LGR001TA | 9LGE001TR | K9LGE A0024 A IN 01 400 MTAL 9J22J 9LGR 001TA 9LGR 001TA 9J22J 9LGE 001TR 9LGE 001TR 22 |  | 400
9 | LGE | 9LGEA0025 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 20 | 7 | 7 | 9LGE001TR | 9LGE001AR | IND (SITE RUN) |  | 50
9 | LGE | 9LGEA0026 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 20 | 10 | 10 | 9LGE001AR | 9LGETT8 | IND (SITE RUN) |  | 50
9 | LGE | 9LGEB0001 | OUT | OUT | OUT | YES | 1 | 70 | A | [5 empty] | NO |  |  | 20 | 7 | 7 | 9LGE001TR | 9LGE001AR | IND (SITE RUN) |  | 70
9 | LGE | 9LGEB0002 | OUT | OUT | OUT | YES | 1 | 70 | A | [5 empty] | NO |  |  | 20 | 7 | 7 | 9LGE001TR | 9LGE001AR | IND (SITE RUN) |  | 70
9 | LGF | 9LGFA0001 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 12 | 1 | 9LGR002TA | 9LGF0401 | K9LGF A0001 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 1 |  | 500
9 | LGF | 9LGFA0002 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR002TA | 9LGF0401 | K9LGF A0002 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 15 |  | 500
9 | LGF | 9LGFA0003 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 13 | 13 | 9LGR002TA | 9LGF0401 | K9LGF A0003 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 13 |  | 500
9 | LGF | 9LGFA0004 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 16 | 16 | 9LGR002TA | 9LGF0401 | K9LGF A0004 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 16 |  | 500
9 | LGF | 9LGFA0005 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR002TA | 9LGF0401 | K9LGF A0005 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 15 |  | 500
9 | LGF | 9LGFA0006 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 14 | 14 | 9LGR002TA | 9LGF0401 | K9LGF A0006 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 14 |  | 500
9 | LGF | 9LGFA0007 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 14 | 14 | 9LGR002TA | 9LGF0401 | K9LGF A0007 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 14 |  | 500
9 | LGF | 9LGFA0008 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 16 | 16 | 9LGR002TA | 9LGF0401 | K9LGF A0008 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 16 |  | 500
9 | LGF | 9LGFA0009 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 16 | 16 | 9LGR002TA | 9LGF0401 | K9LGF A0009 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 16 |  | 500
9 | LGF | 9LGFA0010 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 20 | 14 | 14 | 9LGR002TA | 9LGF0401 | K9LGF A0010 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 14 |  | 500
9 | LGF | 9LGFA0011 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 5 | 15 | 9LGR002TA | 9LGF0401 | K9LGF A0011 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 15 |  | 500
9 | LGF | 9LGFA0012 | OUT | OUT | OUT | YES | 1 | 500 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 0 | 15 | 15 | 9LGR002TA | 9LGF0401 | K9LGF A0012 A IN 01 500 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 0401 9LGF 0401 15 |  | 500
9 | LGF | 9LGFA0013 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 21 | 21 | 21 | 9LGR002TA | 9LGF001TR | A 01 9J1100D4 9J11J A 01 9J1100D4 9J11J A 02 9J1100C4 9J11J A 03 9J1100B4 9J11J |  | 400
9 | LGF | 9LGFA0014 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 21 | 21 | 21 | 9LGR002TA | 9LGF001TR | K9LGF A0014 A IN 01 400 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 001TR 9LGF 001TR 21 |  | 400
9 | LGF | 9LGFA0015 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 21 | 23 | 23 | 9LGR002TA | 9LGF001TR | K9LGF A0015 A IN 01 400 MTAL 9J22J 9LGR 002TA 9LGR 002TA 9J22J 9LGF 001TR 9LGF 001TR 23 |  | 400
9 | LGF | 9LGFA0016 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 20 | 5 | 5 | 9LGF001TR | 9LGF001AR | IND (SITE RUN) |  | 50
9 | LGF | 9LGFA0017 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 20 | 9 | 9 | 9LGF001AR | 9LGFTT9 | IND (SITE RUN) |  | 50
9 | LGF | 9LGFB0001 | OUT | OUT | OUT | YES | 1 | 70 | A | [5 empty] | NO |  |  | 20 | 7 | 7 | 9LGF001TR | 9LGF001AR | IND (SITE RUN) |  | 70
9 | LGF | 9LGFB0002 | OUT | OUT | OUT | YES | 1 | 70 | A | [5 empty] | NO |  |  | 20 | 7 | 7 | 9LGF001TR | 9LGF001AR | IND (SITE RUN) |  | 70
9 | LGI | 9LGIA0001 | OUT | OUT | OUT | YES | 3 | 240 | MTAL | [5 empty] | NO |  |  | 75 | 77 | 1 | 1LGC0201 | 9LGI0101 | A 01 1L3325A1 1L304 A 01 1L3325A1 1L304 A 02 1L3325B1 1L304 A 03 1L3325C1 1L304 A 04 1L3325D1 1L304 A 05 1L3339D1 1L304 A 06 1L3339E1 1L304 A 07 1L3339F1 1L304 A 08 1L3339G1 1L304 A 09 1L3339H1 1L304 A 09 1L3339H1 1L306 A 10 1L3339J1 1L306 A 11 1L3339K1 1L306 A 12 1L3339L1 1L306 A 13 1L3339M1 1L306 A 14 1L3339N1 1L306 A 15 1L3339P1 1L306 A 16 1L3339R1 1L306 A 17 1L3339S1 1L306 A 18 1L3339T1 1L306 A 19 9L3339T1 9L310 A 19 9L3339T1 9L312 A 20 9L3339U1 9L310 A 21 9L3339V1 9L310 A 22 9L3339W1 9L310 A 23 9L3339X1 9L310 A 24 9L3339Y1 9L310 A 25 9L3361A1 9L310 A 26 9L3361B1 9L310 |  | 240
9 | LGI | 9LGIA0002 | OUT | OUT | OUT | YES | 3 | 240 | MTAL | [5 empty] | NO |  |  | 55 | 62 | 62 | 2LGC0201 | 9LGI0501 | A 01 2L3314D1 2L344 A 01 2L3314D1 2L344 A 02 2L3314C1 2L344 A 02 2L3314C1 2L346 A 03 2L3314B1 2L346 A 04 2L3314A1 2L346 A 05 2L3310C1 2L346 A 06 9L3363A1 9L310 A 07 9L3369A1 9L310 A 08 9L3369B1 9L310 A 09 9L3369C1 9L310 A 10 9L3369D1 9L310 |  | 240
9 | LGI | 9LGIA0003 | OUT | OUT | OUT | YES | 3 | 240 | MTAL | [5 empty] | NO |  |  | 77 | 81 | 81 | 1LGC0201 | 9LGI0101 | A 01 1L3325A3 1L304 A 01 1L3325A3 1L304 A 02 1L3325B3 1L304 A 03 1L3326A1 1L304 A 04 1L3324D1 1L304 A 05 1L3324E1 1L304 A 06 1L3324F1 1L304 A 07 1L3324G1 1L304 A 08 1L3324H1 1L304 A 09 1L3324J1 1L304 A 10 1L3324K1 1L304 A 11 1L3324L1 1L304 A 11 1L3324L1 1L306 A 12 1L3324M1 1L306 A 13 1L3324N1 1L306 A 14 1L3324P1 1L306 A 15 1L3324R1 1L306 A 16 1L3339N1 1L306 A 17 1L3345A1 1L306 A 18 1L3345B1 1L306 A 19 1L3345C1 1L306 A 20 1L3345D1 1L306 A 21 9L3345D1 9L310 A 21 9L3345D1 9L312 A 22 9L3345E1 9L310 A 23 9L3345F1 9L310 A 24 9L3345G1 9L310 A 25 9L3345H1 9L310 A 26 9L3345J1 9L310 A 27 9L3345K1 9L310 A 28 9L3345L1 9L310 A 29 9L3345M1 9L310 A 30 9L3345N1 9L310 |  | 240
9 | LGI | 9LGIA0004 | OUT | OUT | OUT | YES | 3 | 240 | MTAL | [5 empty] | NO |  |  | 71 | 69 | 69 | 2LGC0201 | 9LGI0501 | A 01 2L3314D1 2L344 A 01 2L3314D1 2L344 A 02 2L3314E1 2L344 A 03 2L3314F1 2L344 A 04 2L3311A2 2L341 A 04 2L3311A2 2L344 A 04 2L3311A2 2L346 A 05 9L3363A1 9L310 A 06 9L3369A1 9L310 A 07 9L3369B1 9L310 A 08 9L3369C1 9L310 A 09 9L3369D1 9L310 |  | 240
9 | LGI | 9LGIA0005 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 28 | 33 | 33 | 9LGI0301 | 9LHC0801 | A 01 9L3360J1 9L310 A 01 9L3360J1 9L310 A 02 9L3360H1 9L310 A 03 9L3360G1 9L310 A 04 9L3360F1 9L310 A 05 9L3360E1 9L310 A 06 9L3386C1 9L310 A 07 9L3387A1 9L310 A 08 9L3387B1 9L310 A 08 9L3387B1 9L312 |  | 400
9 | LGI | 9LGIA0006 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 28 | 32 | 32 | 9LGI0301 | 9LHC0801 |  |  | 400 | [5 empty] | not in pericles
9 | LGI | 9LGIA0007 | OUT | OUT | OUT | YES | 1 | 400 | MTAL | [5 empty] | NO |  |  | 28 | 32 | 32 | 9LGI0301 | 9LHC0801 |  |  | 400 | [5 empty] | not in pericles
9 | LGI | 9LGIB0900 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | 0 | 20 | 0 | 9LGI071JA | 9LTP001AR | E9LGI B0900 A IN 03 50 A 9L410 9LGI 071JA 9LGI 071JA 9L410 9LTP 001AR 9LTP 001AR 0 |  | 3 x 50mm2 | [5 empty] | duplicate cable number
9 | LGR | 9LGRB0001 | IN | IN | OUT | NO | 3 | 150 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 242 | 251 | 251 | 9LKK0105 | 9LGR001CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA1 1L306 A 13 1L224JA1 1L204 A 14 1L114JA1 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1M1100A4 1M1? A 23 1M11H1A4 1M1? A 24 1M1101A4 1M1? A 25 1M1101B4 1M1? A 26 1M1101C4 1M1? A 27 1M1101D4 1M1? A 28 1G1100A5 1G1GJ |  | 3 x 150mm2
9 | LGR | 9LGRB0002 | IN | IN | OUT | NO | 3 | 150 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4Y | YES | ALSTHOM | EMS | 242 | 253 | 253 | 9LKK0105 | 9LGR001CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA1 1L306 A 13 1L224JA1 1L204 A 14 1L114JA1 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1M1100A4 1M1? A 23 1M11H1A4 1M1? A 24 1M1101A4 1M1? A 25 1M1101B4 1M1? A 26 1M1101C4 1M1? A 27 1M1101D4 1M1? A 28 1G1100A5 1G1GJ |  | 3 x 150mm2
9 | LGR | 9LGRB0003 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 261 | 266 | 266 | 9LKK0309 | 9LGR101CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA1 1L306 A 13 1L224JA1 1L204 A 14 1L114JA1 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1M1100A4 1M1? A 23 1M11H1A4 1M1? A 24 1M1101A4 1M1? A 25 1M1101B4 1M1? A 26 1M1101C4 1M1? A 27 1M1101D4 1M1? A 28 1G1100A5 1G1GJ A 29 9J1101A5 9J11J A 30 9J1101B5 9J11J A 31 9J1101C5 9J11J A 32 9J1101D5 9J11J A 33 9J1101E5 9J11J A 34 9J1101F5 9J11J A 35 9J1101G5 9J11J A 36 9J1101H5 9J11J |  | 3 x 50mm2
9 | LGR | 9LGRB0004 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 10 | 10 | 9LGR101CR | 9LGR103CR | K9LGR B0004 A IN 03 16 A 9J22J 9LGR 101CR 9LGR 101CR 9J22J 9LGR 103CR 9LGR 103CR 10 |  | 3 x 16mm2
9 | LGR | 9LGRB0005 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 261 | 265 | 265 | 9LKK0307 | 9LGR201CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA1 1L306 A 13 1L224JA1 1L204 A 14 1L114JA1 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1M1100A4 1M1? A 23 1M11H1A4 1M1? A 24 1M1101A4 1M1? A 25 1M1101B4 1M1? A 26 1M1101C4 1M1? A 27 1M1101D4 1M1? A 28 1G1100A5 1G1GJ A 29 9J1101A5 9J11J A 30 9J1101B5 9J11J A 31 9J1101C5 9J11J A 32 9J1101D5 9J11J |  | 3 x 50mm2
9 | LGR | 9LGRB0006 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 10 | 10 | 9LGR201CR | 9LGR203CR | K9LGR B0006 A IN 03 16 A 9J22J 9LGR 201CR 9LGR 201CR 9J22J 9LGR 203CR 9LGR 203CR 10 |  | 3 x 16mm2
9 | LGR | 9LGRB0007 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 11 | 11 | 9LGR101CR | 9LGR103CR | K9LGR B0007 A IN 02 2.5 A 9J22J 9LGR 101CR 9LGR 101CR 9J22J 9LGR 103CR 9LGR 103CR 11 |  | 2 x 2,5mm2
9 | LGR | 9LGRB0008 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 11 | 11 | 9LGR101CR | 9LGR103CR | K9LGR B0008 A IN 02 2.5 A 9J22J 9LGR 101CR 9LGR 101CR 9J22J 9LGR 103CR 9LGR 103CR 11 |  | 2 x 2,5mm2
9 | LGR | 9LGRB0009 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 10 | 10 | 9LGR201CR | 9LGR203CR | K9LGR B0009 A IN 02 2.5 A 9J22J 9LGR 201CR 9LGR 201CR 9J22J 9LGR 203CR 9LGR 203CR 10 |  | 2 x 2,5mm2
9 | LGR | 9LGRB0010 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 11 | 11 | 9LGR201CR | 9LGR203CR | K9LGR B0010 A IN 02 2.5 A 9J22J 9LGR 201CR 9LGR 201CR 9J22J 9LGR 203CR 9LGR 203CR 11 |  | 2 x 2,5mm2
9 | LGR | 9LGRB0011 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 13 | 42 | 42 | 9LGR001CR | 9LGR002CR | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 3 x 50mm2
9 | LGR | 9LGRB0012 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 13 | 34 | 34 | 9LGR001CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 3 x 16mm2
9 | LGR | 9LGRB0013 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 13 | 35 | 35 | 9LGR001CR | 9LGR002CR | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 2 x 2,5mm2
9 | LGR | 9LGRB0014 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 14 | 14 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 2 x 2,5mm2
9 | LGR | 9LGRB0015 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 12 | 12 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 2 x 2,5mm2
9 | LGR | 9LGRB0016 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 12 | 12 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 2 x 2,5mm2
9 | LGR | 9LGRB0017 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 23 | 23 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 2 x 2,5mm2
9 | LGR | 9LGRB0018 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 17 | 17 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 3 x 50mm2
9 | LGR | 9LGRB0019 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 22 | 18 | 18 | 9LGR002CR | 9GEV007TP | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 3 x 2,5mm2
9 | LGR | 9LGRB0020 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 14 | 0 | 40 | 9LGR003CR | 9LGR003AR | A 01 0G1111A2 0G1C A 01 0G1111A2 0G1C |  | 3 x 35mm2
9 | LGR | 9LGRB0021 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 4 | 9LGR001CR | 9LGR003CR | K9LGR B0021 A IN 03 35 A 9J22J 9LGR 001CR 9LGR 001CR 9J22J 9J22J 38BN 9LGR 003CR 4 |  | 3 x 35mm2
9 | LGR | 9LGRB0022 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0022 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0023 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 9 | 9LGR003AR | 9LGR009CR | K9LGR B0023 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 9 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0024 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0024 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0025 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0025 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0026 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0026 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0027 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0027 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0028 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0028 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0029 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 10 | 9LGR003AR | 9LGR009CR | K9LGR B0029 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 10 |  | 3 x 2,5mm2
9 | LGR | 9LGRB0030 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 4Y | YES | ALSTHOM | EMS | 20 | 0 | 5 | 9LGR003AR | 9LGR009CR | K9LGR B0030 A IN 03 2.5 A 9J22J 9J22J 38BN 9LGR 003AR 9J22J 9J22J 38BN 9LGR 009CR 5 |  | 3 x 2,5mm2
9 | LHA | 9LHAA0007 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 156 | 159 | 159 | 9LHS001AR | 9LHC0501 | A 01 9D1180C1 9D181 A 01 9D1180C1 9D181 A 02 9D11H0A1 9D181 A 03 9D00H0A1 9D083 A 04 9D0000A1 9D082 A 04 9D0000A1 9D083 A 05 1D0000B1 1D042 A 06 1D0000C1 1D042 A 07 2D0000D1 2D022 A 08 2D00W3A1 2D022 A 09 2L11Z0A1 2L142 A 10 2L1110A1 2L142 A 10 2L1110A1 2L146 A 10 2L1110A1 2L150 A 11 9L1110A1 9L115 A 12 9L11JAA1 9L115 A 13 2L22JAA1 2L244 A 14 9L33JAA1 9L307 A 15 9L3358A1 9L307 A 16 9L3358B1 9L307 A 17 9L3358C1 9L307 A 17 9L3358C1 9L312 A 18 9L3358D1 9L312 A 19 9L3359B2 9L312 A 20 9L3359A2 9L312 |  | 1 x 400mm2
9 | LHA | 9LHAA0008 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 69 |  |  | 9LHC0201 | 1LHA0701
9 | LHA | 9LHAA0009 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 73 |  |  | 9LHC0201 | 1LHA0701
9 | LHB | 9LHBA0007 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 69 |  |  | 9LHC0201 | 1LHA0701
9 | LHB | 9LHBA0008 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 15 |  |  | 9LHC0101 | 1LHB0801
9 | LHB | 9LHBA0009 | OUT | OUT | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 18 |  |  | 9LHC0101 | 1LHB0801
9 | LHC | 9LHCA0001 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 13 | 159 | 159 | 9LHC0101 | 1LHB0801 | A 01 9D1180C1 9D181 A 01 9D1180C1 9D181 A 02 9D11H0A1 9D181 A 03 9D00H0A1 9D083 A 04 9D0000A1 9D082 A 04 9D0000A1 9D083 A 05 1D0000B1 1D042 A 06 1D0000C1 1D042 A 07 2D0000D1 2D022 A 08 2D00W3A1 2D022 A 09 2L11Z0A1 2L142 A 10 2L1110A1 2L142 A 10 2L1110A1 2L146 A 10 2L1110A1 2L150 A 11 9L1110A1 9L115 A 12 9L11JAA1 9L115 A 13 2L22JAA1 2L244 A 14 9L33JAA1 9L307 A 15 9L3358A1 9L307 A 16 9L3358B1 9L307 A 17 9L3358C1 9L307 A 17 9L3358C1 9L312 A 18 9L3358D1 9L312 A 19 9L3359B2 9L312 A 20 9L3359A2 9L312
9 | LHC | 9LHCA0002 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 156 | 167 | 167 | 9LHS001AR | 9LHC0501 | K9LHC A0002 A IN 01 400 MTAL 9D281 9LHS 001AR 9LHS 001AR 9L411 9LHC 0501 9LHC 0501 167 |  | 1 x 400mm2 | [5 empty] | not in pericles
9 | LHC | 9LHCA0003 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 156 | 143 | 143 | 9LHS001AR | 9LHC0501 | K9LHC A0003 A IN 01 400 MTAL 9D281 9LHS 001AR 9LHS 001AR 9L411 9LHC 0501 9LHC 0501 143 |  | 1 x 400mm2 | [5 empty] | not in pericles
9 | LHS | 9LHSA0001 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 11 | 15 | 15 | 9LHS001GA | 9LHS001AR | A 01 9D11A5A1 9D182 A 01 9D11A5A1 9D182 A 02 9D1190A1 9D182 A 03 9D1180A1 9D181 A 04 9D1180B1 9D181 |  | 1 x 400mm2
9 | LHS | 9LHSA0002 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 11 | 15 | 15 | 9LHS001GA | 9LHS001AR | K9LHS A0002 A IN 01 400 MTAL 9D282 9LHS 001GA 9LHS 001GA 9D281 9LHS 001AR 9LHS 001AR 15 |  | 1 x 400mm2 | [5 empty] | not in pericles
9 | LHS | 9LHSA0003 | IN | IN | OUT | YES | 1 | 400 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 11 | 20 | 20 | 9LHS001GA | 9LHS001AR | K9LHS A0003 A IN 01 400 MTAL 9D282 9LHS 001GA 9LHS 001GA 9D281 9LHS 001AR 9LHS 001AR 20 |  | 1 x 400mm2 | [5 empty] | not in pericles
9 | LHS | 9LHSB0001 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 14 | 20 | 20 | 9LLV0204 | 9LHS001CO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0002 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 14 | 20 | 20 | 9LLV0205 | 9LHS002CO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0003 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 61 | 61 | 9LLV0206 | 9LHS004MO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 A 04 9D2290A1 9D283 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0004 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 23 | 42 | 42 | 9LLV0304 | 9LHS006MO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D1191B1 9D182 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0005 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 31 | 40 | 40 | 9LLV0208 | 9LHS001PO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D1191B1 9D182 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0006 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 31 | 43 | 43 | 9LLV0209 | 9LHS002PO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D1191B1 9D182 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0007 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 32 | 47 | 47 | 9LLV0210 | 9LHS003PO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D1191B1 9D182 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0008 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 16 | 23 | 23 | 9LLV0211 | 9LHS005PO | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 A 04 9D2290A1 9D283 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0009 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 40 | 40 | 9LLV0212 | 9LHS001RE | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 A 04 9D2290A1 9D283 |  | 3 x 16mm2
9 | LHS | 9LHSB0010 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 18 | 38 | 38 | 9LLV0312 | 9LHS002RE | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D1191B1 9D182 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0011 | IN | IN | OUT | YES | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 11 | 15 | 15 | 9LLV0311 | 9LHS003RE | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 |  | 2 x 2,5mm2
9 | LHS | 9LHSB0012 | IN | IN | OUT | YES | 3 | 70 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 32 | 50 | 50 | 9LLV0107 | 9LHS001ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 A 11 9D3390B1 9D383 |  | 3 x 70mm2
9 | LHS | 9LHSB0013 | IN | IN | OUT | YES | 3 | 70 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 32 | 46 | 46 | 9LLV0105 | 9LHS002ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 A 11 9D3390B1 9D383 |  | 3 x 70mm2
9 | LHS | 9LHSB0014 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 29 | 38 | 38 | 9LLV0308 | 9LHS003ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 |  | 3 x 16mm2
9 | LHS | 9LHSB0015 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 29 | 40 | 40 | 9LLV0307 | 9LHS004ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 |  | 3 x 16mm2
9 | LHS | 9LHSB0016 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 29 | 41 | 41 | 9LLV0306 | 9LHS005ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 |  | 3 x 16mm2
9 | LHS | 9LHSB0017 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 29 | 45 | 45 | 9LLV0305 | 9LHS006ZV | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181C1 9D181 A 03 9D1181D1 9D181 A 04 9D1181E1 9D181 A 05 9D1184A1 9D181 A 06 9D1191C1 9D182 A 07 9D11A4A1 9D182 A 08 9D22A4A1 9D282 A 09 9D33A4A1 9D383 A 10 9D33A4B1 9D383 |  | 3 x 16mm2
9 | LHS | 9LHSB0019 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 12 | 50 | 50 | 9LLV0207 | 9LHS001RS | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0021 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 15 | 19 | 19 | 9LHS002AR | 9LHS001GA | A 01 9D1181D1 9D181 A 01 9D1181D1 9D181 A 02 9D1181E1 9D181 A 03 9D1184A1 9D181 A 04 9D1191C1 9D182 |  | 3 x 16mm2
9 | LHS | 9LHSB0022 | IN | IN | OUT | YES | 2 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 0 | 0 | 1 | 9LHS002AR | 9LHS001GA | K9LHS B0022 A IN 02 16 A 9D281 9LHS 002AR 9LHS 002AR 9D282 9LHS 001GA 9LHS 001GA 1 |  | 2 x 16mm2
9 | LHS | 9LHSB0023 | IN | IN | OUT | YES | 2 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 15 | 30 | 1 | 9LHS002AR | 9LHS001GA | A 01 9D1181D1 9D181 A 01 9D1181D1 9D181 A 02 9D1181E1 9D181 A 03 9D1184A1 9D181 A 04 9D1191C1 9D182 |  | 2 x 6mm2
9 | LHS | 9LHSB0024 | IN | IN | OUT | YES | 2 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 15 | 33 | 33 | 9LHS002AR | 9LHS001GA | A 01 9D1181D1 9D181 A 01 9D1181D1 9D181 A 02 9D1181E1 9D181 A 03 9D1184A1 9D181 A 04 9D1191C1 9D182 |  | 2 x 35mm2
9 | LHS | 9LHSB0025 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 16 | 16 | 9LLV0212 | 9LHS004RE | A 01 9D1181B1 9D181 A 01 9D1181B1 9D181 A 02 9D1181A1 9D181 A 03 9D22B2A1 9D283 A 04 9D2290A1 9D283 |  | 3 x 16mm2
9 | LHS | 9LHSB0026 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 168 | 189 | 189 | 9LLM001TR | 9LHS007ZV | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 A 02 9L3330U3 9L310 A 03 9L3330T3 9L310 A 03 9L3330T3 9L312 A 04 9L3358C2 9L307 A 04 9L3358C2 9L312 A 05 9L3358B2 9L307 A 06 9L3358A2 9L307 A 07 9L33JAA3 9L307 A 08 2L22JAA3 2L244 A 09 9L11JAA3 9L115 A 10 9L1110A2 9L115 A 11 2L1110A2 2L142 A 11 2L1110A2 2L146 A 11 2L1110A2 2L150 A 12 2L11Z0A2 2L142 A 13 2D00W3A2 2D022 A 14 2D0000D2 2D022 A 15 1D0000C2 1D042 A 16 1D0000B2 1D042 A 17 9D0000A2 9D082 A 17 9D0000A2 9D083 A 18 9D00H0A2 9D083 A 19 9D11H0A2 9D181 A 20 9D1184B1 9D181 A 21 9D1181E1 9D181 A 22 9D1181D1 9D181 A 23 9D1181C1 9D181 A 24 9D1181B1 9D181 A 25 9D1181A1 9D181 |  | 3 x 2,5mm2
9 | LHS | 9LHSB0117 | IN | IN | OUT | YES | 2 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 4 | 0 | 1 | 9LHS003AR | 9LHS002AR | A 01 9D1181D1 9D181 A 01 9D1181D1 9D181 |  | 2 x 1,5mm2
9 | LHS | 9LHSB0900 | IN | IN | OUT | NO | NIA | NIA | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | [7 empty] | No Information Available | [5 empty] | not in pericles
9 | LHS | 9LHSB0901 | IN | IN | OUT | NO | NIA | NIA | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | [7 empty] | No Information Available | [5 empty] | not in pericles
9 | LHS | 9LHSB0902 | IN | IN | OUT | NO | NIA | NIA | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | [7 empty] | No Information Available | [5 empty] | not in pericles
9 | LHS | 9LHSB0903 | IN | IN | OUT | NO | NIA | NIA | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | [7 empty] | No Information Available | [5 empty] | not in pericles
9 | LHS | 9LHSB0904 | IN | IN | OUT | NO | NIA | NIA | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | [7 empty] | No Information Available | [5 empty] | not in pericles
9 | LHS | 9LHSB0905 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LHS401CR | 9LHS005AR | E9LHS B0905 A IN 03 2.5 A 9D281 9LHS 005AR 9LHS 005AR 9D282 9LHS 401CR 9LHS 401CR 0 |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LHS | 9LHSB0910 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9DSDC01CR | 9LHS002AR |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LKI | 9LKIA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 99 | 94 | 94 | 9LGI0203 | 9LKI001TR | A 01 9L3361B1 9L310 A 01 9L3361B1 9L310 A 02 9L3361A1 9L310 A 03 9L3339Y1 9L310 A 04 9L3339X1 9L310 A 05 9L3339W1 9L310 A 06 9L3339V1 9L310 A 07 9L3362A1 9L310 A 08 9L3362B1 9L310 A 08 9L3362B1 9L312 A 09 9L3362C1 9L312 A 10 9N3340A1 9N395 A 11 9N3340B1 9N395 A 12 9N3340C1 9N395 A 13 9N33A3A1 9N395 A 14 9N22A3A1 9N2A34 A 15 9N2200A1 9N2A34 A 16 9N2200B1 9N2A34 A 16 9N2200B1 9N2C34 A 17 9N2200C1 9N2C34 A 18 9N2200D1 9N2C34 A 19 9N2225A1 9N2C45 A 20 9N2258A1 9N2C45 |  | 50
9 | LKI | 9LKIB0001 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 21 | 36 | 36 | 9LKI0905 | 9LKIB10CR | A 01 9N2221E3 9N2C45 A 01 9N2221E3 9N2C45 A 02 9N2221D3 9N2C45 A 03 9N2221C3 9N2C45 A 04 9N2221B3 9N2C47 A 05 9N2200D2 9N2C34 A 06 9N2200E2 9N2C34 |  | 70
9 | LKI | 9LKIB0002 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 45 | 58 | 58 | 9LKI0903 | 9LKIE20CR | A 01 9N2222E2 9N2C45 A 01 9N2222E2 9N2C45 A 02 9N2224A1 9N2C47 A 03 9N22C0A1 9N2C47 A 04 1N33C0A1 1N3C76 A 05 1N33C0B1 1N3C76 A 06 1N44C0A1 1N4C76 A 07 1N44C0B1 1N4C76 A 08 1N55C0A1 1N5C76 A 09 1N5500A1 1N5C76 A 10 9N5500A1 9N5A01 A 11 9N5500B1 9N5A01 A 12 9N5500C1 9N5A01 A 13 9N5505A1 9N5A01 A 13 9N5505A1 9N5B02 |  | 70
9 | LKI | 9LKIB0003 | OUT | OUT | OUT | NO | 3 | 35 | A | [5 empty] | NO |  |  | 237 | 240 | 240 | 9LKI0507 | 9LKI001CR | A 01 9N2221G1 9N2C45 A 01 9N2221G1 9N2C45 A 02 9N2221F1 9N2C45 A 03 9N2221E1 9N2C45 A 04 9N2221D1 9N2C45 A 05 9N2260A2 9N2C45 A 06 9N2260B2 9N2C45 A 07 9N2260C2 9N2C45 A 08 9N2263A1 9N2D34 A 09 9N2203A1 9N2D34 A 09 9N2203A1 9N2D70 A 10 9N2201C1 9N2B34 A 10 9N2201C1 9N2D70 A 11 9N2201B1 9N2B34 A 12 9N2201A1 9N2B34 A 13 9N22B2A1 9N2B34 A 14 9N33B2A1 9N395 A 15 9N3342C2 9N395 A 16 9N33A8A1 9N395 A 17 9N3340A3 9N395 A 18 9L3385A1 9L312 A 19 9L3385B1 9L310 A 19 9L3385B1 9L312 A 20 9L3385C1 9L310 A 21 9L3385D1 9L310 A 22 9L3385E1 9L310 A 23 9L3385F1 9L310 A 24 2L3312A1 2L346 A 25 2L3319C1 2L346 A 26 2L3319B1 2L346 A 27 2L3325A1 2L346 A 28 2L3325B1 2L346 A 29 2L3325C1 2L344 A 29 2L3325C1 2L346 A 30 2L3325D1 2L344 A 31 2L3325E1 2L344 A 32 2L3325F1 2L341 A 32 2L3325F1 2L344 A 33 2M3302A1 2M3? A 34 2M22HCA1 2M2? A 35 2M2205A1 2M2? A 36 2M225HA1 2M2? A 37 2M115HA1 2M1? A 38 2M1120A1 2M1? A 39 2M1120B1 2M1? |  | 35
9 | LKI | 9LKIB0004 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9LKI001CR | 9LKI002CR | IND (SITE RUN) |  | 16
9 | LKI | 9LKIB0005 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9LKI001CR | 9ACO001RS | IND (SITE RUN) |  | 2.5
9 | LKI | 9LKIB0006 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 20 | 9LKI001CR | 9APA001RS | IND (SITE RUN) |  | 2.5
9 | LKI | 9LKIB0007 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 27 | 9LKI001CR | 9CEX001RS | IND (SITE RUN) |  | 2.5
9 | LKI | 9LKIB0008 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9LKI002CR | 9RCP001RS | IND (SITE RUN) |  | 2.5
9 | LKI | 9LKIB0009 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 0 | 1 | 9LKI002CR | 9RCP001PO | IND (SITE RUN) |  | 2.5
9 | LKI | 9LKIB0904 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKIB10CR | 9DVN001JF |  |  | 3 X 2.5mm2 | [5 empty] | not in pericles
9 | LKK | 9LKKA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 14 | 20 | 20 | 9LGI0201 | 9LKK001TR | A 01 9L3361B1 9L310 A 01 9L3361B1 9L310 A 02 9L3361A1 9L310 A 03 9L3339Y1 9L310 A 04 9L3339X1 9L310 A 05 9L3339W1 9L310 |  | 50
9 | LKK | 9LKKB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | SPARE | [9 empty] | not in pericles
9 | LKK | 9LKKB0905 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKK612JA | 9DMM002BX |  |  | 4 x 185mm2 Armoured | [5 empty] | not in pericles
9 | LKM | 9LKMA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 342 | 255 | 255 | 9LGI0402 | 9LKM001TR | A 01 9L3361B1 9L310 A 01 9L3361B1 9L310 A 02 9L3361A1 9L310 A 03 9L3339Y1 9L310 A 04 9L3339X1 9L310 A 05 9L3339W1 9L310 A 06 9L3339V1 9L310 A 07 9L3339U1 9L310 A 08 9L3339T1 9L310 A 08 9L3339T1 9L312 A 09 1L3339T1 1L306 A 10 1L3339S1 1L306 A 11 1L3339R1 1L306 A 12 1L3339P1 1L306 A 13 1L3339N1 1L306 A 14 1L3339M1 1L306 A 15 1L3339L1 1L306 A 16 1L3339K1 1L306 A 17 1L3339J1 1L306 A 18 1L3339H1 1L304 A 18 1L3339H1 1L306 A 19 1L3339G1 1L304 A 20 1L3339F1 1L304 A 21 1L3339E1 1L304 A 22 1L3339D1 1L304 A 23 1L3339C1 1L304 A 24 1L3339B1 1L304 A 25 1L3341A1 1L304 A 26 1L3341B1 1L304 A 27 1L3319C2 1L304 A 28 1L33JAA1 1L304 A 29 1L22JAA1 1L204 A 30 1L11JAA1 1L105 A 31 1L1102J1 1L105 A 32 1L1102H1 1L105 A 33 1L1102G1 1L105 A 34 1L1102F1 1L101 A 34 1L1102F1 1L113 A 35 1L1102E1 1L101 A 36 1L1102D1 1L101 A 37 1L1102C1 1L101 A 37 1L1102C1 1L102 A 38 1L1102B1 1L102 A 38 1L1102B1 1L103 A 38 1L1102B1 1L104 A 39 1L1102A1 1L104 A 39 1L1102A1 1L114 A 40 0G1120D1 0G1C A 41 0G1120C1 0G1C A 42 0G1120B1 0G1C A 43 0G1120A1 0G1B A 44 0G11Z1A1 0G1B A 45 0G1193A1 0G1B |  | 50
9 | LKM | 9LKMB0901 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKM302JA | 9SRO001TB |  |  | 4c x 240mm2 PVC SWA | [5 empty] | not in pericles
9 | LKM | 9LKMB0902 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKM302JA | 9SRO001TB |  |  | 4c x 240mm2 PVC SWA | [5 empty] | not in pericles
9 | LKN | 9LKNA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 253 | 258 | 258 | 9LGI0202 | 9LKN001TR | A 01 9L3361B1 9L310 A 01 9L3361B1 9L310 A 02 9L3361A1 9L310 A 03 9L3339Y1 9L310 A 04 9L3339X1 9L310 A 05 9L3339W1 9L310 A 06 9L3339V1 9L310 A 07 9L3339U1 9L310 A 08 9L3339T1 9L310 A 08 9L3339T1 9L312 A 09 1L3339T1 1L306 A 10 1L3339S1 1L306 A 11 1L3339R1 1L306 A 12 1L3339P1 1L306 A 13 1L3339N1 1L306 A 14 1L3339M1 1L306 A 15 1L3339L1 1L306 A 16 1L3339K1 1L306 A 17 1L3339J1 1L306 A 18 1L3339H1 1L304 A 18 1L3339H1 1L306 A 19 1L3339G1 1L304 A 20 1L3339F1 1L304 A 21 1L3339E1 1L304 A 22 1L3339D1 1L304 A 23 1L3339C1 1L304 A 24 1L3339B1 1L304 A 25 1L3341A1 1L304 A 26 1L3341B1 1L304 A 27 1L3319C2 1L304 A 28 1L33JAA2 1L304 A 29 1L22JAA2 1L204 A 30 1L11JAA2 1L105 A 31 1L1102J1 1L105 A 32 1L1102H1 1L105 A 33 1L1102G1 1L105 A 34 1L1102F1 1L101 A 34 1L1102F1 1L113 A 35 1L1102E1 1L101 A 36 1L1102D1 1L101 A 37 1L1102C1 1L101 A 37 1L1102C1 1L102 A 38 1L1102B1 1L102 A 38 1L1102B1 1L103 A 38 1L1102B1 1L104 A 39 1L1102A1 1L104 A 39 1L1102A1 1L114 A 40 0G1120D1 0G1C A 41 0G1121A1 0G1C A 42 0G11Z3A1 0G1C A 43 0G1105A1 0G1C A 44 9Y2200A1 9Y20Y A 45 9Y2200B1 9Y20Y |  | 50
9 | LKN | 9LKNB0001 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 7 | 13 | 13 | 9LKN0404 | 9LKN010CR | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201B1 9Y20Y |  | 70
9 | LKN | 9LKNB0002 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 20 | 14 | 14 | 9LKN010CR | 9LKN011CR | IND (SITE RUN) |  | 70
9 | LKN | 9LKNB0003 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 20 | 31 | 31 | 9LKN011CR | 9LKN012CR | IND (SITE RUN) |  | 70
9 | LKN | 9LKNB0004 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 106 | 91 | 91 | 9LKN010CR | 9LKN020CR | A 01 9Y2201B1 9Y20Y A 01 9Y2201B1 9Y20Y A 02 9Y2201A1 9Y20Y A 03 9Y2200A2 9Y20Y A 04 0G1105A2 0G1C A 05 0G11Z3A2 0G1C A 06 0G1121A2 0G1C A 07 0G1120C2 0G1C A 08 0G1120B2 0G1C A 09 0G1120A2 0G1B A 10 0G11Z1A2 0G1B A 11 0G1193A2 0G1B |  | 70
9 | LKP | 9LKPA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 482 | 393 | 393 | 9LGI0401 | 9LKP001TR | A 01 9L3361B1 9L310 A 01 9L3361B1 9L310 A 02 9L3361A1 9L310 A 03 9L3339Y1 9L310 A 04 9L3339X1 9L310 A 05 9L3339W1 9L310 A 06 9L3339V1 9L310 A 07 9L3339U1 9L310 A 08 9L3339T1 9L310 A 08 9L3339T1 9L312 A 09 1L3339T1 1L306 A 10 1L3339S1 1L306 A 11 1L3339R1 1L306 A 12 1L3339P1 1L306 A 13 1L3339N1 1L306 A 14 1L3339M1 1L306 A 15 1L3339L1 1L306 A 16 1L3339K1 1L306 A 17 1L3339J1 1L306 A 18 1L3339H1 1L304 A 18 1L3339H1 1L306 A 19 1L3339G1 1L304 A 20 1L3339F1 1L304 A 21 1L3339E1 1L304 A 22 1L3339D1 1L304 A 23 1L3339C1 1L304 A 24 1L3339B1 1L304 A 25 1L3341A1 1L304 A 26 1L3341B1 1L304 A 27 1L3319C2 1L304 A 28 1L33JAA1 1L304 A 29 1L22JAA1 1L204 A 30 1L11JAA1 1L105 A 31 1L1102J1 1L105 A 32 1L1102H1 1L105 A 33 1L1102G1 1L105 A 34 1L1102F1 1L101 A 34 1L1102F1 1L113 A 35 1L1102E1 1L101 A 36 1L1102D1 1L101 A 37 1L1102C1 1L101 A 37 1L1102C1 1L102 A 38 1L1102B1 1L102 A 38 1L1102B1 1L103 A 38 1L1102B1 1L104 A 39 1L1102A1 1L104 A 39 1L1102A1 1L114 A 40 0G1120D1 0G1C A 41 0G1120C1 0G1C A 42 0G1120B1 0G1C A 43 0G1120A1 0G1B A 44 0G11Z0A1 0G1B A 45 0G1191A1 0G1B A 46 9H2201C1 9H2? A 47 9H2201B1 9H2? A 48 9H2201A1 9H2? |  | 50
9 | LKP | 9LKPB0001 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 4 | 12 | 12 | 9LKP0511 | 9LKP010CR | A 01 9H2202A1 9H2? A 01 9H2202A1 9H2? |  | 70
9 | LKX | 9LKXB0001 | OUT | OUT | OUT | YES | 3 | 2.5 | [6 empty] | NO | [5 empty] | 9LKX101JA | 6WFI001AR | A 01 2C1143A1 2C1A A 01 2C1143A1 2C1A A 02 2C1108B1 2C1A A 03 2C1108A1 2C1A |  | 4 C, 35mm2,30m
9 | LKX | 9LKXB0002 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 65 | 59 | 65 | 9LKX0101 | 9LKX001PR | A 01 1C1106C1 1C1A A 01 1C1106C1 1C1A A 02 1C1119A1 1C1A A 03 1C1144B1 1C1A A 04 1C1144C1 1C1A A 05 1C1144D1 1C1A A 06 1C1144E1 1C1A |  | 50
9 | LKX | 9LKXB0003 | OUT | OUT | OUT | YES | 3 | 150 | A | [5 empty] | NO |  |  | 99 | 107 | 107 | 9LKP0309 | 9LKX001TB | A 01 9H2200D4 9H2? A 01 9H2200D4 9H2? A 02 9H2200C4 9H2? A 03 9H2200B4 9H2? A 04 9H2200A4 9H2? A 05 0G1189A1 0G1H A 06 2C00T0A1 2C0A A 07 2C0001D3 2C0A A 08 2C0009A3 2C0A A 09 2C1109A2 2C1A A 10 2C1109B2 2C1A A 11 2C1109C2 2C1A A 12 2C1143C1 2C1A A 13 2C1143B1 2C1A A 14 2C1143A1 2C1A |  | 150
9 | LKX | 9LKXB0004 | OUT | OUT | OUT | YES | 3 | 150 | A | [5 empty] | NO |  |  | 99 | 116 | 116 | 9LKP0309 | 9LKX001TB | A 01 9H2200D4 9H2? A 01 9H2200D4 9H2? A 02 9H2200C4 9H2? A 03 9H2200B4 9H2? A 04 9H2200A4 9H2? A 05 0G1189A1 0G1H A 06 2C00T0A1 2C0A A 07 2C0001D3 2C0A A 08 2C0009A3 2C0A A 09 2C1109A2 2C1A A 10 2C1109B2 2C1A A 11 2C1109C2 2C1A A 12 2C1143C1 2C1A A 13 2C1143B1 2C1A A 14 2C1143A1 2C1A |  | 150
9 | LKX | 9LKXB0005 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 9LKX0204 | 9LKX003CR |  |  | 6 | [5 empty] | not in pericles
9 | LKZ | 9LKZA0001 | OUT | OUT | OUT | YES | 3 | 50 | MTAL | [5 empty] | NO |  |  | 88 | 104 | 1 | 9LGI0601 | 9LKZ001TR | A 01 9L3369D1 9L310 A 01 9L3369D1 9L310 A 02 9L3369C1 9L310 A 03 9L3369B1 9L310 A 04 9L3369A1 9L310 A 05 9L3363A1 9L310 A 06 2L3310C1 2L346 A 07 2L3310B1 2L346 A 08 2L3310A1 2L346 A 09 2L33JCA2 2L346 A 10 2L22JCA2 2L244 A 11 2L11JCA2 2L149 A 12 2L1118B1 2L149 A 13 2L1118C1 2L149 A 14 2L1120A1 2L141 A 14 2L1120A1 2L145 A 14 2L1120A1 2L149 A 14 2L1120A1 2L153 A 15 2L1120B1 2L141 A 16 2L1120C1 2L141 A 17 2L1120D1 2L141 |  | 50
9 | LKZ | 9LKZB0900 | OUT | OUT | OUT | YES | 3 | 16 | [6 empty] | NO | [5 empty] | 9LKZ001TB | 9LXZ001RD |  |  | 3c x 16mm2 | [5 empty] | not in pericles
9 | LLH | 9LLHB0900 | IN | IN | OUT | NO | 2 | 4 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LLH001TB | 1LLX001TB | E9LLH B0900 A IN 02 4 NA 9H000 9LLH 001TB 9LLH 001TB 9H000 1LLX 001TB 1LLX 001TB 0 |  | 4 x 1.5mm2 | [5 empty] | not in pericles
9 | LLH | 9LLHB0901 | IN | IN | OUT | NO | 2 | 4 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LLH001TB | 2LLX001TB | E9LLH B0901 A IN 02 4 NA 9H000 9LLH 001TB 9LLH 001TB 9H000 2LLX 001TB 2LLX 001TB 0 |  | 4 x 1.5mm2 | [5 empty] | not in pericles
9 | LLH | 9LLHB0902 | IN | IN | OUT | NO | 2 | 4 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LLH001TB | 9LLX001TB | E9LLH B0902 A IN 02 4 NA 9H000 9LLH 001TB 9LLH 001TB 9H000 9LLX 001TB 9LLX 001TB 0 |  | 4 x 1.5mm2 | [5 empty] | not in pericles
9 | LLM | 9LLMB0001 | OUT | OUT | OUT | NO | 3 | 185 | A | [5 empty] | NO |  |  | 32 | 34 | 34 | 1LLE0103 | 9LLM001CR | A 01 1L3330M3 1L306 A 01 1L3330M3 1L306 A 02 1L3330N3 1L306 A 03 1L3330P3 1L306 A 04 1L3330R3 1L306 A 05 1L3330S3 1L306 A 06 1L3330T3 1L306 A 07 9L3330T3 9L310 A 07 9L3330T3 9L312 A 08 9L3330U3 9L310 A 09 9L3362A2 9L310 |  | 185
9 | LLM | 9LLMB0002 | OUT | OUT | OUT | NO | 3 | 185 | A | [5 empty] | NO |  |  | 31 | 53 | 53 | 2LLE0103 | 9LLM002CR | A 01 2L3316D1 2L346 A 01 2L3316D1 2L346 A 02 2L3316C1 2L346 A 03 2L3319C1 2L346 A 04 2L3312A1 2L346 A 05 9L3385F1 9L310 A 06 9L3385E1 9L310 A 07 9L3385D1 9L310 A 08 9L3385C1 9L310 |  | 185
9 | LLM | 9LLMB0003 | OUT | OUT | OUT | YES | 3 | 185 | A | [5 empty] | NO |  |  | 17 | 13 | 13 | 9LLM001CR | 9LLM001TR | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 |  | 185
9 | LLM | 9LLMB0005 | OUT | OUT | OUT | NO | 2 | 35 | A | [5 empty] | NO |  |  | 108 | 133 | 133 | 9LLM001TR | 9DTVA01AR | A 01 9L3362A2 9L310 A 01 9L3362A2 9L310 A 02 9L3330U3 9L310 A 03 9L3330T3 9L310 A 03 9L3330T3 9L312 A 04 1L3330T3 1L306 A 05 1L3330S3 1L306 A 06 1L3330R3 1L306 A 07 1L3330P3 1L306 A 08 1L3330N3 1L306 A 09 1L3330M3 1L306 A 10 1L3330L3 1L304 A 10 1L3330L3 1L306 A 11 1L3330K3 1L304 A 12 1L3330J3 1L304 A 13 1L3330H3 1L304 A 14 1L3330G3 1L304 A 15 1L3330F3 1L304 A 16 1L3333A1 1L304 A 17 1L3333B1 1L304 A 18 1L3333C1 1L304 A 19 1L3333D1 1L304 A 20 1L3317F2 1L304 A 21 1L3317G2 1L304 A 22 1L33JNB2 1L304 A 23 1L44JNA2 1L404 A 24 1L55JNA2 1L506 A 25 1L66JNA2 1L605 A 26 1L6640E2 1L605 A 27 1L6640D2 1L605 A 28 1L6640C2 1L601 A 29 1L6640B2 1L601 |  | 35
9 | LLM | 9LLMB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LLM001TR | 9DTVE016A |  |  | 25 mm2 SWA 2Core | [5 empty] | not in pericles
9 | LLV | 9LLVB0001 | IN | IN | OUT | YES | 3 | 150 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 157 | 165 | 165 | 9LLZ0103 | 9LLV001TB | A 01 9L3380A2 9L312 A 01 9L3380A2 9L312 A 02 9L3380B2 9L312 A 03 9L3358C2 9L307 A 03 9L3358C2 9L312 A 04 9L3358B2 9L307 A 05 9L3358A2 9L307 A 06 9L33JAA3 9L307 A 07 2L22JAA3 2L244 A 08 9L11JAA3 9L115 A 09 9L1110A2 9L115 A 10 2L1110A2 2L142 A 10 2L1110A2 2L146 A 10 2L1110A2 2L150 A 11 2L11Z0A2 2L142 A 12 2D00W3A2 2D022 A 13 2D0000D2 2D022 A 14 1D0000C2 1D042 A 15 1D0000B2 1D042 A 16 9D0000A2 9D082 A 16 9D0000A2 9D083 A 17 9D00H0A2 9D083 A 18 9D11H0A2 9D181 A 19 9D1184B1 9D181 A 20 9D1181E1 9D181 A 21 9D1181D1 9D181 A 22 9D1181C1 9D181 A 23 9D1181B1 9D181 |  | 3 x 150mm2
9 | LLV | 9LLVB0002 | IN | IN | OUT | YES | 3 | 150 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 157 | 190 | 190 | 9LLZ0103 | 9LLV001TB | A 01 9L3380A2 9L312 A 01 9L3380A2 9L312 A 02 9L3380B2 9L312 A 03 9L3358C2 9L307 A 03 9L3358C2 9L312 A 04 9L3358B2 9L307 A 05 9L3358A2 9L307 A 06 9L33JAA3 9L307 A 07 2L22JAA3 2L244 A 08 9L11JAA3 9L115 A 09 9L1110A2 9L115 A 10 2L1110A2 2L142 A 10 2L1110A2 2L146 A 10 2L1110A2 2L150 A 11 2L11Z0A2 2L142 A 12 2D00W3A2 2D022 A 13 2D0000D2 2D022 A 14 1D0000C2 1D042 A 15 1D0000B2 1D042 A 16 9D0000A2 9D082 A 16 9D0000A2 9D083 A 17 9D00H0A2 9D083 A 18 9D11H0A2 9D181 A 19 9D1184B1 9D181 A 20 9D1181E1 9D181 A 21 9D1181D1 9D181 A 22 9D1181C1 9D181 A 23 9D1181B1 9D181 |  | 3 x 150mm2
9 | LLX | 9LLXB0900 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 70 | 9LLH001TB | JDT5200AN | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LLX | 9LLXB0901 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 10 | 9LLH001TB | VENTUNIT | IND (SITE RUN) |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | LLZ | 9LLZA0001 | IN | IN | OUT | YES | 3 | 50 | MTAL (A) | PVC | XLPE | 6,6kV | IRT, OHT, V&T, VLF-TD and VLF-PD | 4RO | NO | ALSTHOM | EMS | 14 | 16 | 16 | 9LHC0602 | 9LLZ001TR | A 01 9L3359B4 9L312 A 01 9L3359B4 9L312 A 02 9L3310Z2 9L312 A 03 9L3380A3 9L312 |  | 3 x 50mm2
9 | LLZ | 9LLZB0001 | IN | IN | OUT | YES | 3 | 185 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 1 | 9LKK0103 | 9LLZ001TB | A 01 9L3357G1 9L310 A 01 9L3357G1 9L310 A 02 9L3357F1 9L310 A 03 9L3357E1 9L310 A 04 9L3380B2 9L312 A 05 9L3380A2 9L312 |  | 3 x 185mm2
9 | LLZ | 9LLZB0002 | IN | IN | OUT | YES | 3 | 185 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 1 | 9LKK0103 | 9LLZ001TB | A 01 9L3357G1 9L310 A 01 9L3357G1 9L310 A 02 9L3357F1 9L310 A 03 9L3357E1 9L310 A 04 9L3380B2 9L312 A 05 9L3380A2 9L312 |  | 3 x 185mm2
9 | LNE | 9LNEB0901 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 2LNE500CR | PN2L319 | E9JDT B0901 A IN 03 2.5 A 2W441 2LNE 500CR 2LNE 500CR 2W370 PN2 L319 PN2 L319 0 |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNE | 9LNEB0902 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 2LMA500CR | PN2L316 | E9JDT B0902 A IN 03 2.5 A 2W466 2LMA 500CR 2LMA 500CR 2W370 PN2 L316 PN2 L316 0 |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0001 | IN | IN | OUT | YES | 2 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 17 | 22 | 22 | 9LKI0305 | 9LNF001TR | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2222D1 9N2C45 A 07 9N2222C1 9N2C45 A 08 9N2222B1 9N2C47 A 09 9N2222A1 9N2C47 |  | 2 x 6mm2
9 | LNF | 9LNFB0002 | IN | IN | OUT | NO | 2 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 11 | 15 | 15 | 9LNF001DL | 9LNF0141 | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 |  | 2 x 16mm2
9 | LNF | 9LNFB0003 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 79 | 93 | 93 | 9LNF0143 | 9LBG0150 | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N2256A1 9N2C70 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N3340A2 9N395 A 10 9L3362C2 9L312 A 11 9L3362B2 9L310 A 11 9L3362B2 9L312 A 12 9L3362A2 9L310 A 13 9L3356K4 9L310 A 14 9L3356L4 9L310 A 15 9L3356M4 9L310 A 16 9L3356N4 9L310 A 17 9L3356P4 9L310 A 18 9L33KAA1 9L310 A 19 9L44KAA1 9L410 A 20 9L4442F1 9L410 A 21 9L4442E1 9L410 A 22 9L4442D1 9L410 A 23 9L4442C1 9L410 A 24 9L4442B1 9L410 |  | 6
9 | LNF | 9LNFB0004 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 183 | 188 | 188 | 9LNF0131 | 9LBK0140 | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N2256A1 9N2C70 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N3340A2 9N395 A 10 9L3362C2 9L312 A 11 9L3362B2 9L310 A 11 9L3362B2 9L312 A 12 9L3362A2 9L310 A 13 9L3357E1 9L310 A 14 9L3358C2 9L307 A 14 9L3358C2 9L312 A 15 9L3358B2 9L307 A 16 9L3358A2 9L307 A 17 9L33JAA3 9L307 A 18 2L22JAA3 2L244 A 19 9L11JAA3 9L115 A 20 9L1110A2 9L115 A 21 2L1110A2 2L142 A 21 2L1110A2 2L146 A 21 2L1110A2 2L150 A 22 2L11Z0A2 2L142 A 23 2D00W3A2 2D022 A 24 2D0000D2 2D022 A 25 1D0000C2 1D042 A 26 1D0000B2 1D042 A 27 9D0000A2 9D082 A 27 9D0000A2 9D083 |  | 16
9 | LNF | 9LNFB0005 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 83 | 93 | 93 | 9LNF0132 | 9LCD0150 | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N2256A1 9N2C70 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N3340A2 9N395 A 10 9L3362C2 9L312 A 11 9L3362B2 9L310 A 11 9L3362B2 9L312 A 12 9L3362A2 9L310 A 13 9L3356K4 9L310 A 14 9L3356L4 9L310 A 15 9L3356M4 9L310 A 16 9L3356N4 9L310 A 17 9L3356P4 9L310 A 18 9L33KAA1 9L310 A 19 9L44KAA1 9L410 A 20 9L4442F1 9L410 A 21 9L4442E1 9L410 A 22 9L4442D1 9L410 A 23 9L4442C1 9L410 A 24 9L4442B1 9L410 |  | 6
9 | LNF | 9LNFB0006 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 181 | 187 | 187 | 9LNF0133 | 9LCG0140 | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N2256A1 9N2C70 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N3340A2 9N395 A 10 9L3362C2 9L312 A 11 9L3362B2 9L310 A 11 9L3362B2 9L312 A 12 9L3362A2 9L310 A 13 9L3357E1 9L310 A 14 9L3358C2 9L307 A 14 9L3358C2 9L312 A 15 9L3358B2 9L307 A 16 9L3358A2 9L307 A 17 9L33JAA3 9L307 A 18 2L22JAA3 2L244 A 19 9L11JAA3 9L115 A 20 9L1110A2 9L115 A 21 2L1110A2 2L142 A 21 2L1110A2 2L146 A 21 2L1110A2 2L150 A 22 2L11Z0A2 2L142 A 23 2D00W3A2 2D022 A 24 2D0000D2 2D022 A 25 1D0000C2 1D042 A 26 1D0000B2 1D042 A 27 9D0000A2 9D082 A 27 9D0000A2 9D083 |  | 16
9 | LNF | 9LNFB0007 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 79 | 119 | 119 | 9LNF0123 | 9RRB001AR | A 01 9N2263A1 9N2D34 A 01 9N2263A1 9N2D34 A 02 9N2203A1 9N2D34 A 02 9N2203A1 9N2D70 A 03 9N2201C1 9N2B34 A 03 9N2201C1 9N2D70 A 04 9N2201B1 9N2B34 A 05 9N2201A1 9N2B34 A 06 9N22B2A1 9N2B34 A 07 9N33B2A1 9N395 A 08 9N3342C2 9N395 A 09 9N3342B2 9N395 A 10 9N3342A2 9N395 A 11 9N33A2A5 9N3A81 A 12 9N3330A1 9N3A81 A 13 9N3330B1 9N3A81 A 13 9N3330B1 9N3B27 A 14 9N3313C2 9N3B27 A 15 9N3313D2 9N3B27 A 16 9N3321A1 9N3B27 A 17 9N331BA1 9N3B27 |  | 16
9 | LNF | 9LNFB0008 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 80 | 119 | 119 | 9LNF0124 | 9REA001AR | A 01 9N2263A1 9N2D34 A 01 9N2263A1 9N2D34 A 02 9N2203A1 9N2D34 A 02 9N2203A1 9N2D70 A 03 9N2201C1 9N2B34 A 03 9N2201C1 9N2D70 A 04 9N2201B1 9N2B34 A 05 9N2201A1 9N2B34 A 06 9N22B2A1 9N2B34 A 07 9N33B2A1 9N395 A 08 9N3342C2 9N395 A 09 9N3342B2 9N395 A 10 9N3342A2 9N395 A 11 9N33A2A5 9N3A81 A 12 9N3330A1 9N3A81 A 13 9N3330B1 9N3A81 A 13 9N3330B1 9N3B27 A 14 9N3313C2 9N3B27 A 15 9N3313D2 9N3B27 A 16 9N3321A1 9N3B27 A 17 9N331BA1 9N3B27 |  | 16
9 | LNF | 9LNFB0010 | IN | IN | OUT | NO | 2 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 127 | 150 | 150 | 9LNF0112 | 9LNF500CR | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N2256A1 9N2C70 A 03 9N2200B2 9N2A34 A 03 9N2200B2 9N2C34 A 04 9N2200A2 9N2A34 A 05 9N22A3A2 9N2A34 A 06 9N33A3A2 9N395 A 07 9N3340C2 9N395 A 08 9N3340B2 9N395 A 09 9N3340A2 9N395 A 10 9L3362C2 9L312 A 11 9L3362B2 9L310 A 11 9L3362B2 9L312 A 12 9L3362A2 9L310 A 13 9L3330U3 9L310 A 14 9L3330T3 9L310 A 14 9L3330T3 9L312 A 15 1L3330T3 1L306 A 16 1L3335L1 1L306 A 17 1L3335K1 1L306 A 18 1L3335J1 1L306 A 19 1L3335H1 1L306 A 20 1L3335G1 1L306 A 21 1L3335F1 1L304 A 21 1L3335F1 1L306 A 22 1L3335E1 1L304 A 23 1L33JNB1 1L304 A 24 1L44JNA1 1L404 A 25 1L55JNA1 1L506 A 26 1L66JNA1 1L605 A 27 1L6640E2 1L605 A 28 1L6640F2 1L605 A 29 1L6640G3 1L605 |  | 2 x 6mm2
9 | LNF | 9LNFB0011 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 9 | 12 | 12 | 9LNF0134 | 9LDB001BN | A 01 9N2222A1 9N2C47 A 01 9N2222A1 9N2C47 A 02 9N22C0A1 9N2C47 A 03 9N2224A1 9N2C47 |  | 2.5
9 | LNF | 9LNFB0014 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 28 | 65 | 65 | 9LNF0361 | 9LNF520CR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N22C1A1 9N2C47 A 06 9N2269A2 9N2C34 A 06 9N2269A2 9N2D35 A 06 9N2269A2 9N2D36 A 07 9N229DA2 9N2D36 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0015 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 29 | 58 | 58 | 9LNF0362 | 9LNF540CR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N22C1A1 9N2C47 A 06 9N2269A3 9N2C34 A 06 9N2269A3 9N2D35 A 06 9N2269A3 9N2D36 A 07 9N229DA2 9N2D36 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0017 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 44 | 38 | 53 | 9LNF0364 | 9LNF620CR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N22C1A1 9N2C47 A 06 9N2269A2 9N2C34 A 06 9N2269A2 9N2D35 A 06 9N2269A2 9N2D36 A 07 9N229DA2 9N2D36 A 08 9N2201J1 9N2D36 A 09 9N2201H1 9N2D36 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0018 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 54 | 59 | 71 | 9LNF0351 | 9LNF660CR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N2200D2 9N2C34 A 06 9N2200E2 9N2C34 A 07 9N2200F2 9N2C34 A 08 9N2200G2 9N2C34 A 09 9N22C4A3 9N2C34 A 10 9N33D6A1 9N3D51 A 11 9N3338A1 9N3D51 A 12 9N3337A1 9N3D51 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0019 | IN | IN | OUT | YES | 2 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 118 | 129 | 129 | 9LNF0352 | 9KRT501AR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N2200C2 9N2C34 A 06 9N2200B2 9N2A34 A 06 9N2200B2 9N2C34 A 07 9N2200A2 9N2A34 A 08 9N22A3A2 9N2A34 A 09 9N33A3A2 9N395 A 10 9N3340C2 9N395 A 11 9N3340B2 9N395 A 12 9N3340A2 9N395 A 13 9L3362C2 9L312 A 14 9L3362B2 9L310 A 14 9L3362B2 9L312 A 15 9L3362A2 9L310 A 16 9L3330U3 9L310 A 17 9L3330T3 9L310 A 17 9L3330T3 9L312 A 18 1L3330T3 1L306 A 19 1L3335L1 1L306 A 20 1L3335K1 1L306 A 21 1L3335J1 1L306 A 22 1L3335H1 1L306 A 23 1L3335G1 1L306 A 24 1L3335F1 1L304 A 24 1L3335F1 1L306 A 25 1L3335E1 1L304 A 26 1L33JNB1 1L304 A 27 1L44JNA1 1L404 A 28 1L55JNA1 1L506 A 29 1L66JNA1 1L605 A 30 1L6640E2 1L605 A 31 1L6640F2 1L605 A 32 1L6640G3 1L605 |  | 2 x 6mm2
9 | LNF | 9LNFB0020 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 59 | 72 | 72 | 9LNF0353 | 9RRB007AR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N2200D2 9N2C34 A 06 9N2200E2 9N2C34 A 07 9N2200F2 9N2C34 A 08 9N2200G2 9N2C34 A 09 9N22C4A3 9N2C34 A 10 9N33D6A1 9N3D51 A 11 9N3332D1 9N3C02 A 12 9N33C4A1 9N3C02 A 13 9N4404A1 9N4C01 |  | 2.5
9 | LNF | 9LNFB0022 | OUT | OUT | OUT | NO | 2 | 2.5 | GRA | [5 empty] | NO |  |  | 114 | 136 | 136 | 9LNF0341 | 9ASG803UB | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 A 02 9N2222D1 9N2C45 A 03 9N2222C1 9N2C45 A 04 9N2222B1 9N2C47 A 05 9N2200C2 9N2C34 A 06 9N2200B2 9N2A34 A 06 9N2200B2 9N2C34 A 07 9N2200A2 9N2A34 A 08 9N22A3A2 9N2A34 A 09 9N33A3A2 9N395 A 10 9N3340C2 9N395 A 11 9N3340B2 9N395 A 12 9N3340A2 9N395 A 13 9L3362C2 9L312 A 14 9L3362B2 9L310 A 14 9L3362B2 9L312 A 15 9L3362A2 9L310 A 16 9L3330U3 9L310 A 17 9L3330T3 9L310 A 17 9L3330T3 9L312 A 18 1L3330T3 1L306 A 19 1L3335L1 1L306 A 20 1L3335K1 1L306 A 21 1L3335J1 1L306 A 22 1L3335H1 1L306 A 23 1L3335G1 1L306 A 24 1L3335F1 1L304 A 24 1L3335F1 1L306 A 25 1L3335E1 1L304 A 26 1L33JNB1 1L304 A 27 1L44JNA1 1L404 A 28 1L55JNA1 1L506 |  | 2.5
9 | LNF | 9LNFB0502 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 58 | 80 | 80 | 9LNF500CR | 9DTVH01AR | A 01 1L6640F2 1L605 A 01 1L6640F2 1L605 A 02 1L6640E2 1L605 A 03 1L6640D2 1L605 A 04 1L6640C2 1L601 A 05 1L6640B2 1L601 A 06 1L6640A2 1L601 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0503 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 124 | 170 | 170 | 9LNF500CR | 9TEG001AR | A 01 1L6640G3 1L605 A 01 1L6640G3 1L605 A 02 1L6640F2 1L605 A 03 1L6640E2 1L605 A 04 1L66JNA1 1L605 A 05 1L55JNA1 1L506 A 06 1L44JNA1 1L404 A 07 1L33JNB1 1L304 A 08 1L3335E1 1L304 A 09 1L3335F1 1L304 A 09 1L3335F1 1L306 A 10 1L3335G1 1L306 A 11 1L3335H1 1L306 A 12 1L3335J1 1L306 A 13 1L3335K1 1L306 A 14 1L3335L1 1L306 A 15 1L3330T3 1L306 A 16 9L3330T3 9L310 A 16 9L3330T3 9L312 A 17 9L3330U3 9L310 A 18 9L3362A2 9L310 A 19 9L3362B2 9L310 A 19 9L3362B2 9L312 A 20 9L3362C2 9L312 A 21 9N3340A2 9N395 A 22 9N33A8A2 9N395 A 23 9N3342B1 9N395 A 24 9N3342A1 9N395 A 25 9N33A2A1 9N3A81 A 26 9N33A2B1 9N3A81 A 27 9N3330A2 9N3A81 A 28 9N3315A1 9N3A81 A 28 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0521 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF520CR | 9LNFN02 | K9LNF B0521 A IN 02 2.5 A 9N2D46 9LNF 520CR 9LNF 520CR 9N2D48 N2D48 N21 9LNF N02 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0522 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF520CR | 9LNFN03 | K9LNF B0522 A IN 02 2.5 A 9N2D46 9LNF 520CR 9LNF 520CR 9N2D48 N2D48 N31 9LNF N03 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0523 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 19 | 19 | 9LNF520CR | 9LNFN04 | K9LNF B0523 A IN 02 2.5 A 9N2D46 9LNF 520CR 9LNF 520CR 9N2D48 N2D48 N41 9LNF N04 19 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0524 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 133 | 184 | 184 | 9LNF520CR | 9ASG801AR | A 01 9N2206B1 9N2D36 A 01 9N2206B1 9N2D36 A 02 9N2206A1 9N2D36 A 03 9N229DA2 9N2D36 A 04 9N2269A3 9N2C34 A 04 9N2269A3 9N2D35 A 04 9N2269A3 9N2D36 A 05 9N22C1A1 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N3340A2 9N395 A 14 9L3362C2 9L312 A 15 9L3362B2 9L310 A 15 9L3362B2 9L312 A 16 9L3362A2 9L310 A 17 9L3330U3 9L310 A 18 9L3330T3 9L310 A 18 9L3330T3 9L312 A 19 1L3330T3 1L306 A 20 1L3330S3 1L306 A 21 1L3339L4 1L306 A 22 1L3351B2 1L306 A 23 1L3352A1 1L306 A 24 1L3352B1 1L306 A 25 1L3352C1 1L306 A 26 1M2210A4 1M2? A 27 1M22H8A1 1M2? A 28 1M11H8A1 1M1? A 29 1M1108A2 1M1? A 30 1M11H9A5 1M1? A 31 1M1109A5 1M1? A 32 1M1109B5 1M1? |  | 2 x 2,5mm2
9 | LNF | 9LNFB0541 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 12 | 12 | 9LNF540CR | 9TEP540UB | K9LNF B0541 A IN 02 2.5 A 9N2D46 9LNF 540CR 9LNF 540CR 9N2D46 N2D46 D21 9TEP 540UB 12 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0542 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 10 | 10 | 9LNF540CR | 9TEP740UB | K9LNF B0542 A IN 02 2.5 A 9N2D46 9LNF 540CR 9LNF 540CR 9N2D46 N2D46 C43 9TEP 740UB 10 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0543 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 16 | 16 | 9LNF540CR | 9TEU524UB | K9LNF B0543 A IN 02 2.5 A 9N2D46 9LNF 540CR 9LNF 540CR 9N2D46 N2D46 F27 9TEU 524UB 16 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0544 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 17 | 17 | 9LNF540CR | 9TEU536UB | K9LNF B0544 A IN 02 2.5 A 9N2D46 9LNF 540CR 9LNF 540CR 9N2D46 N2D46 C07 9TEU 536UB 17 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0545 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 17 | 17 | 9LNF540CR | 9TEU736UB | K9LNF B0545 A IN 02 2.5 A 9N2D46 9LNF 540CR 9LNF 540CR 9N2D46 N2D46 D29 9TEU 736UB 17 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0546 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF540CR | 9KRG704AR |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0547 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF540CR | 9KRG703AR |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0548 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 212 | 236 | 235 | 9LNF540CR | 0KER002AR | A 01 9N2206C2 9N2D36 A 01 9N2206C2 9N2D36 A 02 9N224DA1 9N2D36 A 03 9N2267A3 9N2C34 A 03 9N2267A3 9N2D35 A 03 9N2267A3 9N2D36 A 04 9N22C2A1 9N2C45 A 05 9N2263A1 9N2D34 A 06 9N2203A1 9N2D34 A 06 9N2203A1 9N2D70 A 07 9N2201C1 9N2B34 A 07 9N2201C1 9N2D70 A 08 9N2201B1 9N2B34 A 09 9N2201A1 9N2B34 A 10 9N22B2A1 9N2B34 A 11 9N33B2A1 9N395 A 12 9N3342C2 9N395 A 13 9N33A8A1 9N395 A 14 9N3340A3 9N395 A 15 9L3385A1 9L312 A 16 9L3385B1 9L310 A 16 9L3385B1 9L312 A 17 9L3385C1 9L310 A 18 9L3385D1 9L310 A 19 9L3385E1 9L310 A 20 9L3385F1 9L310 A 21 2L3312A1 2L346 A 22 2L3319C1 2L346 A 23 2L3318B1 2L346 A 24 2L3318A1 2L346 A 25 2L33JEA1 2L346 A 26 2L22JEA1 2L244 A 27 2L11JEA1 2L149 A 28 2L1119D3 2L149 A 29 2L1119E3 2L149 A 30 2L1125E1 2L149 A 31 2L1125F1 2L145 A 31 2L1125F1 2L149 A 32 2L1125G1 2L145 A 33 2L1125H1 2L141 A 33 2L1125H1 2L145 A 33 2L1125H1 2L153 A 34 2L1125J1 2L141 A 35 2L1125K1 2L141 A 36 2L1125L1 2L141 A 37 2L1113A3 2L141 A 37 2L1113A3 2L142 A 38 2L1113B3 2L142 A 38 2L1113B3 2L143 A 38 2L1113B3 2L144 A 39 2L1113C3 2L144 A 40 2W1113C3 2W170 A 41 2W1113D3 2W170 A 42 2W1113E3 2W170 A 43 2W11M2A1 2W171 A 44 2W0010A1 2W071 A 45 9W0010A1 9W080 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0561 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 18 | 9LNF560CR | 6KPM001HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0562 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 18 | 9LNF560CR | 6KPM002HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0563 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 18 | 9LNF560CR | 6KPM003HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0564 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 16 | 9LNF560CR | 6KPM004HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0565 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 16 | 9LNF560CR | 6KPM005HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0566 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 16 | 9LNF560CR | 6KPM006HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0567 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 6LNF567JA | 6KPM567HL |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0568 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF568JA | 6KPM568HL |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0569 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF569JA | 6KPM569HL |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0570 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF570JA | 9KPMTurnstile1 |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0571 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 6 | 9LNF570CR | 6KPM007HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0572 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 6 | 9LNF570CR | 6KPM008HL | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0573 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 15 | 9LNF570CR | 6KPM100CR | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0574 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 5 | 9LNF570CR | 6KPM001GT | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0575 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 5 | 9LNF570CR | 6KPM002GT | IND (SITE RUN) |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0621 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF620CR | 9TEP405RK | K9LNF B0621 A IN 02 2.5 A 9N2D36 9LNF 620CR 9LNF 620CR 9N2D48 N2D48 60W 9TEP 405RK 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0622 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF620CR | 9TEP406RK | K9LNF B0622 A IN 02 2.5 A 9N2D36 9LNF 620CR 9LNF 620CR 9N2D48 N2D48 60W 9TEP 406RK 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0623 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF620CR | 9TEU100RK | K9LNF B0623 A IN 02 2.5 A 9N2D36 9LNF 620CR 9LNF 620CR 9N2D48 N2D48 60W 9TEU 100RK 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0624 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 20 | 20 | 9LNF620CR | 9TEU600RK | K9LNF B0624 A IN 02 2.5 A 9N2D36 9LNF 620CR 9LNF 620CR 9N2D48 N2D48 60W 9TEU 600RK 20 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0625 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF620CR | 9TEP501QD |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0626 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF620CR | 9TEP503QD |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0627 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF620CR | 9TEP502QD |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0628 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9LNF620CR | 9TEP504QD |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0661 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 60 | 60 | 9LNF660CR | 9TES001RK | K9LNF B0661 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D03 N4D03 59Y 9TES 001RK 60 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0662 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 11 | 11 | 9LNF660CR | 9TES003RK | K9LNF B0662 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 59X 9TES 003RK 11 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0663 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 15 | 15 | 9LNF660CR | 9TES004RK | K9LNF B0663 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 59X 9TES 004RK 15 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0664 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 17 | 17 | 9LNF660CR | 9TES005RK | K9LNF B0664 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 59X 9TES 005RK 17 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0665 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 11 | 11 | 9LNF660CR | 9TES013RK | K9LNF B0665 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 58X 9TES 013RK 11 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0666 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 10 | 10 | 9LNF660CR | 9TES014RK | K9LNF B0666 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 59X 9TES 014RK 10 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0667 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 12 | 12 | 9LNF660CR | 9TES015RK | K9LNF B0667 A IN 02 2.5 A 9N3D52 9LNF 660CR 9LNF 660CR 9N4D71 N4D71 59X 9TES 015RK 12 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0668 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 63 | 110 | 110 | 9LNF500CR | 0ESC005CR | A 01 1L6640C2 1L601 A 01 1L6640C2 1L601 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0669 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 22 | 65 | 65 | 9LNF660CR | 9TES007CR | A 01 9N3337A1 9N3D51 A 01 9N3337A1 9N3D51 A 02 9N337DA2 9N3D09 A 03 9N227DA2 9N2D09 A 04 9N2207D1 9N2D09 A 05 9N228DA1 9N2D09 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0670 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 72 | 65 | 65 | 9LNF660CR | 9TES007CR | A 01 9N2200D2 9N2C34 A 01 9N2200D2 9N2C34 A 02 9N2200E2 9N2C34 A 03 9N2200F2 9N2C34 A 04 9N2200G2 9N2C34 A 05 9N22C4A3 9N2C34 A 06 9N33D6A1 9N3D51 A 07 9N3338A1 9N3D51 A 08 9N3337A1 9N3D51 A 09 9N337DA2 9N3D09 A 10 9N227DA2 9N2D09 A 11 9N2207D1 9N2D09 A 12 9N228DA1 9N2D09 A 13 9N2209A1 9N2D09 A 14 9N2209B1 9N2D09 |  | 2 x 2,5mm2
9 | LNF | 9LNFB0900 | IN | IN | OUT | NO | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS | 12 | 20 | 0 | 9LNF032JA | 9LNF550CR | A 01 9N2224A1 9N2C47 A 01 9N2224A1 9N2C47 |  | 3 x 6mm2
9 | LNF | 9LNFB0901 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LNF033JA | 9LNF601CR |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0902 | IN | IN | OUT | NO | 3 | 10 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9PMC100CR | 9LNF013JA |  |  | 3 x 10mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0903 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LNF530CR | 9LNF3011A |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0904 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LNF530CR | 9LNF3012A |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0905 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LNF530CR | 9LNF3010A |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0906 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LNF035JA | 9LNF530CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | LNF | 9LNFB0936 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 100 | 9LNF036JA | 9LNF560CR | LV-9N2221A-B, LV-9N2561A, LV-9N2002C-A- IND |  | 2 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0937 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 100 | 9LNF037JA | 9LNF561CR | LV-9N2221A-B, LV-9N2561A, LV-9N2002C-A- IND |  | 2 x 2,5mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0940 | IN | IN | OUT | NO | 2 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 60 | 9LNF039JA | 9TES030CR | IND, LV 9N 2221B-A-LV 2C11A, LV 2091A-B - IND / A-B-C. |  | 2 X 16mm2 | [5 empty] | duplicate cable number
9 | LNF | 9LNFB0941 | IN | IN | OUT | NO | 2 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 86 | 9LNF040JA | 9TES031CR | IND, LV 9N 2221B-A-LV 2C11A LV 2091A-B-C-D, LV 2F01A, LV 9N00F01A-LV 0011A, LV 0031A-IND / A. |  | 2 X 16mm2 | [5 empty] | duplicate cable number
9 | LNG | 9LNGB0001 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 7 | 101 | 16 | 9LKN0406 | 9LNG001TR | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201C1 9Y20Y |  | 6
9 | LNG | 9LNGB0002 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 2 | 16 | 9 | 9LNG001DL | 9LNG0141 | A 01 9Y2201C1 9Y20Y A 01 9Y2201C1 9Y20Y A 02 9Y2201D1 9Y20Y |  | 16
9 | LNG | 9LNGB0003 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 3 | 13 | 13 | 9LNG0143 | 9LBH0150 | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y |  | 2.5
9 | LNG | 9LNGB0004 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 6 | 19 | 19 | 9LNG0132 | 9LCE0150 | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y |  | 2.5
9 | LNG | 9LNGB0005 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 18 | 30 | 30 | 9LNG0133 | 9SDA101AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y A 05 9Y2201H1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2204E1 9Y20Y A 08 9Y2204D1 9Y20Y A 09 9Y2204C1 9Y20Y |  | 6
9 | LNG | 9LNGB0006 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 15 | 23 | 23 | 9LNG0134 | 9SDA201AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y A 05 9Y2201H1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2204E1 9Y20Y |  | 6
9 | LNG | 9LNGB0007 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 10 | 33 | 33 | 9LNG0121 | 1ATE101AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201C1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2204B1 9Y20Y |  | 6
9 | LNG | 9LNGB0008 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 14 | 25 | 25 | 9LNG0122 | 2ATE101AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y A 05 9Y2201H1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2204E1 9Y20Y |  | 16
9 | LNG | 9LNGB0009 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 18 | 33 | 33 | 9LNG0123 | 1ATE102AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y A 05 9Y2201H1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2204E1 9Y20Y A 08 9Y2204D1 9Y20Y A 09 9Y2204C1 9Y20Y |  | 16
9 | LNG | 9LNGB0010 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 14 | 24 | 24 | 9LNG0124 | 2ATE102AR | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y A 05 9Y2201H1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2204E1 9Y20Y |  | 6
9 | LNG | 9LNGB0011 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 6 | 0 | 1 | 9LNG0110 | 9LCE0150 | A 01 9Y2201D1 9Y20Y A 01 9Y2201D1 9Y20Y A 02 9Y2201E1 9Y20Y A 03 9Y2201F1 9Y20Y A 04 9Y2201G1 9Y20Y |  | 6
9 | LNH | 9LNHB0001 | OUT | OUT | OUT | NO | 2 | 6 | A | [5 empty] | NO |  |  | 7 | 15 | 15 | 9LKP0503 | 9LNH001TR | A 01 9H2202A1 9H2? A 01 9H2202A1 9H2? |  | 6
9 | LNH | 9LNHB0002 | OUT | OUT | OUT | NO | 2 | 16 | A | [5 empty] | NO |  |  | 3 | 12 | 12 | 9LNH001DL | 9LNH0141 | A 01 9H2203H2 9H2? A 01 9H2203H2 9H2? A 02 9H2203G2 9H2? |  | 16
9 | LNH | 9LNHB0003 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 4 | 11 | 11 | 9LNH0143 | 9LBL0150 | A 01 9H2203G2 9H2? A 01 9H2203G2 9H2? A 02 9H2203F2 9H2? A 03 9H2203E2 9H2? |  | 2.5
9 | LNH | 9LNHB0004 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 5 | 16 | 16 | 9LNH0132 | 9LCH0150 | A 01 9H2203G2 9H2? A 01 9H2203G2 9H2? A 02 9H2203F2 9H2? A 03 9H2203E2 9H2? A 04 9H2203D2 9H2? |  | 2.5
9 | LNH | 9LNHB0005 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 12 | 23 | 23 | 9LNH0133 | 9CTE001AR | A 01 9H2203G2 9H2? A 01 9H2203G2 9H2? A 02 9H2203F2 9H2? A 03 9H2203E2 9H2? A 04 9H2203D2 9H2? A 05 9H2203C2 9H2? A 06 9H2203B2 9H2? |  | 2.5
9 | LNH | 9LNHB0006 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 228 | 300 | 300 | 9LNH0134 | 9CTE002AR | A 01 9H2200G4 9H2? A 01 9H2200G4 9H2? A 02 9H2200F4 9H2? A 03 9H2200E4 9H2? A 04 9H2200D4 9H2? A 05 9H2200C4 9H2? A 06 9H2200B4 9H2? A 07 9H2200A4 9H2? A 08 0G1189A1 0G1H A 09 2C00T0A1 2C0A A 10 2C0001D3 2C0A A 11 2C0001C3 2C0A A 12 1C0001B3 1C0A A 13 1C0001A3 1C0A A 14 2G0000A3 2G0P A 15 2P0002A3 2P0A |  | 2.5
9 | LNH | 9LNHB0007 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 401 | 262 | 262 | 9LNH0121 | 0SEK001AR | A 01 9H2200G4 9H2? A 01 9H2200G4 9H2? A 02 9H2200F4 9H2? A 03 9H2200E4 9H2? A 04 9H2200D4 9H2? A 05 9H2200C4 9H2? A 06 9H2200B4 9H2? A 07 9H2200A4 9H2? A 08 0G1189A1 0G1H A 09 2C00T0A1 2C0A A 10 2C0001D3 2C0A A 11 2C0001C3 2C0A A 12 1C0001B3 1C0A A 13 1C0001A3 1C0A A 14 2G0000A3 2G0P A 15 2P0002A3 2P0A A 16 2P00W2A3 2P0A A 17 2P0000F6 2P0A A 18 2P00W4A1 2P0A A 19 2P00A0A1 2P0A A 20 2P11A0A1 2P1A A 21 2P1104A1 2P1A A 22 0G1182A1 0G1P A 23 0G1182B1 0G1P |  | 2.5
9 | LNH | 9LNHB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LNH001TB | 9CTE001BN |  |  | 2core x 2,5 mm2 | [5 empty] | not in pericles
9 | LST | 9LSTB0001 | OUT | OUT | OUT | NO | 4 | 95 | A | [5 empty] | NO |  |  | 217 | 256 | 256 | 9LKZ0508 | 9LST001TR | A 01 1L1112E1 1L109 A 01 1L1112E1 1L109 A 02 1L1112D1 1L109 A 03 1L1112C1 1L105 A 03 1L1112C1 1L109 A 04 1L1114A1 1L105 A 05 1L1110G3 1L105 A 06 1L1110F3 1L105 A 07 1L1110E3 1L101 A 07 1L1110E3 1L113 A 08 1L1100E3 1L101 A 09 1L1100D3 1L101 A 09 1L1100D3 1L102 A 10 1L1100C3 1L102 A 10 1L1100C3 1L103 A 10 1L1100C3 1L104 A 11 1L1100B3 1L104 A 12 1W1100B3 1W130 A 13 1W1100A3 1W130 A 14 1W1107A1 1W130 A 15 1W11M0A1 1W131 A 16 1W00M0A1 1W031 A 17 1W0000A1 1W031 A 17 1W0000A1 1W032 A 17 1W0000A1 1W035 A 17 1W0000A1 1W037 A 17 1W0000A1 1W038 |  | 95
9 | LST | 9LSTB0002 | OUT | OUT | OUT | NO | 4 | 35 | A | [5 empty] | NO |  |  | 20 | 0 | 25 | 9LST001TR | 9LST001CR | IND (SITE RUN) |  | 35
9 | PMC | 9PMCB0320 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 1/2PMC020 | 9PMC320PJ |  |  | 4 x 1.5mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0321 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC327PJ | 9PMC330AR |  |  | 8 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0322 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC330AR | 9PMC330AR |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0323 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC330AR | 9PMC330PJ |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0325 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC330PJ | 9PMC330PP |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0326 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC331PJ | 9PMC331PO |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0328 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC326PJ | 9PMC330AR |  |  | 1 x 4mm2 Earth Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0330 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC333VA | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0331 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC331VB | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0332 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC332VB | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0333 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC333VB | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0334 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC336VA | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0335 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC334VA | 9PMC337VA |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | PMC | 9PMCB0927 | OUT | OUT | OUT | NO |  |  |  | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS |  |  |  | 9PMC332PJ | 9PMC332PO |  |  | 4 x 0.75mm2 Power Cable | [5 empty] | not in pericles
9 | REA | 9REAB0001 | OUT | OUT | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 83 | 101 | 101 | 9LKI0309 | 9REA002AG | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N33A8A2 9N395 A 16 9N3342B1 9N395 A 17 9N3342A1 9N395 A 18 9N33A2A1 9N3A81 A 19 9N33A2B1 9N3A81 A 20 9N3330A2 9N3A81 A 21 9N3330B2 9N3A81 A 21 9N3330B2 9N3B27 A 22 9N3313C1 9N3B27 A 23 9N3313D1 9N3B27 A 24 9N3321A3 9N3B27 A 25 9N331BA3 9N3B27 |  | 2.5
9 | REA | 9REAB0002 | OUT | OUT | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 83 | 91 | 1 | 9LKI0303 | 9REA005CR | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N33A8A2 9N395 A 16 9N3342B1 9N395 A 17 9N3342A1 9N395 A 18 9N33A2A1 9N3A81 A 19 9N33A2B1 9N3A81 A 20 9N3330A2 9N3A81 A 21 9N3330B2 9N3A81 A 21 9N3330B2 9N3B27 A 22 9N3313C1 9N3B27 A 23 9N3313D1 9N3B27 A 24 9N3321A3 9N3B27 A 25 9N331BA3 9N3B27 |  | 50
9 | REA | 9REAB0003 | OUT | OUT | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 20 | 30 | 1 | 9REA005CR | 9REA003RS | IND (SITE RUN) |  | 6
9 | REA | 9REAB0004 | OUT | OUT | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 20 | 26 | 26 | 9REA005CR | 9REA004RS | IND (SITE RUN) |  | 6
9 | REA | 9REAB0005 | OUT | OUT | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 20 | 30 | 22 | 9REA005CR | 9REA005RS | IND (SITE RUN) |  | 6
9 | REA | 9REAB0006 | OUT | OUT | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 20 | 30 | 25 | 9REA005CR | 9REA006RS | IND (SITE RUN) |  | 6
9 | REA | 9REAB0007 | OUT | OUT | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 20 | 30 | 26 | 9REA005CR | 9REA007RS | IND (SITE RUN) |  | 6
9 | REA | 9REAB0008 | OUT | OUT | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 84 | 92 | 92 | 9LKI0101 | 9REA005CR | A 01 9N2221J3 9N2C45 A 01 9N2221J3 9N2C45 A 02 9N2221H3 9N2C45 A 03 9N2221G3 9N2C45 A 04 9N2221F3 9N2C45 A 05 9N2221E3 9N2C45 A 06 9N2221D3 9N2C45 A 07 9N2221C3 9N2C45 A 08 9N2221B3 9N2C47 A 09 9N2200C2 9N2C34 A 10 9N2200B2 9N2A34 A 10 9N2200B2 9N2C34 A 11 9N2200A2 9N2A34 A 12 9N22A3A2 9N2A34 A 13 9N33A3A2 9N395 A 14 9N3340C2 9N395 A 15 9N3340B2 9N395 A 16 9N33A8A2 9N395 A 17 9N3342B1 9N395 A 18 9N3342A1 9N395 A 19 9N33A2A1 9N3A81 A 20 9N33A2B1 9N3A81 A 21 9N3330A2 9N3A81 A 22 9N3330B2 9N3A81 A 22 9N3330B2 9N3B27 A 23 9N3313C1 9N3B27 A 24 9N3313D1 9N3B27 A 25 9N3321A3 9N3B27 A 26 9N331BA3 9N3B27 |  | 50
9 | RIS | 9RISB0001 | IN | IN | OUT | YES | 3 | 185 | MTAL (A) | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 37 | 49 | 49 | 9LKI0105 | 9RIS001AR | A 01 9N2222J1 9N2C45 A 01 9N2222J1 9N2C45 A 02 9N2222H1 9N2C45 A 03 9N2222G1 9N2C45 A 04 9N2222F1 9N2C45 A 05 9N2222E1 9N2C45 A 06 9N2224A1 9N2C47 A 07 9N22C0A3 9N2C47 A 08 1N33C0A3 1N3C76 A 09 1N3310A2 1N3C76 A 10 9N3318B2 9N3C70 A 10 9N3318B2 9N3C79 |  | 3 x 185mm2
9 | RPE | 9RPEB0001 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 69 | 97 | 97 | 9LKI0401 | 9RPE019BX | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2222A1 9N2C47 A 09 9N2200D2 9N2C34 A 10 9N2200E2 9N2C34 A 11 9N2200F2 9N2C34 A 12 9N2200G2 9N2C34 A 13 9N22C4A3 9N2C34 A 14 9N33D6A1 9N3D51 A 15 9N3332D1 9N3C02 A 16 9N3332C1 9N3C02 A 17 9N3332B1 9N3C02 |  | 2.5
9 | RPE | 9RPEB0002 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 90 | 112 | 112 | 9LKI0402 | 9RPE027BX | A 01 9N2221H1 9N2C45 A 01 9N2221H1 9N2C45 A 02 9N2221G1 9N2C45 A 03 9N2221F1 9N2C45 A 04 9N2221E1 9N2C45 A 05 9N2221D1 9N2C45 A 06 9N2260A2 9N2C45 A 07 9N2260B2 9N2C45 A 08 9N2260C2 9N2C45 A 09 9N2263A1 9N2D34 A 10 9N2203B1 9N2D34 A 11 9N33D5A1 9N3D51 A 12 9N3338A2 9N3D51 A 13 9N3332E1 9N3C02 A 13 9N3332E1 9N3D08 A 14 9N3332F1 9N3D08 A 15 9N3332G1 9N3D08 A 16 9N3332H1 9N3D08 A 17 9N3334A1 9N3D08 A 18 9N3350A3 9N3F03 |  | 2.5
9 | RPE | 9RPEB0003 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 83 | 86 | 87 | 9LKI0606 | 9RPE032BX | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A3 9N2C34 A 08 9N2269A3 9N2D35 A 08 9N2269A3 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 A 18 9N2209D1 9N2F67 A 19 9N22F0A1 9N2F67 A 20 9N00F0A1 9N0F33 A 21 9N0001A1 9N0F33 A 22 9N0003A1 9N0F31 A 22 9N0003A1 9N0F32 |  | 2.5
9 | RPE | 9RPEB0004 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 74 | 86 | 82 | 9LKI0607 | 9RPE033BX | A 01 9N2222G2 9N2C45 A 01 9N2222G2 9N2C45 A 02 9N2222F2 9N2C45 A 03 9N2222E2 9N2C45 A 04 9N2222D2 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A6 9N2C34 A 08 9N2269A6 9N2D35 A 08 9N2269A6 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 A 18 9N2209D1 9N2F67 A 19 9N22F0A1 9N2F67 A 20 9N00F0A1 9N0F33 A 21 9N0001B1 9N0E33 A 21 9N0001B1 9N0F33 |  | 2.5
9 | RRB | 9RRBB0712 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 28 | 0 | 28 | 9RRB802AR | 9RRB801RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0713 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 28 | 0 | 28 | 9RRB802AR | 9RRB820RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0714 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 66 | 0 | 66 | 9RRB802AR | 9RRB821RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0715 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 66 | 0 | 66 | 9RRB802AR | 9RRB822RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0716 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 66 | 0 | 66 | 9RRB802AR | 9RRB823RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0717 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 33 | 0 | 33 | 9RRB802AR | 9RRB824RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0718 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 33 | 0 | 33 | 9RRB802AR | 9RRB825RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0719 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 33 | 0 | 33 | 9RRB802AR | 9RRB826RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0720 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 66 | 0 | 66 | 9RRB802AR | 9RRB828RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0721 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 28 | 0 | 28 | 9RRB802AR | 9RRB829RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0724 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 26 | 0 | 26 | 9RRB803AR | 9RRB802RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0725 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 26 | 0 | 26 | 9RRB803AR | 9RRB803RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0726 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 36 | 0 | 36 | 9RRB803AR | 9RRB804RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0727 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 36 | 0 | 36 | 9RRB803AR | 9RRB806RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0728 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 36 | 0 | 36 | 9RRB803AR | 9RRB807RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0729 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 36 | 0 | 36 | 9RRB803AR | 9RRB808RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0730 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 30 | 0 | 30 | 9RRB803AR | 9RRB809RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0731 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 30 | 0 | 30 | 9RRB803AR | 9RRB810RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0732 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 31 | 0 | 31 | 9RRB803AR | 9RRB712RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0733 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 28 | 0 | 28 | 9RRB803AR | 9RRB830RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRB | 9RRBB0740 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 53 | 0 | 53 | 9RRB601AR | 9RRB627RS | A 01 9N3332G2 9N3D08 A 01 9N3332G2 9N3D08 A 02 9N3332H2 9N3D08 A 03 9N3332J2 9N3D08 |  | 2.5
9 | RRI | 9RRIB0001 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 108 | 77 | 77 | 9LKI0403 | 9RRI044VN | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2200D2 9N2C34 A 09 9N2200E2 9N2C34 A 10 9N2200F2 9N2C34 A 11 9N2200G2 9N2C34 A 12 9N22C4A3 9N2C34 A 13 9N33D6A1 9N3D51 A 14 9N3332D1 9N3C02 A 15 9N3332C1 9N3C02 A 16 9N3332B1 9N3C02 A 17 9N3332A1 9N3C02 A 18 1N33C2A1 1N3C14 |  | 3 x 2,5mm2
9 | RRI | 9RRIB0002 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 83 | 100 | 100 | 9LKI0404 | 9RRI045VN | A 01 9N2221H1 9N2C45 A 01 9N2221H1 9N2C45 A 02 9N2221G1 9N2C45 A 03 9N2221F1 9N2C45 A 04 9N2221E1 9N2C45 A 05 9N2221D1 9N2C45 A 06 9N2260A2 9N2C45 A 07 9N2260B2 9N2C45 A 08 9N2260C2 9N2C45 A 09 9N2263A1 9N2D34 A 10 9N2203B1 9N2D34 A 11 9N33D5A1 9N3D51 A 12 9N3338A2 9N3D51 A 13 9N3332E1 9N3C02 A 13 9N3332E1 9N3D08 A 14 9N3332F1 9N3D08 A 15 9N3332G1 9N3D08 A 16 9N3332H1 9N3D08 A 17 9N3332J1 9N3D08 A 18 9N3332K1 9N3D08 A 19 9N3332L1 9N3D08 A 20 2N33D2A1 2N3D24 |  | 3 x 2,5mm2
9 | RRI | 9RRIB0003 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 108 | 87 | 87 | 9LKI0405 | 9RRI322VN | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2200D2 9N2C34 A 09 9N2200E2 9N2C34 A 10 9N2200F2 9N2C34 A 11 9N2200G2 9N2C34 A 12 9N22C4A3 9N2C34 A 13 9N33D6A1 9N3D51 A 14 9N3332D1 9N3C02 A 15 9N3332C1 9N3C02 A 16 9N3332B1 9N3C02 A 17 9N3332A1 9N3C02 A 18 1N33C2A1 1N3C14 |  | 3 x 2,5mm2
9 | RRI | 9RRIB0004 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | YES | ALSTHOM | EMS | 86 | 116 | 116 | 9LKI0406 | 9RRI323VN | A 01 9N2221H1 9N2C45 A 01 9N2221H1 9N2C45 A 02 9N2221G1 9N2C45 A 03 9N2221F1 9N2C45 A 04 9N2221E1 9N2C45 A 05 9N2221D1 9N2C45 A 06 9N2260A2 9N2C45 A 07 9N2260B2 9N2C45 A 08 9N2260C2 9N2C45 A 09 9N2263A1 9N2D34 A 10 9N2203B1 9N2D34 A 11 9N33D5A1 9N3D51 A 12 9N3338A2 9N3D51 A 13 9N3332E1 9N3C02 A 13 9N3332E1 9N3D08 A 14 9N3332F1 9N3D08 A 15 9N3332G1 9N3D08 A 16 9N3332H1 9N3D08 A 17 9N3332J1 9N3D08 A 18 9N3332K1 9N3D08 A 19 9N3332L1 9N3D08 A 20 2N33D2A1 2N3D24 |  | 3 x 2,5mm2
9 | SDA | 9SDAB0001 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 63 | 77 | 77 | 9LKN0409 | 9SDA001PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y A 13 9Y2220D1 9Y20Y A 14 9Y2220E1 9Y20Y |  | 16
9 | SDA | 9SDAB0002 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 65 | 78 | 78 | 9LKN0408 | 9SDA002PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y A 13 9Y2220D1 9Y20Y A 14 9Y2220E1 9Y20Y |  | 16
9 | SDA | 9SDAB0003 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 67 | 77 | 77 | 9LKN0407 | 9SDA003PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y A 13 9Y2220D1 9Y20Y A 14 9Y2220E1 9Y20Y A 15 9Y2220F1 9Y20Y |  | 16
9 | SDA | 9SDAB0004 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 70 | 79 | 79 | 9LKN0103 | 9SDA004PO | A 01 9Y2204A1 9Y20Y A 01 9Y2204A1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204C1 9Y20Y A 04 9Y2204D1 9Y20Y A 05 9Y2204E1 9Y20Y A 06 9Y2209C1 9Y20Y A 07 9Y2209B1 9Y20Y A 08 9Y22Z2A1 9Y20Y A 09 9Y2226A3 9Y20Y A 10 9Y2226B3 9Y20Y A 11 9Y2226C3 9Y20Y A 12 9Y2220A1 9Y20Y A 13 9Y2220B1 9Y20Y A 14 9Y2220C1 9Y20Y A 15 9Y2220D1 9Y20Y A 16 9Y2220E1 9Y20Y A 17 9Y2220F1 9Y20Y |  | 16
9 | SDA | 9SDAB0005 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 71 | 79 | 79 | 9LKN0105 | 9SDA005PO | A 01 9Y2204A1 9Y20Y A 01 9Y2204A1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204C1 9Y20Y A 04 9Y2204D1 9Y20Y A 05 9Y2204E1 9Y20Y A 06 9Y2209C1 9Y20Y A 07 9Y2209B1 9Y20Y A 08 9Y22Z2A1 9Y20Y A 09 9Y2226A3 9Y20Y A 10 9Y2226B3 9Y20Y A 11 9Y2226C3 9Y20Y A 12 9Y2220A1 9Y20Y A 13 9Y2220B1 9Y20Y A 14 9Y2220C1 9Y20Y A 15 9Y2220D1 9Y20Y A 16 9Y2220E1 9Y20Y A 17 9Y2220F1 9Y20Y A 18 9Y2220G1 9Y20Y |  | 16 | [5 empty] | not in pericles
9 | SDA | 9SDAB0006 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  | 75 | 80 | 80 | 9LKN0107 | 9SDA006PO | A 01 9Y2204A1 9Y20Y A 01 9Y2204A1 9Y20Y A 02 9Y2201C1 9Y20Y A 03 9Y2201D1 9Y20Y A 04 9Y2201E1 9Y20Y A 05 9Y2201F1 9Y20Y A 06 9Y2201G1 9Y20Y A 07 9Y2201H1 9Y20Y A 08 9Y2209B1 9Y20Y A 09 9Y22Z2A1 9Y20Y A 10 9Y2226A3 9Y20Y A 11 9Y2226B3 9Y20Y A 12 9Y2226C3 9Y20Y A 13 9Y2220A1 9Y20Y A 14 9Y2220B1 9Y20Y A 15 9Y2220C1 9Y20Y A 16 9Y2220D1 9Y20Y A 17 9Y2220E1 9Y20Y A 18 9Y2220F1 9Y20Y A 19 9Y2220G1 9Y20Y |  | 16 | [5 empty] | not in pericles
9 | SDA | 9SDAB0011 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 54 | 51 | 51 | 1ATE102AR | 9SDA391MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y A 04 9Y2201D1 9Y20Y A 05 9Y2201E1 9Y20Y A 06 9Y2201F1 9Y20Y A 07 9Y2201G1 9Y20Y A 08 9Y2201H1 9Y20Y A 09 9Y2209B1 9Y20Y A 10 9Y22Z2A2 9Y20Y A 11 9Y2226A3 9Y20Y A 12 9Y2226B3 9Y20Y A 13 9Y2226C3 9Y20Y A 14 9Y2221A1 9Y20Y A 15 9Y2221B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0012 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 54 | 48 | 48 | 1ATE102AR | 9SDA301MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y A 04 9Y2201D1 9Y20Y A 05 9Y2201E1 9Y20Y A 06 9Y2201F1 9Y20Y A 07 9Y2201G1 9Y20Y A 08 9Y2201H1 9Y20Y A 09 9Y2209B1 9Y20Y A 10 9Y22Z2A2 9Y20Y A 11 9Y2226A3 9Y20Y A 12 9Y2226B3 9Y20Y A 13 9Y2226C3 9Y20Y A 14 9Y2221A1 9Y20Y A 15 9Y2221B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0013 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 45 | 67 | 67 | 1ATE102AR | 9SDA162MG | A 01 9Y2204A1 9Y20Y A 01 9Y2204A1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204C1 9Y20Y A 04 9Y2204D1 9Y20Y A 05 9Y2204E1 9Y20Y A 06 9Y2209C1 9Y20Y A 07 9Y2209B1 9Y20Y A 08 9Y22Z2A1 9Y20Y A 09 9Y2226A3 9Y20Y A 10 9Y2226B3 9Y20Y A 11 9Y2226C3 9Y20Y A 12 9Y2220A1 9Y20Y A 13 9Y2220B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0014 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 31 | 50 | 50 | 1ATE102AR | 9SDZ001MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0015 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 1ATE102AR | 9SDA053BN | IND (SITE RUN) |  | 2.5
9 | SDA | 9SDAB0016 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 30 | 48 | 48 | 9SDA101AR | 9SDZ002MG | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0017 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 30 | 48 | 48 | 9SDA101AR | 9SDZ004MG | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0018 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 15 | 15 | 9SDA101AR | 9SDA153BN | IND (SITE RUN) |  | 2.5
9 | SDA | 9SDAB0019 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 25 | 48 | 48 | 9SDA201AR | 9SDZ003MG | A 01 9Y2204E1 9Y20Y A 01 9Y2204E1 9Y20Y A 02 9Y2209C1 9Y20Y A 03 9Y2209B1 9Y20Y A 04 9Y22Z2A2 9Y20Y A 05 9Y2226A1 9Y20Y A 06 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0020 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 25 | 35 | 35 | 9SDA201AR | 9SDZ005MG | A 01 9Y2204E1 9Y20Y A 01 9Y2204E1 9Y20Y A 02 9Y2209C1 9Y20Y A 03 9Y2209B1 9Y20Y A 04 9Y22Z2A2 9Y20Y A 05 9Y2226A1 9Y20Y A 06 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0021 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 9SDA201AR | 9SDA253BN | IND (SITE RUN) |  | 2.5
9 | SDA | 9SDAB0022 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 26 | 40 | 40 | 1ATE102AR | 9SDZ014MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0023 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 26 | 34 | 34 | 1ATE102AR | 9SDZ014ZL | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0024 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 26 | 33 | 33 | 1ATE102AR | 9SDZ010ZL | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0025 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 26 | 37 | 37 | 1ATE102AR | 9SDZ010MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0026 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 26 | 43 | 43 | 1ATE102AR | 9SDZ009MG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0027 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 33 | 60 | 60 | 1ATE102AR | 9SER001VD | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0028 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 23 | 45 | 45 | 1ATE102AR | 9SER002VD | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0029 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 33 | 63 | 63 | 1ATE102AR | 9SER005VD | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0030 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 23 | 48 | 48 | 1ATE102AR | 9SER006VD | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201C1 9Y20Y |  | 2.5
9 | SDA | 9SDAB0031 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 14 | 14 | 9SDA101AR | 9SDA101QM | IND (SITE RUN) |  | 2.5
9 | SDA | 9SDAB0032 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 14 | 14 | 9SDA201AR | 9SDA201QD | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0001 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 66 | 73 | 73 | 9LKN0410 | 9SDX151AG | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0002 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 66 | 79 | 79 | 9LKN0411 | 9SDX152AG | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0003 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 77 | 95 | 95 | 9LKN0603 | 9SDX101BN | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y A 13 9Y2220D1 9Y20Y A 14 9Y2220E1 9Y20Y A 15 9Y2220F1 9Y20Y A 16 9Y2220G1 9Y20Y A 17 9Y2220H1 9Y20Y A 18 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0004 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 77 | 100 | 100 | 9LKN0604 | 9SDX102BN | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y A 13 9Y2220D1 9Y20Y A 14 9Y2220E1 9Y20Y A 15 9Y2220F1 9Y20Y A 16 9Y2220G1 9Y20Y A 17 9Y2220H1 9Y20Y A 18 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0005 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 77 | 83 | 83 | 9LKN0205 | 9SDX001CO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y A 14 9Y2221D1 9Y20Y A 15 9Y2221E1 9Y20Y A 16 9Y2221F1 9Y20Y A 17 9Y2221G1 9Y20Y |  | 50
9 | SDX | 9SDXB0006 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 74 | 76 | 76 | 9LKN0207 | 9SDX002CO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y A 14 9Y2221D1 9Y20Y A 15 9Y2221E1 9Y20Y A 16 9Y2221F1 9Y20Y A 17 9Y2221G1 9Y20Y |  | 50
9 | SDX | 9SDXB0007 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 71 | 78 | 78 | 9LKN0209 | 9SDX003CO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y A 14 9Y2221D1 9Y20Y A 15 9Y2221E1 9Y20Y A 16 9Y2221F1 9Y20Y A 17 9Y2221G1 9Y20Y |  | 50
9 | SDX | 9SDXB0008 | OUT | OUT | OUT | YES | 3 | 185 | A | [5 empty] | NO |  |  | 52 | 48 | 48 | 9LKN0709 | 9SDX002CR | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A2 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y |  | 185
9 | SDX | 9SDXB0009 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 79 | 101 | 96 | 9LKN0510 | 9SDX001PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2221D1 9Y20Y A 14 9Y2221E1 9Y20Y A 15 9Y2221F1 9Y20Y A 16 9Y2221G1 9Y20Y A 17 9Y2221H1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0010 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 79 | 91 | 91 | 9LKN0509 | 9SDX002PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2221D1 9Y20Y A 14 9Y2221E1 9Y20Y A 15 9Y2221F1 9Y20Y A 16 9Y2221G1 9Y20Y A 17 9Y2221H1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0011 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 78 | 85 | 85 | 9LKN0508 | 9SDX003PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2221D1 9Y20Y A 14 9Y2221E1 9Y20Y A 15 9Y2221F1 9Y20Y A 16 9Y2221G1 9Y20Y A 17 9Y2221H1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0012 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 77 | 82 | 82 | 9LKN0507 | 9SDX004PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2221D1 9Y20Y A 14 9Y2221E1 9Y20Y A 15 9Y2221F1 9Y20Y A 16 9Y2221G1 9Y20Y A 17 9Y2221H1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0013 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 64 | 81 | 81 | 9LKN0506 | 9SDX005PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0014 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 64 | 77 | 77 | 9LKN0505 | 9SDX006PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0015 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 63 | 76 | 76 | 9LKN0504 | 9SDX007PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0016 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 65 | 75 | 75 | 9LKN0503 | 9SDX008PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y A 10 9Y2221A1 9Y20Y A 11 9Y2221B1 9Y20Y A 12 9Y2221C1 9Y20Y A 13 9Y2223A1 9Y20Y A 14 9Y2224A1 9Y20Y A 15 9Y2224B1 9Y20Y A 16 9Y2224C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0017 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 59 | 76 | 76 | 9LKN0502 | 9SDX009PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A2 9Y20Y A 07 9Y2226A1 9Y20Y A 08 9Y2226B1 9Y20Y A 09 9Y2226C1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0020 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  |  |  | 14 | 9LKN707JA | 9SDX001JT | IND 9Y2 2041D E 2091C B 2Z21A IND |  | 03x50
9 | SDX | 9SDXB0021 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  |  |  | 14 | 9LKN705JA | 9SDX002JT | IND 9Y2 2041D E 2091C B 2Z21A IND |  | 03x16
9 | SDX | 9SDXB0022 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  |  |  | 15 | 9LKN703JA | 9SDX003JT | IND 9Y2 2041D E 2091C B 2Z21A IND |  | 03x16
9 | SDX | 9SDXB0023 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  |  |  | 14 | 9LKN701JA | 9SDX004JT | IND 9Y2 2041D E 2091C B 2Z21A IND |  | 03x50
9 | SDX | 9SDXB0024 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  |  |  | 14 | 9LKN412JA | 9SDX005JT | IND 9Y2 2041C B A 2011C IND |  | 03x16
9 | SDX | 9SDXB0025 | OUT | OUT | OUT | YES | 3 | 16 | A | [5 empty] | NO |  |  |  |  | 16 | 9LKN602JA | 9SDX006JT | IND 9Y2 2041D C B A 2011C IND |  | 03x16
9 | SDX | 9SDXB0026 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 9 | 9 | 9SDX101BN | 9SDX035RS | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0027 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 11 | 11 | 9SDX101BN | 9SDX036RS | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0028 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 12 | 12 | 9SDX102BN | 9SDX037RS | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0029 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 13 | 13 | 9SDX102BN | 9SDX038RS | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0030 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 20 | 11 | 11 | 9SDX002CR | 9SDX091RS | IND (SITE RUN) |  | 50
9 | SDX | 9SDXB0031 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 20 | 14 | 14 | 9SDX002CR | 9SDX092RS | IND (SITE RUN) |  | 50
9 | SDX | 9SDXB0032 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 20 | 7 | 7 | 9SDX002CR | 9SDX093RS | IND (SITE RUN) |  | 50
9 | SDX | 9SDXB0033 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 54 | 72 | 72 | 9LKN0309 | 9SDX025PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y A 14 9Y2221D1 9Y20Y A 15 9Y2221E1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0034 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 62 | 84 | 84 | 9LKN0310 | 9SDX026PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A1 9Y20Y A 09 9Y2226B1 9Y20Y A 10 9Y2226C1 9Y20Y A 11 9Y2221A1 9Y20Y A 12 9Y2221B1 9Y20Y A 13 9Y2221C1 9Y20Y A 14 9Y2221D1 9Y20Y A 15 9Y2221E1 9Y20Y A 16 9Y2221F1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0041 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 79 | 87 | 87 | 2ATE101AR | 9SDX001AR | A 01 9Y2209C1 9Y20Y A 01 9Y2209C1 9Y20Y A 02 9Y2209B1 9Y20Y A 03 9Y22Z2A1 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y2226B3 9Y20Y A 06 9Y2226C3 9Y20Y A 07 9Y2220A1 9Y20Y A 08 9Y2220B1 9Y20Y A 09 9Y2220C1 9Y20Y A 10 9Y2220D1 9Y20Y A 11 9Y2220E1 9Y20Y A 12 9Y2220F1 9Y20Y A 13 9Y2220G1 9Y20Y A 14 9Y2220H1 9Y20Y A 15 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0042 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 79 | 84 | 84 | 9SDA201AR | 9SDX001AR | A 01 9Y2209C1 9Y20Y A 01 9Y2209C1 9Y20Y A 02 9Y2209B1 9Y20Y A 03 9Y22Z2A1 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y2226B3 9Y20Y A 06 9Y2226C3 9Y20Y A 07 9Y2220A1 9Y20Y A 08 9Y2220B1 9Y20Y A 09 9Y2220C1 9Y20Y A 10 9Y2220D1 9Y20Y A 11 9Y2220E1 9Y20Y A 12 9Y2220F1 9Y20Y A 13 9Y2220G1 9Y20Y A 14 9Y2220H1 9Y20Y A 15 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0043 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 22 | 22 | 9SDX001AR | 9SDX231MG | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0044 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 106 | 106 | 9SDX001AR | 9SDX232MG | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0045 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 85 | 97 | 97 | 2ATE101AR | 9SDX013PO | A 01 9Y2209C1 9Y20Y A 01 9Y2209C1 9Y20Y A 02 9Y2209B1 9Y20Y A 03 9Y22Z2A1 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y2226B3 9Y20Y A 06 9Y2226C3 9Y20Y A 07 9Y2220A1 9Y20Y A 08 9Y2220B1 9Y20Y A 09 9Y2220C1 9Y20Y A 10 9Y2220D1 9Y20Y A 11 9Y2220E1 9Y20Y A 12 9Y2220F1 9Y20Y A 13 9Y2220G1 9Y20Y A 14 9Y2220H1 9Y20Y A 15 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0046 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 2ATE101AR | 9SDX053BN | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0047 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 29 | 29 | 9SDX001AR | 9SDX233MG | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0048 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 31 | 31 | 9SDX001AR | 9SDX234MG | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0049 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 88 | 111 | 111 | 9SDA201AR | 9SDX024PO | A 01 9Y2204E1 9Y20Y A 01 9Y2204E1 9Y20Y A 02 9Y2209C1 9Y20Y A 03 9Y2209B1 9Y20Y A 04 9Y22Z2A1 9Y20Y A 05 9Y2226A3 9Y20Y A 06 9Y2226B3 9Y20Y A 07 9Y2226C3 9Y20Y A 08 9Y2220A1 9Y20Y A 09 9Y2220B1 9Y20Y A 10 9Y2220C1 9Y20Y A 11 9Y2220D1 9Y20Y A 12 9Y2220E1 9Y20Y A 13 9Y2220F1 9Y20Y A 14 9Y2220G1 9Y20Y A 15 9Y2220H1 9Y20Y A 16 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0050 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 86 | 19 | 19 | 9SDA201AR | 9SDX023PO | A 01 9Y2204E1 9Y20Y A 01 9Y2204E1 9Y20Y A 02 9Y2209C1 9Y20Y A 03 9Y2209B1 9Y20Y A 04 9Y22Z2A1 9Y20Y A 05 9Y2226A3 9Y20Y A 06 9Y2226B3 9Y20Y A 07 9Y2226C3 9Y20Y A 08 9Y2220A1 9Y20Y A 09 9Y2220B1 9Y20Y A 10 9Y2220C1 9Y20Y A 11 9Y2220D1 9Y20Y A 12 9Y2220E1 9Y20Y A 13 9Y2220F1 9Y20Y A 14 9Y2220G1 9Y20Y A 15 9Y2220H1 9Y20Y A 16 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0051 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 15 | 15 | 2ATE101AR | 9SDX055BN | IND (SITE RUN) |  | 2.5
9 | SDX | 9SDXB0052 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 82 | 92 | 92 | 2ATE101AR | 9SDX014PO | A 01 9Y2209C1 9Y20Y A 01 9Y2209C1 9Y20Y A 02 9Y2209B1 9Y20Y A 03 9Y22Z2A1 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y2226B3 9Y20Y A 06 9Y2226C3 9Y20Y A 07 9Y2220A1 9Y20Y A 08 9Y2220B1 9Y20Y A 09 9Y2220C1 9Y20Y A 10 9Y2220D1 9Y20Y A 11 9Y2220E1 9Y20Y A 12 9Y2220F1 9Y20Y A 13 9Y2220G1 9Y20Y A 14 9Y2220H1 9Y20Y A 15 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0055 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 99 | 101 | 101 | 9LKN0308 | 9SDX027PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0056 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 98 | 103 | 103 | 9LKN0307 | 9SDX028PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0057 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 88 | 104 | 104 | 9LKN0306 | 9SDX029PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0058 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 98 | 103 | 103 | 9LKN0305 | 9SDX030PO | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0059 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 97 | 101 | 101 | 9LKN0304 | 9SDX153AG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0060 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 88 | 95 | 95 | 9LKN0303 | 9SDX154AG | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204C1 9Y20Y A 03 9Y2204D1 9Y20Y A 04 9Y2204E1 9Y20Y A 05 9Y2209C1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y22Z2A1 9Y20Y A 08 9Y2226A3 9Y20Y A 09 9Y2226B3 9Y20Y A 10 9Y2226C3 9Y20Y A 11 9Y2220A1 9Y20Y A 12 9Y2220B1 9Y20Y A 13 9Y2220C1 9Y20Y A 14 9Y2220D1 9Y20Y A 15 9Y2220E1 9Y20Y A 16 9Y2220F1 9Y20Y A 17 9Y2220G1 9Y20Y A 18 9Y2220H1 9Y20Y A 19 9Y2220J1 9Y20Y |  | 2.5
9 | SDX | 9SDXB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKN601JA | 9SDX100JA |  |  | 4c x 4,0mm2 | [5 empty] | not in pericles
9 | SDX | 9SDXB0901 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SDXJ001J | 9SDX033PO |  |  | 4c x 4,0mm2 | [5 empty] | not in pericles
9 | SDY | 9SDYB0001 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 268 | 270 | 270 | 9LKK0611 | 9SDY001CR | A 01 9L3385F1 9L310 A 01 9L3385F1 9L310 A 02 2L3312A1 2L346 A 03 2L3319C1 2L346 A 04 2L3318B1 2L346 A 05 2L3325A1 2L346 A 06 2L3325B1 2L346 A 07 2L3325C1 2L344 A 07 2L3325C1 2L346 A 08 2L3325D1 2L344 A 09 2L3325E1 2L344 A 10 2L3325F1 2L341 A 10 2L3325F1 2L344 A 11 2M3300A1 2M3? A 12 2M22HAA1 2M2? A 13 2M2203A1 2M2? A 14 2M220HA2 2M2? A 15 2M110HA2 2M1? A 16 2M1121A2 2M1? A 17 2M1121B2 2M1? A 18 0G1108C3 0G1D A 19 0G1108B3 0G1D |  | 6
9 | SDY | 9SDYB0002 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 1 | 9SDY001CR | 9SDY001PO | IND (SITE RUN) |  | 2.5
9 | SDY | 9SDYB0003 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 10 | 1 | 9SDY001CR | 9SDY002PO | IND (SITE RUN) |  | 2.5
9 | SDZ | 9SDZB0001 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 21 | 0 | 39 | 2ATE101AR | 9SDZ001CR | A 01 9Y2220A1 9Y20Y A 01 9Y2220A1 9Y20Y A 02 9Y2226C3 9Y20Y A 03 9Y2226B3 9Y20Y A 04 9Y2226A3 9Y20Y A 05 9Y22Z2A1 9Y20Y A 06 9Y2209B1 9Y20Y A 07 9Y2209C1 9Y20Y |  | 2.5
9 | SDZ | 9SDZB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SDZ001CR | 9SDZ002CR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SED | 9SEDB0001 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 309 | 320 | 320 | 9LKK0101 | 9SED001PO | A 01 9L3356L4 9L310 A 01 9L3356L4 9L310 A 02 9L3356K4 9L310 A 03 9L3356J4 9L310 A 04 9L3356H4 9L310 A 05 9L3356G4 9L312 A 06 1L3356G4 1L306 A 07 1L3356F4 1L306 A 08 1L3356E4 1L306 A 09 1L3356D4 1L306 A 10 1L3356C4 1L306 A 11 1L334JA2 1L306 A 12 1L224JA2 1L204 A 13 1L114JA2 1L109 A 14 1L1112E1 1L109 A 15 1L1112D1 1L109 A 16 1L1112C1 1L105 A 16 1L1112C1 1L109 A 17 1L1114A1 1L105 A 18 1L1110G3 1L105 A 19 1L1110F3 1L105 A 20 1L1110E3 1L101 A 20 1L1110E3 1L113 A 21 1L11J5A5 1L101 A 22 1L1100F3 1L101 A 22 1L1100F3 1L113 A 23 1L1100E3 1L101 A 24 1L1100D3 1L101 A 24 1L1100D3 1L102 A 25 1L1100C3 1L102 A 25 1L1100C3 1L103 A 25 1L1100C3 1L104 A 26 1L1103A1 1L104 A 27 1L1102A2 1L104 A 27 1L1102A2 1L114 A 28 0G1120D2 0G1C A 29 0G1121A2 0G1C A 30 0G11Z3A2 0G1C A 31 0G1105A2 0G1C A 32 9Y2200A2 9Y20Y A 33 9Y2201A1 9Y20Y A 34 9Y2201B1 9Y20Y A 35 9Y2201C1 9Y20Y A 36 9Y2201D1 9Y20Y A 37 9Y2201E1 9Y20Y A 38 9Y2201F1 9Y20Y A 39 9Y2201G1 9Y20Y A 40 9Y2201H1 9Y20Y A 41 9Y2209B1 9Y20Y A 42 9Y22Z2A1 9Y20Y A 43 9Y2226A3 9Y20Y A 44 9Y2226B3 9Y20Y A 45 9Y2226C3 9Y20Y A 46 9Y2220A1 9Y20Y A 47 9Y2220B1 9Y20Y A 48 9Y2220C1 9Y20Y A 49 9Y2220D1 9Y20Y |  | 3 x 50mm2
9 | SED | 9SEDB0002 | IN | IN | OUT | NO | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 310 | 314 | 314 | 9LKK0207 | 9SED002PO | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA2 1L306 A 13 1L224JA2 1L204 A 14 1L114JA2 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1L11J5A5 1L101 A 23 1L1100F3 1L101 A 23 1L1100F3 1L113 A 24 1L1100E3 1L101 A 25 1L1100D3 1L101 A 25 1L1100D3 1L102 A 26 1L1100C3 1L102 A 26 1L1100C3 1L103 A 26 1L1100C3 1L104 A 27 1L1103A1 1L104 A 28 1L1102A2 1L104 A 28 1L1102A2 1L114 A 29 0G1120D2 0G1C A 30 0G1121A2 0G1C A 31 0G11Z3A2 0G1C A 32 0G1105A2 0G1C A 33 9Y2200A2 9Y20Y A 34 9Y2201A1 9Y20Y A 35 9Y2201B1 9Y20Y A 36 9Y2201C1 9Y20Y A 37 9Y2201D1 9Y20Y A 38 9Y2201E1 9Y20Y A 39 9Y2201F1 9Y20Y A 40 9Y2201G1 9Y20Y A 41 9Y2201H1 9Y20Y A 42 9Y2209B1 9Y20Y A 43 9Y22Z2A1 9Y20Y A 44 9Y2226A3 9Y20Y A 45 9Y2226B3 9Y20Y A 46 9Y2226C3 9Y20Y A 47 9Y2220A1 9Y20Y A 48 9Y2220B1 9Y20Y A 49 9Y2220C1 9Y20Y A 50 9Y2220D1 9Y20Y |  | 3 x 50mm2
9 | SED | 9SEDB0003 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 279 | 308 | 308 | 9LKK0405 | 9SED008VD | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L334JA1 1L306 A 13 1L224JA1 1L204 A 14 1L114JA1 1L109 A 15 1L1112E1 1L109 A 16 1L1112D1 1L109 A 17 1L1112C1 1L105 A 17 1L1112C1 1L109 A 18 1L1114A1 1L105 A 19 1L1110G3 1L105 A 20 1L1110F3 1L105 A 21 1L1110E3 1L101 A 21 1L1110E3 1L113 A 22 1L11J5A5 1L101 A 23 1L1100F3 1L101 A 23 1L1100F3 1L113 A 24 1L1100E3 1L101 A 25 1L1100D3 1L101 A 25 1L1100D3 1L102 A 26 1L1100C3 1L102 A 26 1L1100C3 1L103 A 26 1L1100C3 1L104 A 27 1L1103A1 1L104 A 28 1L1102A2 1L104 A 28 1L1102A2 1L114 A 29 0G1120D2 0G1C A 30 0G1121A2 0G1C A 31 0G11Z3A2 0G1C A 32 0G1105A2 0G1C A 33 9Y2200A2 9Y20Y A 34 9Y2201A1 9Y20Y A 35 9Y2201B1 9Y20Y A 36 9Y2201C1 9Y20Y
9 | SEK | 9SEKB0900 | OUT | OUT | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T |  | NO | ALSTHOM |  | 47 |  |  | 0SEK001AR | 0SEK001MD |  |  | 2.5
9 | SEO | 9SEOB0001 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 510 | 577 | 1 | 9LKK0406 | 9SEO001CR | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB2 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3314A3 1L301 A 22 1L33J5A6 1L301 A 23 1L22J5A6 1L201 A 24 1L11J5A6 1L101 A 25 1L1100F3 1L101 A 25 1L1100F3 1L113 A 26 1L1100E3 1L101 A 27 1L1100D3 1L101 A 27 1L1100D3 1L102 A 28 1L1100C3 1L102 A 28 1L1100C3 1L103 A 28 1L1100C3 1L104 A 29 1L1103A1 1L104 A 30 1L1102A2 1L104 A 30 1L1102A2 1L114 A 31 0G1120D2 0G1C A 32 0G1121A2 0G1C A 33 0G1121B2 0G1C A 34 0G1121C2 0G1C A 35 0G1121D2 0G1C A 36 1M1116B2 1M1? A 37 1M1116A2 1M1? A 38 1M11ABA1 1M1? A 39 1M00ABA1 1M0? A 40 1M0001A2 1M0? A 41 1M00A7A2 1M0? A 42 1M11A7A2 1M1? A 43 1M1112C4 1M1? A 44 0G1107A3 0G1D |  | 2.5
9 | SEO | 9SEOB0002 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 359 | 408 | 1 | 9LKK0610 | 9SEO002CR | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB2 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3314A3 1L301 A 22 1L33J5A6 1L301 A 23 1L22J5A6 1L201 A 24 1L11J5A6 1L101 A 25 1L1100F3 1L101 A 25 1L1100F3 1L113 A 26 1L1100E3 1L101 A 27 1L1100D3 1L101 A 27 1L1100D3 1L102 A 28 1L1100C3 1L102 A 28 1L1100C3 1L103 A 28 1L1100C3 1L104 A 29 1L1103A1 1L104 A 30 1L1102A2 1L104 A 30 1L1102A2 1L114 A 31 0G1120D2 0G1C A 32 0G1121A2 0G1C A 33 0G1121B2 0G1C A 34 0G1121C2 0G1C A 35 0A22A3A2 0A2? |  | 2.5
9 | SEO | 9SEOB0003 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 48 | 100 | 100 | 9LKN0312 | 9SEO003CR | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201B1 9Y20Y A 04 9Y2201A1 9Y20Y A 05 9Y2200A2 9Y20Y A 06 0G1105A2 0G1C A 07 0G11Z3A2 0G1C A 08 0G1121A2 0G1C |  | 2.5
9 | SEO | 9SEOB0004 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 120 | 158 | 158 | 9LKN0311 | 9SEO004CR | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201B1 9Y20Y A 04 9Y2201A1 9Y20Y A 05 9Y2200A2 9Y20Y A 06 0G1105A2 0G1C A 07 0G11Z3A2 0G1C A 08 0G1121A2 0G1C A 09 0G1120D2 0G1C |  | 2.5
9 | SEO | 9SEOB0005 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 510 | 599 | 599 | 9LKK0406 | 9SEO001CR | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB2 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3314A3 1L301 A 22 1L33J5A6 1L301 A 23 1L22J5A6 1L201 A 24 1L11J5A6 1L101 A 25 1L1100F3 1L101 A 25 1L1100F3 1L113 A 26 1L1100E3 1L101 A 27 1L1100D3 1L101 A 27 1L1100D3 1L102 A 28 1L1100C3 1L102 A 28 1L1100C3 1L103 A 28 1L1100C3 1L104 A 29 1L1103A1 1L104 A 30 1L1102A2 1L104 A 30 1L1102A2 1L114 A 31 0G1120D2 0G1C A 32 0G1121A2 0G1C A 33 0G1121B2 0G1C A 34 0G1121C2 0G1C A 35 0G1121D2 0G1C A 36 1M1116B2 1M1? A 37 1M1116A2 1M1? A 38 1M11ABA1 1M1? A 39 1M00ABA1 1M0? A 40 1M0001A2 1M0? A 41 1M00A7A2 1M0? A 42 1M11A7A2 1M1? A 43 1M1112C4 1M1? A 44 0G1107A3 0G1D |  | 16
9 | SEO | 9SEOB0006 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 120 | 129 | 129 | 9LKN0311 | 9SEO004CR | A 01 9Y2204B1 9Y20Y A 01 9Y2204B1 9Y20Y A 02 9Y2204A1 9Y20Y A 03 9Y2201B1 9Y20Y A 04 9Y2201A1 9Y20Y A 05 9Y2200A2 9Y20Y A 06 0G1105A2 0G1C A 07 0G11Z3A2 0G1C A 08 0G1121A2 0G1C A 09 0G1120D2 0G1C |  | 2.5
9 | SEP | 9SEPB0001 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 296 | 326 | 326 | 9LKK0512 | 9SEP606VE | A 01 9L3385F1 9L310 A 01 9L3385F1 9L310 A 02 2L3312A1 2L346 A 03 2L3319C1 2L346 A 04 2L3318B1 2L346 A 05 2L3325A1 2L346 A 06 2L3325B1 2L346 A 07 2L3325C1 2L344 A 07 2L3325C1 2L346 A 08 2L3325D1 2L344 A 09 2L3325E1 2L344 A 10 2L3325F1 2L341 A 10 2L3325F1 2L344 A 11 2M3300A1 2M3? A 12 2M22HAA1 2M2? A 13 2M2203A1 2M2? A 14 2M220HA2 2M2? A 15 2M110HA2 2M1? A 16 2M1121A2 2M1? A 17 2M1121B2 2M1? A 18 0G1108C3 0G1D A 19 0G1108B3 0G1D |  | 2.5
9 | SEP | 9SEPB0002 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 296 | 319 | 319 | 9LKK0511 | 9SEP607VE | A 01 9L3385F1 9L310 A 01 9L3385F1 9L310 A 02 2L3312A1 2L346 A 03 2L3319C1 2L346 A 04 2L3318B1 2L346 A 05 2L3325A1 2L346 A 06 2L3325B1 2L346 A 07 2L3325C1 2L344 A 07 2L3325C1 2L346 A 08 2L3325D1 2L344 A 09 2L3325E1 2L344 A 10 2L3325F1 2L341 A 10 2L3325F1 2L344 A 11 2M3300A1 2M3? A 12 2M22HAA1 2M2? A 13 2M2203A1 2M2? A 14 2M220HA2 2M2? A 15 2M110HA2 2M1? A 16 2M1121A2 2M1? A 17 2M1121B2 2M1? A 18 0G1108C3 0G1D A 19 0G1108B3 0G1D |  | 2.5
9 | SEP | 9SEPB0003 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 296 | 319 | 319 | 9LKK0510 | 9SEP611VE | A 01 9L3385F1 9L310 A 01 9L3385F1 9L310 A 02 2L3312A1 2L346 A 03 2L3319C1 2L346 A 04 2L3318B1 2L346 A 05 2L3325A1 2L346 A 06 2L3325B1 2L346 A 07 2L3325C1 2L344 A 07 2L3325C1 2L346 A 08 2L3325D1 2L344 A 09 2L3325E1 2L344 A 10 2L3325F1 2L341 A 10 2L3325F1 2L344 A 11 2M3300A1 2M3? A 12 2M22HAA1 2M2? A 13 2M2203A1 2M2? A 14 2M220HA2 2M2? A 15 2M110HA2 2M1? A 16 2M1121A2 2M1? A 17 2M1121B2 2M1? A 18 0G1108C3 0G1D A 19 0G1108B3 0G1D |  | 2.5
9 | SEP | 9SEPB0004 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 296 | 316 | 316 | 9LKK0509 | 9SEP613VE | A 01 9L3385F1 9L310 A 01 9L3385F1 9L310 A 02 2L3312A1 2L346 A 03 2L3319C1 2L346 A 04 2L3318B1 2L346 A 05 2L3325A1 2L346 A 06 2L3325B1 2L346 A 07 2L3325C1 2L344 A 07 2L3325C1 2L346 A 08 2L3325D1 2L344 A 09 2L3325E1 2L344 A 10 2L3325F1 2L341 A 10 2L3325F1 2L344 A 11 2M3300A1 2M3? A 12 2M22HAA1 2M2? A 13 2M2203A1 2M2? A 14 2M220HA2 2M2? A 15 2M110HA2 2M1? A 16 2M1121A2 2M1? A 17 2M1121B2 2M1? A 18 0G1108C3 0G1D A 19 0G1108B3 0G1D |  | 2.5
9 | SEP | 9SEPB0005 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 106 | 71 | 71 | 0LLL0203 | 9SEP003CR | A 01 0G1109A1 0G1D A 01 0G1109A1 0G1D A 02 0G11Z7A1 0G1D A 03 0G1108B1 0G1D |  | 70
9 | SEP | 9SEPB0006 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 9SEP003CR | 9SEP001CO | IND (SITE RUN) |  | 70
9 | SEP | 9SEPB0007 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 9LKK0212 | 9SEP612VE |  |  | 2.5 | [5 empty] | not in pericles
9 | SEP | 9SEPB0008 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 9LKK0211 | 9SEP614VE |  |  | 2.5 | [5 empty] | not in pericles
9 | SEP | 9SEPB0009 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 0 | 0 | 1 | 9LKK0612 | 9SEP608VE |  |  | 2.5 | [5 empty] | not in pericles
9 | SER | 9SERB0001 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 56 | 61 | 61 | 9LKN0101 | 9SER001PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y |  | 50
9 | SER | 9SERB0002 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 55 | 59 | 59 | 9LKN0201 | 9SER002PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y |  | 50
9 | SER | 9SERB0003 | OUT | OUT | OUT | YES | 3 | 50 | A | [5 empty] | NO |  |  | 54 | 57 | 57 | 9LKN0203 | 9SER003PO | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204D1 9Y20Y A 03 9Y2204E1 9Y20Y A 04 9Y2209C1 9Y20Y A 05 9Y2209B1 9Y20Y A 06 9Y22Z2A1 9Y20Y A 07 9Y2226A3 9Y20Y A 08 9Y2226B3 9Y20Y A 09 9Y2226C3 9Y20Y A 10 9Y2220A1 9Y20Y A 11 9Y2220B1 9Y20Y A 12 9Y2220C1 9Y20Y |  | 50
9 | SER | 9SERB0004 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 33 | 53 | 53 | 9LKN0605 | 9SER001VD | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201C1 9Y20Y |  | 2.5
9 | SER | 9SERB0005 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 23 | 41 | 41 | 9LKN0606 | 9SER002VD | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201C1 9Y20Y |  | 2.5
9 | SER | 9SERB0006 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 33 | 56 | 56 | 9LKN0607 | 9SER005VD | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201C1 9Y20Y |  | 2.5
9 | SER | 9SERB0007 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 23 | 42 | 42 | 9LKN0608 | 9SER006VD | A 01 9Y2204C1 9Y20Y A 01 9Y2204C1 9Y20Y A 02 9Y2204B1 9Y20Y A 03 9Y2204A1 9Y20Y A 04 9Y2201C1 9Y20Y |  | 2.5
9 | SES | 9SESB0001 | OUT | OUT | OUT | NO | 3 | 50 | A | [5 empty] | NO |  |  | 114 | 115 | 115 | 9LKK0205 | 9SES001PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3330S3 1L306 A 08 1L3339L4 1L306 A 09 1L3339K4 1L306 A 10 1L3351B2 1L306 A 11 1L3352A1 1L306 A 12 1L3352B1 1L306 A 13 1L3352C1 1L306 A 14 1M2210A4 1M2? A 15 1M22H8A1 1M2? A 16 1M11H8A1 1M1? A 17 1M1108A2 1M1? A 18 1M11H9A6 1M1? A 19 1M1109A6 1M1? A 20 1M1109B6 1M1? |  | 50
9 | SES | 9SESB0002 | OUT | OUT | OUT | NO | 3 | 50 | A | [5 empty] | NO |  |  | 114 | 115 | 115 | 9LKK0203 | 9SES002PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3330S3 1L306 A 08 1L3339L4 1L306 A 09 1L3339K4 1L306 A 10 1L3351B2 1L306 A 11 1L3352A1 1L306 A 12 1L3352B1 1L306 A 13 1L3352C1 1L306 A 14 1M2210A4 1M2? A 15 1M22H8A1 1M2? A 16 1M11H8A1 1M1? A 17 1M1108A2 1M1? A 18 1M11H9A6 1M1? A 19 1M1109A6 1M1? A 20 1M1109B6 1M1? |  | 50
9 | SES | 9SESB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | SPARE | [9 empty] | not in pericles
9 | SEU | 9SEUB0001 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 65 | 41 | 9LKZ0311 | 9SEU001PO | IND (SITE RUN) |  | 2.5
9 | SEU | 9SEUB0002 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 98 | 30 | 30 | 9LKK0104 | 9SEU002PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 9L3358C2 9L307 A 06 9L3358C2 9L312 A 07 9L3358B2 9L307 A 08 9L3358A2 9L307 A 09 9L33JAA3 9L307 A 10 2L22JAA3 2L244 A 11 9L11JAA3 9L115 |  | 6
9 | SEU | 9SEUB0003 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 192 | 206 | 206 | 9LKZ0312 | 9SEU003PO | A 01 1L1112C5 1L105 A 01 1L1112C5 1L105 A 01 1L1112C5 1L109 A 02 1L1112B5 1L105 A 03 1L1112A5 1L105 A 04 1L1110F5 1L105 A 05 1L1110E5 1L101 A 05 1L1110E5 1L113 A 06 1L1100E3 1L101 A 07 1L1100D3 1L101 A 07 1L1100D3 1L102 A 08 1L1100C3 1L102 A 08 1L1100C3 1L103 A 08 1L1100C3 1L104 A 09 1L1100B3 1L104 A 10 1W1100B3 1W130 A 11 1W1100A3 1W130 A 12 1W1107A1 1W130 A 13 1W11M0A1 1W131 A 14 1W00M0A1 1W031 A 15 1W0000A1 1W031 A 15 1W0000A1 1W032 A 15 1W0000A1 1W035 A 15 1W0000A1 1W037 A 15 1W0000A1 1W038 |  | 6
9 | SEU | 9SEUB0004 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 167 | 0 | 162 | 9LKK0103 | 9SEU004PO | A 01 9L3330X3 9L310 A 01 9L3330X3 9L310 A 02 9L3330W3 9L310 A 03 9L3330V3 9L310 A 04 9L3330U3 9L310 A 05 9L3330T3 9L310 A 05 9L3330T3 9L312 A 06 1L3330T3 1L306 A 07 1L3335L1 1L306 A 08 1L3335K1 1L306 A 09 1L3335J1 1L306 A 10 1L3335H1 1L306 A 11 1L3335G1 1L306 A 12 1L3335F1 1L304 A 12 1L3335F1 1L306 A 13 1L3335E1 1L304 A 14 1L33JNB1 1L304 A 15 1L3317G2 1L304 A 16 1L3317F2 1L304 A 17 1L3317E2 1L304 A 18 1L3317D2 1L304 A 19 1L3317C2 1L304 A 20 1L3317B2 1L301 A 20 1L3317B2 1L304 A 21 1L3318C2 1L301 A 22 1L3318B2 1L301 A 23 1L3308C4 1L301 A 24 1L3308D4 1L301 A 25 1L3308E4 1L301 A 26 1L33J5A6 1L301 A 27 1L22J5A6 1L201 A 28 1L11J5A6 1L101 A 29 1L1100F3 1L101 A 29 1L1100F3 1L113 A 30 1L1100E3 1L101 A 31 1L1100D3 1L101 A 31 1L1100D3 1L102 A 32 1L1100C3 1L102 A 32 1L1100C3 1L103 A 32 1L1100C3 1L104 A 33 1L1100B3 1L104 A 34 1W1100B3 1W130 A 35 1W1100A3 1W130 A 36 1W1107A1 1W130 A 37 1W11M0A1 1W131 A 38 1W00M0A1 1W031 A 39 1W0000A1 1W031 A 39 1W0000A1 1W032 A 39 1W0000A1 1W035 A 39 1W0000A1 1W037 A 39 1W0000A1 1W038 |  | 6
9 | SEU | 9SEUB0005 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 67 | 105 | 599 | 0LLL0102 | 9SEU001AR | A 01 0G1109A1 0G1D A 01 0G1109A1 0G1D A 02 0G11Z7A1 0G1D A 03 0G1108B1 0G1D A 04 0G1181A1 0G1D |  | 16
9 | SEU | 9SEUB0500 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SEU005AR | 9SEU005RG |  |  | SWA 4C 16mm2 | [5 empty] | not in pericles
9 | SEU | 9SEUB0501 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SEU005AR | 9SEU005RG |  |  | SWA 2C 2,5mm2 | [5 empty] | not in pericles
9 | SEU | 9SEUB0502 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SEU005AR | 9SEU005RG |  |  | SWA 4C 2,5mm2 | [5 empty] | not in pericles
9 | SEU | 9SEUB0505 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9DNQA01CR | 0SEU001LD |  |  | 3c x 1,5mm2 CABLE | [5 empty] | not in pericles
9 | SGZ | 9SGZB0001 | OUT | OUT | OUT | NO | 3 | 35 | A | [5 empty] | NO |  |  | 57 | 90 | 1 | 0LLL0202 | 9SGZ001PJ | A 01 0G1109A1 0G1D A 01 0G1109A1 0G1D A 02 0G11Z7A1 0G1D A 03 0G1108A1 0G1D |  | 35
9 | SGZ | 9SGZB0921 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO; A A A A A: A |  |  |  | NO |  |  |  |  | 12 | 9SHY006AR | 9SHY005AR | LOCAL:IND - IND |  | 3 X 95 | [5 empty] | not in pericles
9 | SGZ | 9SGZB0922 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO; A A A A A: A |  |  |  | NO |  |  |  |  | 12 | 9SHY006AR | ACCAGENPS | LOCAL:IND - IND |  | 4 X 2.5 | [5 empty] | not in pericles
9 | SGZ | 9SGZB0923 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO; A A A A A: A |  |  |  | NO |  |  |  |  | 15 | 9SHY006AR | ACCAGENCHILLER | LOCAL:IND - IND |  | 3 X 2.5 | [5 empty] | not in pericles
9 | SGZ | 9SGZB0924 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO; A A A A A: A |  |  |  | NO |  |  |  |  | 6 | 9SHY006AR | 9SHY001CR | LOCAL:IND - IND |  | 3 X 2.5 | [5 empty] | not in pericles
9 | SGZ | 9SGZB0930 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO; A A A A A: A |  |  |  | NO |  |  |  |  | 15 | 9SHY001AR | 9SHY020ZV | LOCAL:IND - IND |  | 7 X 0.5 | [5 empty] | not in pericles
9 | SHY | 9SHYB0001 | OUT | OUT | OUT | NO | 3 | 70 | A | [5 empty] | NO |  |  | 20 | 10 | 10 | 0LLL0201 | 9SHY001AR | IND (SITE RUN) |  | 70
9 | SHY | 9SHYB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY900CR | 9SHY001AR |  |  | 3c x 1,5mm2 PVC | [5 empty] | not in pericles
9 | SHY | 9SHYB0920 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 0LLL001TB | 9SHY006AR |  |  | 3 x 95mm2 Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0921 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY006AR | 9SHY005AR |  |  | 3 x 95mm2 Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0922 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY006AR | 9SHY001AR |  |  | 4 x 2.5mm2 Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0923 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY006AR | 9SHY001RF |  |  | 3 x 2.5mm2 Non Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0924 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY006AR | 9SHY001CR |  |  | 3 x 2.5mm2Non Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0927 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY001CR | 9SHY006ID |  |  | 3 x 1.5mm2 Non Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0929 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY005AR | 9SHY001ET |  |  | 10 x 95.0mm2 Non-Armoured | [5 empty] | not in pericles
9 | SHY | 9SHYB0930 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SHY001AR | 9SHYZV |  |  | 7 x 0.5mm2 Non-Armoured | [5 empty] | not in pericles
9 | SIR | 9SIRB0001 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 124 | 147 | 147 | 9LKK0502 | 9SIR001AG | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0002 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 129 | 149 | 149 | 9LKK0501 | 9SIR002AG | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0003 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 120 | 140 | 140 | 9LKK0601 | 9SIR003AG | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0004 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 125 | 147 | 147 | 9LKK0604 | 9SIR001PO | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0005 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 130 | 162 | 162 | 9LKK0605 | 9SIR002PO | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0006 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 120 | 138 | 138 | 9LKK0602 | 9SIR003PO | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0007 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 120 | 154 | 154 | 9LKK0603 | 9SIR004PO | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 2.5
9 | SIR | 9SIRB0008 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 125 | 141 | 141 | 9LKK0606 | 9SIR001RS | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? |  | 16
9 | SIR | 9SIRB0009 | OUT | OUT | OUT | NO | 3 | 50 | A | [5 empty] | NO |  |  | 122 | 165 | 165 | 9LKK0311 | 9SIR002CR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A9 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A6 1M1? A 18 1M1109B6 1M1? A 19 1M1109C5 1M1? |  | 50
9 | SIR | 9SIRB0010 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 123 | 128 | 128 | 9LKK0607 | 9SIR001TR | A 01 9L3356M4 9L310 A 01 9L3356M4 9L310 A 02 9L3356L4 9L310 A 03 9L3356K4 9L310 A 04 9L3356J4 9L310 A 05 9L3356H4 9L310 A 06 9L3356G4 9L312 A 07 1L3356G4 1L306 A 08 1L3356F4 1L306 A 09 1L3356E4 1L306 A 10 1L3356D4 1L306 A 11 1L3356C4 1L306 A 12 1L3356B4 1L306 A 13 1L3356A4 1L306 A 14 1M2209A8 1M2? A 15 1M22H9A6 1M2? A 16 1M11H9A6 1M1? A 17 1M1109A5 1M1? A 18 1M1109B5 1M1? A 19 1M1109C5 1M1? |  | 2.5
9 | SIR | 9SIRB0011 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 20 | 6 | 6 | 9SIR002CR | 9SIR002RS | IND (SITE RUN) |  | 16
9 | SIR | 9SIRB0012 | OUT | OUT | OUT | NO | 3 | 16 | A | [5 empty] | NO |  |  | 20 | 6 | 6 | 9SIR002CR | 9SIR003RS | IND (SITE RUN) |  | 16
9 | SIR | 9SIRB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001CR | 9SIR001ZV |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0901 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001CR | 1SIR001AR |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0902 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001CR | 2SIR001AR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0903 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9LKZ507JA | 9SIR001CR |  |  | 3c x 16mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0904 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR004JA | 9SIR001CC |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0905 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001TU | 9SIR001LA |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0906 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001TU | 9SIR002LA |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SIR | 9SIRB0907 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SIR001BN | 9SIR001CC |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0005 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001PO |  |  | 3c x 16mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0006 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002PO |  |  | 3c x 16mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0007 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO003PO |  |  | 3c x 16mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0008 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO009PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0009 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO010PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0010 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO011PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0011 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0012 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001AR | 9SRO004PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0013 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0014 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001AR | 9SRO005PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0015 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0016 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001AR | 9SRO006PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0017 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0018 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001AR | 9SRO007PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0019 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0020 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002AR | 9SRO012PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0021 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0022 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002AR | 9SRO013PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0023 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0024 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002AR | 9SRO014PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0025 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002AR |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0026 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002AR | 9SRO015PO |  |  | 3c x 50mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0027 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO003EG |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0028 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002ZV |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0029 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001ZV |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0030 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002EG |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0031 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO003AR |  |  | 3c x 10mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0032 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SR0003AR | 9SRO008PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0034 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001PJ |  |  | 4c x 16mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0035 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO004AR |  |  | 3c x 4,0mm2 220V | [5 empty] | not in pericles
9 | SRO | 9SROB0036 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001AR |  |  | 3c x 4,0mm2 110V | [5 empty] | not in pericles
9 | SRO | 9SROB0037 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002AR |  |  | 3c x 4,0mm2 110V | [5 empty] | not in pericles
9 | SRO | 9SROB0038 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO002TB |  |  | 3c x 4,0mm2 110V | [5 empty] | not in pericles
9 | SRO | 9SROB0039 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO020PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0040 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO021PO |  |  | 3c x 4,0mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0044 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO004AR | 9SRO005AR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0045 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO004AR | 9SRO001CR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0046 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (RED) | [5 empty] | not in pericles
9 | SRO | 9SROB0047 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (RED) | [5 empty] | not in pericles
9 | SRO | 9SROB0048 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (WHITE) | [5 empty] | not in pericles
9 | SRO | 9SROB0049 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (WHITE) | [5 empty] | not in pericles
9 | SRO | 9SROB0050 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (BLUE) | [5 empty] | not in pericles
9 | SRO | 9SROB0051 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (BLUE) | [5 empty] | not in pericles
9 | SRO | 9SROB0052 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 9SRO002TB |  |  | 1c x 500mm2 (BLACK) | [5 empty] | not in pericles
9 | SRO | 9SROB0060 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO001ES |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0070 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO006AR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0071 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO002TB | 9SRO006AR |  |  | 3c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0072 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO006AR | 9SRO006BX |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0073 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO006AR | 9SRO006BX |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0074 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO006BX | 9SRO024PO |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0075 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO006BX | 9SR0025PO |  |  | 3c x 2,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0076 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO006AR | 9SRO007BX |  |  | 1c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0077 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO007BX | 9SRO042VR |  |  | 1c x 1,5mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0078 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 0DID001CR |  |  | 1c x 300mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0079 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 0DID001CR |  |  | 1c x 300mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0080 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 0DID001CR |  |  | 1c x 300mm2 | [5 empty] | not in pericles
9 | SRO | 9SROB0081 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9SRO001TB | 0DID001CR |  |  | 1c x 150mm2 | [5 empty] | not in pericles
9 | SSD | 9SSDB0905 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 6SSP303AR | 6SSD869JA |  |  | 2 core x 6,0mm2 TWIN AND EARTH | [5 empty] | not in pericles
9 | TEG | 9TEGB0001 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 63 | 82 | 82 | 9LKI0302 | 9TEG001RE | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2222D1 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N33A2B1 9N3A81 A 18 9N3330A2 9N3A81 A 19 9N3315A1 9N3A81 A 19 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0002 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 62 | 86 | 86 | 9LKI0702 | 9TEG002AR | A 01 9N2222G2 9N2C45 A 01 9N2222G2 9N2C45 A 02 9N2222F2 9N2C45 A 03 9N2222E2 9N2C45 A 04 9N2222D2 9N2C45 A 05 9N2222C2 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N2200C2 9N2C34 A 08 9N2200B2 9N2A34 A 08 9N2200B2 9N2C34 A 09 9N2200A2 9N2A34 A 10 9N22A3A2 9N2A34 A 11 9N33A3A2 9N395 A 12 9N3340C2 9N395 A 13 9N3340B2 9N395 A 14 9N33A8A2 9N395 A 15 9N3342B1 9N395 A 16 9N3342A1 9N395 A 17 9N33A2A1 9N3A81 A 18 9N33A2B1 9N3A81 A 19 9N3330A2 9N3A81 A 20 9N3315A1 9N3A81 A 20 9N3315A1 9N3B91 |  | 3 x 2,5mm2
9 | TEG | 9TEGB0003 | IN | IN | OUT | NO | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 83 | 95 | 95 | 9LKI0701 | 9TEG004AR | A 01 9N2222G2 9N2C45 A 01 9N2222G2 9N2C45 A 02 9N2222F2 9N2C45 A 03 9N2222E2 9N2C45 A 04 9N2222D2 9N2C45 A 05 9N2222C2 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N2200C2 9N2C34 A 08 9N2200B2 9N2A34 A 08 9N2200B2 9N2C34 A 09 9N2200A2 9N2A34 A 10 9N22A3A2 9N2A34 A 11 9N33A3A2 9N395 A 12 9N3340C2 9N395 A 13 9N3340B2 9N395 A 14 9N33A8A2 9N395 A 15 9N3342B1 9N395 A 16 9N3342A1 9N395 A 17 9N33A2A1 9N3A81 A 18 9N33A2B1 9N3A81 A 19 9N3330A2 9N3A81 A 20 9N3315A1 9N3A81 A 20 9N3315A1 9N3B91 |  | 3 x 6mm2
9 | TEG | 9TEGB0004 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 82 | 89 | 89 | 9LKI0312 | 9TEG001PO | A 01 9N2222H2 9N2C45 A 01 9N2222H2 9N2C45 A 02 9N2222G2 9N2C45 A 03 9N2222F2 9N2C45 A 04 9N2222E2 9N2C45 A 05 9N2222D2 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N33A8A2 9N395 A 16 9N3342B1 9N395 A 17 9N3342A1 9N395 A 18 9N33A2A1 9N3A81 A 19 9N33A2B1 9N3A81 A 20 9N3330A2 9N3A81 A 21 9N3315A1 9N3A81 A 21 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0005 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 88 | 106 | 106 | 9LKI0311 | 9TEG002PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200C2 9N2C34 A 09 9N2200B2 9N2A34 A 09 9N2200B2 9N2C34 A 10 9N2200A2 9N2A34 A 11 9N22A3A2 9N2A34 A 12 9N33A3A2 9N395 A 13 9N3340C2 9N395 A 14 9N3340B2 9N395 A 15 9N33A8A2 9N395 A 16 9N3342B1 9N395 A 17 9N3342A1 9N395 A 18 9N33A2A1 9N3A81 A 19 9N33A2B1 9N3A81 A 20 9N3330A2 9N3A81 A 21 9N3315A1 9N3A81 A 21 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0006 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 85 | 111 | 111 | 9LKI0801 | 9TEG107CR | A 01 9N2221F3 9N2C45 A 01 9N2221F3 9N2C45 A 02 9N2221E3 9N2C45 A 03 9N2221D3 9N2C45 A 04 9N2221C3 9N2C45 A 05 9N2221B3 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N33A2B1 9N3A81 A 18 9N3330A2 9N3A81 A 19 9N3315A1 9N3A81 A 19 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0007 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 86 | 109 | 109 | 9LKI0802 | 9TEG108CR | A 01 9N2221F3 9N2C45 A 01 9N2221F3 9N2C45 A 02 9N2221E3 9N2C45 A 03 9N2221D3 9N2C45 A 04 9N2221C3 9N2C45 A 05 9N2221B3 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N33A2B1 9N3A81 A 18 9N3330A2 9N3A81 A 19 9N3315A1 9N3A81 A 19 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0008 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 79 | 96 | 96 | 9LKI0803 | 9TEG003ZV | A 01 9N2222F2 9N2C45 A 01 9N2222F2 9N2C45 A 02 9N2222E2 9N2C45 A 03 9N2222D2 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N33A2B1 9N3A81 A 18 9N3330A2 9N3A81 A 19 9N3315A1 9N3A81 A 19 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0009 | OUT | OUT | OUT | NO | 3 | 2.5 | A | [5 empty] | NO |  |  | 84 | 95 | 95 | 9LKI0804 | 9TEG004ZV | A 01 9N2222F2 9N2C45 A 01 9N2222F2 9N2C45 A 02 9N2222E2 9N2C45 A 03 9N2222D2 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N33A2B1 9N3A81 A 18 9N3330A2 9N3A81 A 19 9N3315A1 9N3A81 A 19 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0010 | OUT | OUT | OUT | NO | 2 | 2.5 | A | [5 empty] | NO |  |  | 63 | 78 | 78 | 9LKI0301 | 9TEG002RE | A 01 9N2222G2 9N2C45 A 01 9N2222G2 9N2C45 A 02 9N2222F2 9N2C45 A 03 9N2222E2 9N2C45 A 04 9N2222D2 9N2C45 A 05 9N2222C2 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N2200C2 9N2C34 A 08 9N2200B2 9N2A34 A 08 9N2200B2 9N2C34 A 09 9N2200A2 9N2A34 A 10 9N22A3A2 9N2A34 A 11 9N33A3A2 9N395 A 12 9N3340C2 9N395 A 13 9N3340B2 9N395 A 14 9N33A8A2 9N395 A 15 9N3342B1 9N395 A 16 9N3342A1 9N395 A 17 9N33A2A1 9N3A81 A 18 9N33A2B1 9N3A81 A 19 9N3330A2 9N3A81 A 20 9N3315A1 9N3A81 A 20 9N3315A1 9N3B91 |  | 2.5
9 | TEG | 9TEGB0021 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 44 | 9TEG001AR | 9LNF034JA | IND 9N3151A, 9N3302B, 9N3311A, 9N3A52A, 9N3182B, 1N3031A, IN2CBA, 1N2241A, IND |  | 2 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TEG | 9TEGB0022 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 30 | 9TEG001AR | 9TEG502TO | IND 9N3151A,IND |  | 2 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TEG | 9TEGB0023 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  | 30 | 9TEG501MO | 9TEG502TO | IND (SITE RUN) |  | 2 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TEG | 9TEGB0701 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 28 | 0 | 28 | 9TEG002AR | 9TEG101CR | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0702 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 33 | 0 | 33 | 9TEG002AR | 9TEG103CR | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0703 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 45 | 0 | 45 | 9TEG004AR | 9TEG003RS | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 3 x 2,5mm2
9 | TEG | 9TEGB0704 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 30 | 0 | 30 | 9TEG002AR | 9TEG003AR | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0705 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 30 | 0 | 30 | 9TEG002AR | 9TEG003AR | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEG | 9TEGB0706 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 30 | 0 | 30 | 9TEG002AR | 9TEG003AR | A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3A81 A 01 9N3315A1 9N3B91 |  | 2 x 2,5mm2
9 | TEP | 9TEPB0001 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 44 | 59 | 59 | 9LKI0407 | 9TEP005PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200D2 9N2C34 A 09 9N2200E2 9N2C34 A 10 9N2200F2 9N2C34 A 11 9N2213A1 9N2C32 A 12 9N2259A1 9N2C32 |  | 3 x 2,5mm2
9 | TEP | 9TEPB0002 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 44 | 59 | 59 | 9LKI0408 | 9TEP006PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200D2 9N2C34 A 09 9N2200E2 9N2C34 A 10 9N2200F2 9N2C34 A 11 9N2213A1 9N2C32 A 12 9N2259A1 9N2C32 |  | 3 x 2,5mm2
9 | TEP | 9TEPB0003 | IN | IN | OUT | YES | 3 | 50 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 146 | 55 | 55 | 9LKI0103 | 9TEP007PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N2200D2 9N2C34 A 09 9N2200E2 9N2C34 A 10 9N2200F2 9N2C34 A 11 9N2213A1 9N2C32 A 12 9N2259A1 9N2C32 |  | 3 x 50mm2
9 | TEP | 9TEPB0004 | IN | IN | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 69 | 86 | 82 | 9LKI0409 | 9TEP008PO | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N22C1A1 9N2C47 A 09 9N2269A5 9N2C34 A 09 9N2269A5 9N2D35 A 09 9N2269A5 9N2D36 A 10 9N229DA2 9N2D36 A 11 9N2206A1 9N2D36 A 12 9N2206B1 9N2D36 A 13 9N2206C1 9N2D36 A 14 9N2207D1 9N2D09 A 15 9N228DA1 9N2D09 A 16 9N2209A1 9N2D09 A 17 9N2211A1 9N2D09 A 18 9N2212A1 9N2D50 A 19 9N2212B1 9N2D50 A 20 9N2212C1 9N2D50 A 21 9N2212D1 9N2D50 |  | 3 x 6mm2
9 | TEP | 9TEPB0005 | IN | IN | OUT | YES | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 62 | 85 | 66 | 9LKI0412 | 9TEP009PO | A 01 9N2222H1 9N2C45 A 01 9N2222H1 9N2C45 A 02 9N2222G1 9N2C45 A 03 9N2222F1 9N2C45 A 04 9N2222E1 9N2C45 A 05 9N2222D1 9N2C45 A 06 9N2222C1 9N2C45 A 07 9N2222B1 9N2C47 A 08 9N22C1A1 9N2C47 A 09 9N2269A3 9N2C34 A 09 9N2269A3 9N2D35 A 09 9N2269A3 9N2D36 A 10 9N229DA2 9N2D36 A 11 9N2206A1 9N2D36 A 12 9N2206B1 9N2D36 A 13 9N2206C1 9N2D36 A 14 9N2207D1 9N2D09 A 15 9N228DA1 9N2D09 A 16 9N2209A1 9N2D09 A 17 9N2211A1 9N2D09 A 18 9N2212A1 9N2D50 A 19 9N2212B1 9N2D50 |  | 3 x 6mm2
9 | TEP | 9TEPB0006 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 71 | 85 | 78 | 9LKI0411 | 9TEP010PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N22C1A1 9N2C47 A 09 9N2269A8 9N2C34 A 09 9N2269A8 9N2D35 A 09 9N2269A8 9N2D36 A 10 9N229DA2 9N2D36 A 11 9N2206A1 9N2D36 A 12 9N2206B1 9N2D36 A 13 9N2206C1 9N2D36 A 14 9N2207D1 9N2D09 A 15 9N228DA1 9N2D09 A 16 9N2209A1 9N2D09 A 17 9N2211A1 9N2D09 A 18 9N2212A1 9N2D50 A 19 9N2212B1 9N2D50 A 20 9N2212C1 9N2D50 A 21 9N2212D1 9N2D50 |  | 3 x 2,5mm2
9 | TEP | 9TEPB0007 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 65 | 75 | 69 | 9LKI0410 | 9TEP011PO | A 01 9N2221H3 9N2C45 A 01 9N2221H3 9N2C45 A 02 9N2221G3 9N2C45 A 03 9N2221F3 9N2C45 A 04 9N2221E3 9N2C45 A 05 9N2221D3 9N2C45 A 06 9N2221C3 9N2C45 A 07 9N2221B3 9N2C47 A 08 9N22C1A1 9N2C47 A 09 9N2269A6 9N2C34 A 09 9N2269A6 9N2D35 A 09 9N2269A6 9N2D36 A 10 9N229DA2 9N2D36 A 11 9N2206A1 9N2D36 A 12 9N2206B1 9N2D36 A 13 9N2206C1 9N2D36 A 14 9N2207D1 9N2D09 A 15 9N228DA1 9N2D09 A 16 9N2209A1 9N2D09 A 17 9N2211A1 9N2D09 A 18 9N2212A1 9N2D50 A 19 9N2212B1 9N2D50 |  | 3 x 2,5mm2
9 | TEP | 9TEPB0008 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 69 | 76 | 80 | 9LKI0512 | 9TEP012PO | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A9 9N2C34 A 08 9N2269A9 9N2D35 A 08 9N2269A9 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2211A1 9N2D09 A 17 9N2212A1 9N2D50 A 18 9N2212B1 9N2D50 A 19 9N2212C1 9N2D50 |  | 3 x 16mm2
9 | TEP | 9TEPB0009 | IN | IN | OUT | YES | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 69 | 76 | 80 | 9LKI0511 | 9TEP013PO | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A6 9N2C34 A 08 9N2269A6 9N2D35 A 08 9N2269A6 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2211A1 9N2D09 A 17 9N2212A1 9N2D50 A 18 9N2212B1 9N2D50 A 19 9N2212C1 9N2D50 |  | 3 x 16mm2
9 | TEP | 9TEPB0010 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 63 | 75 | 70 | 9LKI0510 | 9TEP014PO | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A3 9N2C34 A 08 9N2269A3 9N2D35 A 08 9N2269A3 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2211A1 9N2D09 A 17 9N2212A1 9N2D50 A 18 9N2212B1 9N2D50 |  | 3 x 2,5mm2
9 | TEP | 9TEPB0546 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 0 | 20 | 9TEP540UB | 9TEP509UB | F9TEP B0546 A IN 02 2.5 A 9N2D46 N2D46 D21 9TEP 540UB 9N2D46 N2D46 D04 9TEP 509UB 20 |  | 2 x 2,5mm2
9 | TEP | 9TEPB0730 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 20 | 0 | 20 | 9TEP740UB | 9TEP709UB | F9TEP B0730 A IN 02 2.5 A 9N2D46 N2D46 C43 9TEP 740UB 9N2D46 N2D46 C26 9TEP 709UB 20 |  | 2 x 2,5mm2
9 | TES | 9TESB0001 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 56 | 85 | 82 | 9LKI0509 | 9TES001AG | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A5 9N2C34 A 08 9N2269A5 9N2D35 A 08 9N2269A5 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2206D1 9N2D36 A 14 9N227DA2 9N2D09 A 15 9N337DA2 9N3D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0002 | IN | IN | OUT | NO | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 213 | 150 | 191 | 9LKX0107 | 9TES801AR | A 01 2C1143A1 2C1A A 01 2C1143A1 2C1A A 02 2C1108B1 2C1A A 03 2C1108A1 2C1A A 04 2C0008A1 2C0A A 05 2C0001C3 2C0A A 06 1C0001B3 1C0A A 07 1C0001A3 1C0A A 08 2G0000A3 2G0P A 09 2P0002A3 2P0A A 10 2P00W2A3 2P0A A 11 2P0000F6 2P0A A 12 2P00W4A1 2P0A A 13 2P00A0A1 2P0A A 14 2P11A0A1 2P1A A 15 2P1104A1 2P1A A 16 0G1182A1 0G1P A 17 0G1182B1 0G1P A 18 0G1104A1 0G1P |  | 3 x 35mm2
9 | TES | 9TESB0003 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 214 | 155 | 193 | 9LKX0203 | 9TES850AR | A 01 2C1143A1 2C1A A 01 2C1143A1 2C1A A 02 2C1108B1 2C1A A 03 2C1108A1 2C1A A 04 2C0008A1 2C0A A 05 2C0001C3 2C0A A 06 1C0001B3 1C0A A 07 1C0001A3 1C0A A 08 2G0000A3 2G0P A 09 2P0002A3 2P0A A 10 2P00W2A3 2P0A A 11 2P0000F6 2P0A A 12 2P00W4A1 2P0A A 13 2P00A0A1 2P0A A 14 2P11A0A1 2P1A A 15 2P1104A1 2P1A A 16 0G1182A1 0G1P A 17 0G1182B1 0G1P A 18 0G1104A1 0G1P |  | 3 x 16mm2
9 | TES | 9TESB0004 | IN | IN | OUT | NO | 3 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 83 | 66 | 92 | 9LKI0506 | 9TES601AR | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A3 9N2C34 A 08 9N2269A3 9N2D35 A 08 9N2269A3 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 A 18 9N2209D1 9N2F67 A 19 9N22F0A1 9N2F67 A 20 9N00F0A1 9N0F33 A 21 9N0001A1 9N0F33 A 22 9N0003A1 9N0F31 A 22 9N0003A1 9N0F32 |  | 3 x 6mm2
9 | TES | 9TESB0005 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 40 | 44 | 1 | 9LKI0505 | 9TES004CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A8 9N2C34 A 08 9N2269A8 9N2D35 A 08 9N2269A8 9N2D36 A 09 9N229DA2 9N2D36 |  | 3 x 16mm2
9 | TES | 9TESB0006 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 60 | 66 | 1 | 9LKI0503 | 9TES002CX | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A9 9N2C34 A 08 9N2269A9 9N2D35 A 08 9N2269A9 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 A 18 9N2209D1 9N2F67 |  | 3 x 2,5mm2
9 | TES | 9TESB0008 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 36 | 61 | 1 | 9LKI0609 | 9TES001DM | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2224A1 9N2C47 A 04 9N22C0A3 9N2C47 A 05 1N33C0A3 1N3C76 A 06 1N33C0B3 1N3C76 A 07 1N44C0A3 1N4C76 A 08 1N44C0B3 1N4C76 A 09 1N55C0A3 1N5C76 A 10 1N5501A1 1N5C76 A 11 9N5501A1 9N5A01 |  | 3 x 2,5mm2
9 | TES | 9TESB0009 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 64 | 67 | 1 | 9LKI0502 | 9TES006CR | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A5 9N2C34 A 08 9N2269A5 9N2D35 A 08 9N2269A5 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 |  | 3 x 2,5mm2
9 | TES | 9TESB0010 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 58 | 65 | 60 | 9LKI0501 | 9TES004MO | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A5 9N2C34 A 08 9N2269A5 9N2D35 A 08 9N2269A5 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 |  | 3 x 2,5mm2
9 | TES | 9TESB0012 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 39 | 41 | 41 | 9LKI0602 | 9TES008CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A8 9N2C34 A 08 9N2269A8 9N2D35 A 08 9N2269A8 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 |  | 3 x 2,5mm2
9 | TES | 9TESB0013 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 39 | 57 | 57 | 9LKI0603 | 9TES008CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A8 9N2C34 A 08 9N2269A8 9N2D35 A 08 9N2269A8 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 |  | 3 x 2,5mm2
9 | TES | 9TESB0014 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 56 | 60 | 63 | 9LKI0604 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A6 9N2C34 A 08 9N2269A6 9N2D35 A 08 9N2269A6 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0015 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 56 | 62 | 64 | 9LKI0605 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A6 9N2C34 A 08 9N2269A6 9N2D35 A 08 9N2269A6 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0016 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 88 | 101 | 100 | 9LKI0505 | 9TES502AR | A 01 9N2222G1 9N2C45 A 01 9N2222G1 9N2C45 A 02 9N2222F1 9N2C45 A 03 9N2222E1 9N2C45 A 04 9N2222D1 9N2C45 A 05 9N2222C1 9N2C45 A 06 9N2222B1 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A6 9N2C34 A 08 9N2269A6 9N2D35 A 08 9N2269A6 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 A 17 9N2209C1 9N2F67 A 18 9N2209D1 9N2F67 A 19 9N22F0A1 9N2F67 A 20 9N00F0A1 9N0F33 A 21 9N0001B1 9N0E33 A 21 9N0001B1 9N0F33 A 22 9N00F5A1 9N0E33 A 23 9N0005A1 9N0E33 A 24 9N0005B1 9N0E34 |  | 3 x 16mm2
9 | TES | 9TESB0017 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 67 | 60 | 84 | 9LKI0610 | 9TES024VS | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3332D1 9N3C02 A 14 9N33C4A1 9N3C02 A 15 9N4404A1 9N4C01 |  | 3 x 2,5mm2
9 | TES | 9TESB0018 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 56 | 64 | 1 | 9LKI0601 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N22C1A1 9N2C47 A 08 9N2269A2 9N2C34 A 08 9N2269A2 9N2D35 A 08 9N2269A2 9N2D36 A 09 9N229DA2 9N2D36 A 10 9N2206A1 9N2D36 A 11 9N2206B1 9N2D36 A 12 9N2206C1 9N2D36 A 13 9N2207D1 9N2D09 A 14 9N228DA1 9N2D09 A 15 9N2209A1 9N2D09 A 16 9N2209B1 9N2D09 |  | 3 x 16mm2
9 | TES | 9TESB0019 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 74 | 90 | 1 | 9LKI0901 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3338A1 9N3D51 A 14 9N3337A1 9N3D51 A 15 9N337DA2 9N3D09 A 16 9N227DA2 9N2D09 A 17 9N2207D1 9N2D09 A 18 9N228DA1 9N2D09 A 19 9N2209A1 9N2D09 A 20 9N2209B1 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0020 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 74 | 90 | 1 | 9LKI0601 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3338A1 9N3D51 A 14 9N3337A1 9N3D51 A 15 9N337DA2 9N3D09 A 16 9N227DA2 9N2D09 A 17 9N2207D1 9N2D09 A 18 9N228DA1 9N2D09 A 19 9N2209A1 9N2D09 A 20 9N2209B1 9N2D09 |  | 3 x 16mm2
9 | TES | 9TESB0021 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 74 | 94 | 1 | 9LKI0608 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3338A1 9N3D51 A 14 9N3337A1 9N3D51 A 15 9N337DA2 9N3D09 A 16 9N227DA2 9N2D09 A 17 9N2207D1 9N2D09 A 18 9N228DA1 9N2D09 A 19 9N2209A1 9N2D09 A 20 9N2209B1 9N2D09 |  | 3 x 16mm2
9 | TES | 9TESB0022 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 75 | 92 | 1 | 9LKI0310 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3338A1 9N3D51 A 14 9N3337A1 9N3D51 A 15 9N337DA2 9N3D09 A 16 9N227DA2 9N2D09 A 17 9N2207D1 9N2D09 A 18 9N228DA1 9N2D09 A 19 9N2209A1 9N2D09 A 20 9N2209B1 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0023 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 75 | 93 | 1 | 9LKI0310 | 9TES007CR | A 01 9N2221G3 9N2C45 A 01 9N2221G3 9N2C45 A 02 9N2221F3 9N2C45 A 03 9N2221E3 9N2C45 A 04 9N2221D3 9N2C45 A 05 9N2221C3 9N2C45 A 06 9N2221B3 9N2C47 A 07 9N2200D2 9N2C34 A 08 9N2200E2 9N2C34 A 09 9N2200F2 9N2C34 A 10 9N2200G2 9N2C34 A 11 9N22C4A3 9N2C34 A 12 9N33D6A1 9N3D51 A 13 9N3338A1 9N3D51 A 14 9N3337A1 9N3D51 A 15 9N337DA2 9N3D09 A 16 9N227DA2 9N2D09 A 17 9N2207D1 9N2D09 A 18 9N228DA1 9N2D09 A 19 9N2209A1 9N2D09 A 20 9N2209B1 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0024 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 45 | 0 | 1 | 9LKI0504 | 9TES007CR | A 01 9N2221G1 9N2C45 A 01 9N2221G1 9N2C45 A 02 9N2221F1 9N2C45 A 03 9N2221E1 9N2C45 A 04 9N2221D1 9N2C45 A 05 9N2260A2 9N2C45 A 06 9N2260B2 9N2C45 A 07 9N22C2A1 9N2C45 A 08 9N2267A6 9N2C34 A 08 9N2267A6 9N2D35 A 08 9N2267A6 9N2D36 A 09 9N224DA1 9N2D36 A 10 9N2206C2 9N2D36 A 11 9N2207D2 9N2D09 |  | 3 x 2,5mm2
9 | TES | 9TESB0816 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TES001RG |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0817 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TES018CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0818 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TES018CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0819 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TES018CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0821 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TESES |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0822 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TESES |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0823 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TESTV |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0824 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS |  |  |  | 9TES007CR | 9TESHV |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0900 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 52 | 9TES030CR | 9TES100BC |  |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0901 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 10 | 9TES030CR | 9TES018CR | IND / C-D-E-G. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0902 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 6 | 9TES030CR | 9TES101BC | IND / C-D-E-F. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0903 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES100PJ | 9TES001HV |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0904 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 10 | 9TES030CR | 9TES100PJ | IND / C-D-E-G-J. |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0905 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 10 | 9TES030CR | 9TES101PJ | IND / C-D-E-G-K. |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0906 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 40 | 9TES030CR | 9TES102PJ | IND / C-B-A-LV 2091B,LV 2092C-D-E-F, IND / A-B-C-D-E-F. |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0907 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 40 | 9TES030CR | 9TES103PJ | IND / C-B-A-LV 2091B,LV 2092C-D-E-F, IND / A-B-C-D-G. |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0908 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 65 | 9TES030CR | 9TES701AR | IND / C-B-A-LV 2091B,LV 2092C-LV 2F01A, LV 0F01A-LV 0011A, LV 0031A-IND / A. |  | 3 x 16mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0909 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 12 | 9TES031CR | 9TES701AR | IND / A. |  | 3 x 16mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0910 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES101PJ | 9TES001SC |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0911 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 15 | 9TES031CR | 9TES104PJ | IND / A-C. |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0912 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 15 | 9TES031CR | 9TES105PJ | IND / A-B-E |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0913 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 15 | 9TES100BC | 9TES001ES | IND / D-E, IND / A. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0914 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES018CR | 9TES002ES |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0915 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES018CR | 9TES003ES |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0916 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 25 | 9TES100BC | 9TES004ES | IND / F-E-B-H, IND / A-B. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0917 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 30 | 9TES101BC | 9TES005ES | IND / F-E-B-H, IND / A-C. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0918 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 13 | 9TES701AR | 9TES032CR | IND / A. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0919 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 13 | 9TES701AR | 9TES032CR | IND / A. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0920 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 30 | 9TES032CR | 9TES006ES | IND / A - LV 0031A, LV 0031A - IND / D, IND / D-E. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0921 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 55 | 9TES032CR | 9TES007ES | IND / A - LV 0031A, LV 0031A - IND / D, IND / D-F. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0922 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 40 | 9TES032CR | 9TES008ES | IND / A - LV 0031A, LV 0031A - IND / D, IND / A-B. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0923 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 50 | 9TES032CR | 9TES009ES | IND / A - LV 0031A, LV 0031A - IND / D, IND / A-C. |  | 3 x 2,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0924 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 5 | 9DMN002PR | 9TES102BC | IND (SITE RUN) |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0925 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 18 | 9DMN005PR | 9TES106BC | IND (SITE RUN) |  | 3 x 1,5mm2 | [5 empty] | duplicate cable number
9 | TES | 9TESB0926 | IN | IN | OUT | NO | 3 | 1 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES102PJ | 9TES002HV |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0927 | IN | IN | OUT | NO | 3 | 1 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES103PJ | 9TES002SC |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0928 | IN | IN | OUT | NO | 3 | 1 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES104PJ | 9TES003HV |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0929 | IN | IN | OUT | NO | 3 | 1 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES105PJ | 9TES003SC |  |  | 3 x 1mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0930 | IN | IN | OUT | NO | 3 | 16 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  | 120 | 9LKI303JA | 9TES900AR | 9N2C45, IND, 9N2222G1-C1, 9N2C47, 2222B1, 22C1A1, 2C34, 2269A6, 2D35, 2269A6, 2D36, 2269A6, 229DA2, 2206A1-C1, 2D09, 2207D1, 228DA1, 2209A1-B1, 2F67, 2209C1-D1, 22F0A1, 0F33, 00F0A1, 0E33, 0001B1, 0F33, 0001B1, 0E33, 00F5A1, 0005A1, 0E34, 0005B1, IND |  | 3 x 16mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0931 | IN | IN | OUT | NO | 4 | 10 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LKI900AR | 9TES601MO |  |  | 4 x 10mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0932 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES900AR | 9TES602MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0933 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES900AR | 9TES603MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0934 | IN | IN | OUT | NO | 4 | 10 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES900AR | 9TES601MO |  |  | 4 x 10mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0940 | IN | IN | OUT | NO | 7 | 6 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES908MO |  |  | 7 x 6mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0941 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES909MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0942 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES910MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0943 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES911MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0944 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES912MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0945 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES913MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0946 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES914MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0947 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES915MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0948 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES917MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0960 | IN | IN | OUT | NO | 3 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES917ES |  |  | 3 x 1,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0961 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES108PJ |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0962 | IN | IN | OUT | NO | 2 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES300CT |  |  | 2 x 1,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0963 | IN | IN | OUT | NO | 2 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES301CT |  |  | 2 x 1,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0964 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES056CR | 9TES931MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0965 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES056CR | 9TES932MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0966 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES011CR | 9TES056CR |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0967 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | CRTV | 9TES911MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0968 | IN | IN | OUT | NO | 4 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | CRTV | 9TES912MO |  |  | 4 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0969 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | CRTV | 9TES007CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0970 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | CRTV | 9TES007CR |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0971 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9LKI610JA | 9TES103ED |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0973 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES105ED | 9TES005MO |  |  | 3 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0975 | IN | IN | OUT | NO | 2 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES051CR | 9TES120TU |  |  | 2 x 2,5mm2 | [5 empty] | not in pericles
9 | TES | 9TESB0976 | IN | IN | OUT | NO | 4 | 1.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | NIA (MODIFICATION) | EMS |  |  |  | 9TES120TU | 9TES051CR |  |  | 4 x 1,5mm2 | [5 empty] | not in pericles
9 | TEU | 9TEUB0001 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 35 | 58 | 58 | 9LKI0611 | 9TEU001AG | A 01 9N2222G2 9N2C45 A 01 9N2222G2 9N2C45 A 02 9N2222F2 9N2C45 A 03 9N2222E2 9N2C45 A 04 9N2224A1 9N2C47 A 05 9N22C0A1 9N2C47 A 06 1N33C0A1 1N3C76 A 07 1N3310A2 1N3C76 A 08 9N3318B2 9N3C70 A 08 9N3318B2 9N3C79 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0002 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 120 | 58 | 58 | 9LKI0612 | 9TEU002AG | A 01 9N2221H1 9N2C45 A 01 9N2221H1 9N2C45 A 02 9N2221G1 9N2C45 A 03 9N2221F1 9N2C45 A 04 9N2221E1 9N2C45 A 05 9N2221D1 9N2C45 A 06 9N2260A2 9N2C45 A 07 9N2260B2 9N2C45 A 08 9N2260C2 9N2C45 A 09 9N2263A1 9N2D34 A 10 9N2203B1 9N2D34 A 11 9N33D5A1 9N3D51 A 12 9N3338A2 9N3D51 A 13 9N3332E1 9N3C02 A 13 9N3332E1 9N3D08 A 14 9N3332F1 9N3D08 A 15 9N3332G1 9N3D08 A 16 9N3332H1 9N3D08 A 17 9N3332J1 9N3D08 A 18 9N3332K1 9N3D08 A 19 9N3332L1 9N3D08 A 20 2N33D2A1 2N3D24 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0003 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 66 | 79 | 74 | 9LKI0712 | 9TEU003AG | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2222D1 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N22C1A1 9N2C47 A 07 9N2269A3 9N2C34 A 07 9N2269A3 9N2D35 A 07 9N2269A3 9N2D36 A 08 9N229DA2 9N2D36 A 09 9N2206A1 9N2D36 A 10 9N2206B1 9N2D36 A 11 9N2206C1 9N2D36 A 12 9N2207D1 9N2D09 A 13 9N228DA1 9N2D09 A 14 9N2209A1 9N2D09 A 15 9N2211A1 9N2D09 A 16 9N2212A1 9N2D50 A 17 9N2212B1 9N2D50 A 18 9N2212C1 9N2D50 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0004 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 124 | 56 | 56 | 9LKI0711 | 9TEU001PO | A 01 9N2221H1 9N2C45 A 01 9N2221H1 9N2C45 A 02 9N2221G1 9N2C45 A 03 9N2221F1 9N2C45 A 04 9N2221E1 9N2C45 A 05 9N2221D1 9N2C45 A 06 9N2260A2 9N2C45 A 07 9N2260B2 9N2C45 A 08 9N2260C2 9N2C45 A 09 9N2263A1 9N2D34 A 10 9N2203B1 9N2D34 A 11 9N33D5A1 9N3D51 A 12 9N3338A2 9N3D51 A 13 9N3332E1 9N3C02 A 13 9N3332E1 9N3D08 A 14 9N3332F1 9N3D08 A 15 9N3332G1 9N3D08 A 16 9N3332H1 9N3D08 A 17 9N3332J1 9N3D08 A 18 9N3332K1 9N3D08 A 19 9N3332L1 9N3D08 A 20 2N33D2A1 2N3D24 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0005 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 49 | 55 | 55 | 9LKI0710 | 9TEU002PO | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2222D1 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N2200D2 9N2C34 A 07 9N2200E2 9N2C34 A 08 9N2200F2 9N2C34 A 09 9N2213A1 9N2C32 A 10 9N2213B1 9N2C32 A 11 9N2216A1 9N2C55 A 12 9N2216B1 9N2C41 A 13 9N2216C1 9N2C41 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0006 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 56 | 72 | 72 | 9LKI0709 | 9TEU003PO | A 01 9N2221F3 9N2C45 A 01 9N2221F3 9N2C45 A 02 9N2221E3 9N2C45 A 03 9N2221D3 9N2C45 A 04 9N2221C3 9N2C45 A 05 9N2221B3 9N2C47 A 06 9N2200C2 9N2C34 A 07 9N2200B2 9N2A34 A 07 9N2200B2 9N2C34 A 08 9N2200A2 9N2A34 A 09 9N22A3A2 9N2A34 A 10 9N33A3A2 9N395 A 11 9N3340C2 9N395 A 12 9N3340B2 9N395 A 13 9N33A8A2 9N395 A 14 9N3342B1 9N395 A 15 9N3342A1 9N395 A 16 9N33A2A1 9N3A81 A 17 9N3312A1 9N3A81 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0007 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 46 | 55 | 55 | 9LKI0708 | 9TEU004PO | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2222D1 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N2200D2 9N2C34 A 07 9N2200E2 9N2C34 A 08 9N2200F2 9N2C34 A 09 9N2213A1 9N2C32 A 10 9N2213B1 9N2C32 A 11 9N2216A1 9N2C55 A 12 9N2216B1 9N2C41 A 13 9N2216C1 9N2C41 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0008 | IN | IN | OUT | YES | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 99 | 117 | 117 | 9LKI0707 | 9TEU008PO | A 01 9N2221F1 9N2C45 A 01 9N2221F1 9N2C45 A 02 9N2221E1 9N2C45 A 03 9N2221D1 9N2C45 A 04 9N2260A2 9N2C45 A 05 9N2260B2 9N2C45 A 06 9N2260C2 9N2C45 A 07 9N2263A1 9N2D34 A 08 9N2203B1 9N2D34 A 09 9N33D5A1 9N3D51 A 10 9N3338A2 9N3D51 A 11 9N3332E1 9N3C02 A 11 9N3332E1 9N3D08 A 12 9N3332F1 9N3D08 A 13 9N3332G1 9N3D08 A 14 9N3332H1 9N3D08 A 15 9N3334A1 9N3D08 A 16 9N3350A3 9N3F03 A 17 9N3353A1 9N3F65 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0009 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 61 | 72 | 74 | 9LKI0706 | 9TEU009PO | A 01 9N2222F1 9N2C45 A 01 9N2222F1 9N2C45 A 02 9N2222E1 9N2C45 A 03 9N2222D1 9N2C45 A 04 9N2222C1 9N2C45 A 05 9N2222B1 9N2C47 A 06 9N22C1A1 9N2C47 A 07 9N2269A3 9N2C34 A 07 9N2269A3 9N2D35 A 07 9N2269A3 9N2D36 A 08 9N229DA2 9N2D36 A 09 9N2206A1 9N2D36 A 10 9N2206B1 9N2D36 A 11 9N2206C1 9N2D36 A 12 9N2207D1 9N2D09 A 13 9N228DA1 9N2D09 A 14 9N2209A1 9N2D09 A 15 9N2211A1 9N2D09 A 16 9N2212A1 9N2D50 A 17 9N2212B1 9N2D50 A 18 9N2212C1 9N2D50 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0010 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 34 | 54 | 54 | 9LKI0705 | 9TEU010PO | A 01 9N2222F2 9N2C45 A 01 9N2222F2 9N2C45 A 02 9N2222E2 9N2C45 A 03 9N2224A1 9N2C47 A 04 9N22C0A1 9N2C47 A 05 1N33C0A1 1N3C76 A 06 1N3310A2 1N3C76 A 07 9N3318B2 9N3C70 A 07 9N3318B2 9N3C79 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0011 | IN | IN | OUT | NO | 3 | 2.5 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 34 | 54 | 54 | 9LKI0704 | 9TEU011PO | A 01 9N2222F2 9N2C45 A 01 9N2222F2 9N2C45 A 02 9N2222E2 9N2C45 A 03 9N2224A1 9N2C47 A 04 9N22C0A1 9N2C47 A 05 1N33C0A1 1N3C76 A 06 1N3310A2 1N3C76 A 07 9N3318B2 9N3C70 A 07 9N3318B2 9N3C79 |  | 3 x 2,5mm2
9 | TEU | 9TEUB0012 | IN | IN | OUT | YES | 3 | 35 | A | PVC | PVC | 1000V ac | DWT, FDR, IRT and V&T | 2RO (V&T) and 4RO | NO | ALSTHOM | EMS | 203 | 190 | 225 | 9LKI0703 | 9TEU014PO | A 01 9N2221F1 9N2C45 A 01 9N2221F1 9N2C45 A 02 9N2221E1 9N2C45 A 03 9N2221D1 9N2C45 A 04 9N2260A2 9N2C45 A 05 9N2260B2 9N2C45 A 06 9N22C2A1 9N2C45 A 07 9N2263A1 9N2D34 A 08 9N2203A1 9N2D34 A 08 9N2203A1 9N2D70 A 09 9N2201C1 9N2B34 A 09 9N2201C1 9N2D70 A 10 9N2201B1 9N2B34 A 11 9N2201A1 9N2B34 A 12 9N22B2A1 9N2B34 A 13 9N33B2A1 9N395 A 14 9N3342C2 9N395 A 15 9N33A8A1 9N395 A 16 9N3340A3 9N395 A 17 9L3385A1 9L312 A 18 9L3385B1 9L310 A 18 9L3385B1 9L312 A 19 9L3385C1 9L310 A 20 9L3385D1 9L310 A 21 9L3385E1 9L310 A 22 9L3385F1 9L310 A 23 2L3312A1 2L346 A 24 2L3319C1 2L346 A 25 2L3318B1 2L346 A 26 2L3318A1 2L346 A 27 2L33JEA1 2L346 A 28 2L22JEA1 2L244 A 29 2L11JEA1 2L149 A 30 2L1119D3 2L149 A 31 2L1119E3 2L149 A 32 2L1125E1 2L149 A 33 2L1125F1 2L145 A 33 2L1125F1 2L149 A 34 2L1125G1 2L145 A 35 2L1125H1 2L141 A 35 2L1125H1 2L145 A 35 2L1125H1 2L153 A 36 2L1125J1 2L141 A 37 2L1125K1 2L141 A 38 2L1125L1 2L141 A 39 2L1113A3 2L141 A 39 2L1113A3 2L142 A 40 2L1113B3 2L142 A 40 2L1113B3 2L143 A 40 2L1113B3 2L144 A 41 2L1113C3 2L144 A 42 2W1113C3 2W170 A 43 2W1113D3 2W170 A 44 2W1113E3 2W170 A 45 2W11M2A1 2W171 A 46 2W0010A1 2W071 A 47 9W0010A1 9W080 |  | 3 x 35mm2
9 | XCA | 9XCAB0001 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 40 | 40 | 9LKM0105 | 9XCA001AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0002 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 41 | 41 | 9LKM0105 | 9XCA001AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0003 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 48 | 48 | 9LKM0103 | 9XCA002AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0004 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 47 | 47 | 9LKM0103 | 9XCA002AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0005 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 54 | 54 | 9LKM0101 | 9XCA003AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0006 | OUT | OUT | OUT | NO | 3 | 150 | A | [5 empty] | NO |  |  | 20 | 64 | 54 | 9LKM0101 | 9XCA003AR | IND (SITE RUN) |  | 150
9 | XCA | 9XCAB0007 | OUT | OUT | OUT | NO | 3 | 6 | A | [5 empty] | NO |  |  | 20 | 16 | 16 | 9LKM0211 | 9XCA004AR | IND (SITE RUN) |  | 6
9 | XCA | 9XCAB0008 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 48 | 48 | 9XCA004AR | 9XPA001PO | IND (SITE RUN) |  | 2.5
9 | XCA | 9XCAB0009 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 47 | 47 | 9XCA004AR | 9XPA002PO | IND (SITE RUN) |  | 2.5
9 | XCA | 9XCAB0010 | OUT | OUT | OUT | YES | 3 | 2.5 | A | [5 empty] | NO |  |  | 20 | 50 | 50 | 9XCA004AR | 9XPA003PO | IND (SITE RUN) |  | 2.5
9 | XCA | 9XCAB0011 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 39 | 39 | 9XCA004AR | 9XCA010PO | IND (SITE RUN) |  | 2.5
9 | XCA | 9XCAB0012 | OUT | OUT | OUT | YES | 2 | 2.5 | A | [5 empty] | NO |  |  | 20 | 1 | 1 | 9XCA004AR | 9XCA010PO | IND (SITE RUN) |  | 2.5
9 | XCA | 9XCAB0900 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9DNVC01CR | 9XCA001AR |  |  | 4mm2 | [5 empty] | not in pericles
9 | XCA | 9XCAB0901 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA002AR |  |  | 4mm2 | [5 empty] | not in pericles
9 | XCA | 9XCAB0902 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA003AR |  |  | 4mm2 | [5 empty] | not in pericles
9 | XCA | 9XCAB0903 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA101MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0904 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA102MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0905 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA103MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0906 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA104MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0907 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA001AR | 9XCA105MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0920 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA201MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0921 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA202MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0922 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA203MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0923 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA204MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0924 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA002AR | 9XCA205MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0930 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA003AR | 9XCA301MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0931 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA003AR | 9XCA302MO |  |  | 3 x 10mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0932 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA003AR | 9XCA303MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0933 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA003AR | 9XCA304MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles
9 | XCA | 9XCAB0934 | IN IN IN IN IN: OUT; IN IN IN IN IN: OUT; OUT OUT OUT OUT OUT: OUT; NO NO NO NO NO: NO |  |  |  | NO | [5 empty] | 9XCA003AR | 9XCA305MO |  |  | 3 x 4mm2 Armoured | [5 empty] | not in pericles

## Unkown Abbrev. (hidden)
Unknown Abbreviations
Coaxial/CP | ?
Coaxial/ETA | ?
LBA | ?
B | ?
GRA | ?
CUS | ?
QDIA | ?
QSNA | ?
SECA | ?

## CAMP MV (hidden)
UNIT | SYST | ER CLASS | CATEG | RGNB | EQMRK_FR | EQMRK_TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | CORE | Dimensions (mm2) | Cable Size & Core | CBTYP | Cable_No | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) | FREQ. | START DATE (Outage) | TYPE OF TEST (ONLINE) | FREQ. | START DATE | TYPE OF TEST VISUAL / TACTILE | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | SAMPLE SELCTED FOR V&T | SAMPLE SELCTED FOR IR | SAMPLE SELCTED FOR VLF-TD | SAMPLE SELCTED FOR PD | MANUFACTURER | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE
1 | ACO | S | A |  | 1LGD 0301 | 1ACO 001PO | A | 106 |  |  | 240 | MTAL | 3 |  |  |  | K1ACOA0001 |  |  |  |  | K1ACO | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | ACO | S | A |  | 1LGD 0101 | 1ACO 002PO | A | 99 |  |  | 240 | MTAL | 3 |  |  |  | K1ACOA0002 |  |  |  |  | K1ACO | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | APA | S | A |  | 9LGE 0101 | 1APA 003PO | A | 248 |  |  | 400 | MTAL | 1 |  |  |  | K1APAA0001 |  |  |  |  | K1APA | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | APA | S | A |  | 9LGE 0101 | 1APA 003PO | A | 248 |  |  | 400 | MTAL | 1 |  |  |  | K1APAA0002 |  |  |  |  | K1APA | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | APA | S | A |  | 9LGE 0101 | 1APA 003PO | A | 248 |  |  | 400 | MTAL | 1 |  |  |  | K1APAA0003 |  |  |  |  | K1APA | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | ATE | S | A |  | 1LGD 0901 | 1ATE 901PO | A | 145 |  |  | 50 | MTAL | 3 |  |  |  | K1ATEA0001 |  |  |  |  | K1ATE | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | ATE | S | A |  | 1LGD 0902 | 1ATE 902PO | A | 144 |  |  | 50 | MTAL | 3 |  |  |  | K1ATEA0002 |  |  |  |  | K1ATE | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | ATE | S | A |  | 1LGD 0903 | 1ATE 903PO | A | 137 |  |  | 50 | MTAL | 3 |  |  |  | K1ATEA0003 |  |  |  |  | K1ATE | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | ASG | C3 | A |  | 1LHA 0601 | 1ASG 001PO | A | 49 |  |  | 50 | MTAL | 3 |  |  |  | K1ASGA0001 |  |  |  |  | K1ASG | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | ASG | C3 | A |  | 1LHB 0701 | 1ASG 002PO | B | 76 |  |  | 50 | MTAL | 3 |  |  |  | K1ASGA0002 |  |  |  |  | K1ASG | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | CEX | C9 | A |  | 1LGA 1001 | 1CEX 001PO | A | 57 |  |  | 240 | MTAL | 3 |  |  |  | K1CEXA0001 |  |  |  |  | K1CEX | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | CEX | C9 | A |  | 1LGA 0701 | 1CEX 002PO | A | 65 |  |  | 240 | MTAL | 3 |  |  |  | K1CEXA0002 |  |  |  |  | K1CEX | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | CEX | C9 | A |  | 1LGA 0501 | 1CEX 003PO | A | 67 |  |  | 240 | MTAL | 3 |  |  |  | K1CEXA0003 |  |  |  |  | K1CEX | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | CRF | C2 SPV | A |  | 1LGA 0401 | 1CRF 001PO | A | 329 |  |  | 240 | MTAL | 3 |  |  |  | K1CRFA0001 |  |  |  |  | K1CRF | A0001 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | CRF | C2 SPV | A |  | 1LGA 0201 | 1CRF 002PO | A | 316 |  |  | 240 | MTAL | 3 |  |  |  | K1CRFA0002 |  |  |  |  | K1CRF | A0002 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | CRF | C2 SPV | A |  | 1LGA 0101 | 1CRF 003PO | A | 307 |  |  | 240 | MTAL | 3 |  |  |  | K1CRFA0003 |  |  |  |  | K1CRF | A0003 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0001 |  |  |  |  | K1LGD | A0001 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0002 |  |  |  |  | K1LGD | A0002 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0003 |  |  |  |  | K1LGD | A0003 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0004 |  |  |  |  | K1LGD | A0004 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0005 |  |  |  |  | K1LGD | A0005 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0006 |  |  |  |  | K1LGD | A0006 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0007 |  |  |  |  | K1LGD | A0007 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0008 |  |  |  |  | K1LGD | A0008 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0009 |  |  |  |  | K1LGD | A0009 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0010 |  |  |  |  | K1LGD | A0010 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0011 |  |  |  |  | K1LGD | A0011 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 0501 | A | 106 |  |  | 500 | MTAL | 1 |  |  |  | K1LGDA0012 |  |  |  |  | K1LGD | A0012 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0001 |  |  |  |  | K1LGA | A0001 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0002 |  |  |  |  | K1LGA | A0002 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0003 |  |  |  |  | K1LGA | A0003 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0004 |  |  |  |  | K1LGA | A0004 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0005 |  |  |  |  | K1LGA | A0005 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0006 |  |  |  |  | K1LGA | A0006 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0007 |  |  |  |  | K1LGA | A0007 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0008 |  |  |  |  | K1LGA | A0008 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0009 |  |  |  |  | K1LGA | A0009 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0010 |  |  |  |  | K1LGA | A0010 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0011 |  |  |  |  | K1LGA | A0011 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGA | C1 SPV | A |  | 1GEV 001TS | 1LGA 0801 | A | 127 |  |  | 500 | MTAL | 1 |  |  |  | K1LGAA0012 |  |  |  |  | K1LGA | A0012 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | DEG | E | A |  | 1LHB 0901 | 1DEG 101CO | B | 148 |  |  | 50 | MTAL | 3 |  |  |  | K1DEGA0001 |  |  |  |  | K1DEG | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | DEG | E | A |  | 1LHA 0901 | 1DEG 201CO | A | 221 |  |  | 50 | MTAL | 3 |  |  |  | K1DEGA0002 |  |  |  |  | K1DEG | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | DEG | E | A |  | 1LHB 1001 | 1DEG 301CO | B | 147 |  |  | 50 | MTAL | 3 |  |  |  | K1DEGA0003 |  |  |  |  | K1DEG | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | DEG | E | A |  | 1LHA 1001 | 1DEG 401CO | A | 222 |  |  | 50 | MTAL | 3 |  |  |  | K1DEGA0004 |  |  |  |  | K1DEG | A0004 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | EAS | C3 | A |  | 1LHA 0201 | 1EAS 001PO | A | 229 |  |  | 50 | MTAL | 3 |  |  |  | K1EASA0001 |  |  |  |  | K1EAS | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | EAS | C3 | A |  | 1LHB 0201 | 1EAS 002PO | B | 147 |  |  | 50 | MTAL | 3 |  |  |  | K1EASA0002 |  |  |  |  | K1EAS | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | GGR | S | A |  | 1LGB 0101 | 1GGR 001TR | A | 137 |  |  | 240 | MTAL | 3 |  |  |  | K1GGRA0001 |  |  |  |  | K1GGR | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 1 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0001 |  |  |  |  | K1LGB | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 177 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0002 |  |  |  |  | K1LGB | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 179 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0003 |  |  |  |  | K1LGB | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 180 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0004 |  |  |  |  | K1LGB | A0004 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 181 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0005 |  |  |  |  | K1LGB | A0005 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGB | C3 | A |  | 9LGE 0201 | 1LGB 0401 | A | 180 |  |  | 500 | MTAL | 1 |  |  |  | K1LGBA0006 |  |  |  |  | K1LGB | A0006 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 225 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0004 |  |  |  |  | K1LGC | A0004 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 223 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0005 |  |  |  |  | K1LGC | A0005 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 224 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0006 |  |  |  |  | K1LGC | A0006 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 225 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0007 |  |  |  |  | K1LGC | A0007 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 227 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0008 |  |  |  |  | K1LGC | A0008 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 225 |  |  | 400 | MTAL | 1 |  |  |  | K1LGCA0009 |  |  |  |  | K1LGC | A0009 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 234 |  |  | 500 | MTAL | 1 |  |  |  | K1LGCA0010 |  |  |  |  | K1LGC | A0010 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 234 |  |  | 500 | MTAL | 1 |  |  |  | K1LGCA0011 |  |  |  |  | K1LGC | A0011 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGC | C3 | A |  | 9LGF 0301 | 1LGC 0601 | A | 233 |  |  | 500 | MTAL | 1 |  |  |  | K1LGCA0012 |  |  |  |  | K1LGC | A0012 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 1 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0013 |  |  |  |  | K1LGD | A0013 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 48 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0014 |  |  |  |  | K1LGD | A0014 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 45 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0015 |  |  |  |  | K1LGD | A0015 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 42 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0016 |  |  |  |  | K1LGD | A0016 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 45 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0017 |  |  |  |  | K1LGD | A0017 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 42 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0018 |  |  |  |  | K1LGD | A0018 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 001TR | A | 11 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0019 |  |  |  |  | K1LGD | A0019 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 001TR | A | 10 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0020 |  |  |  |  | K1LGD | A0020 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1GEV 001TS | 1LGD 001TR | A | 10 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0021 |  |  |  |  | K1LGD | A0021 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 001TR | 1LGD 001AR | A | 8 |  |  | 25 | MTCU | 1 |  |  |  | K1LGDA0022 |  |  |  |  | K1LGD | A0022 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 001AR | 1LGA TT19 | A | 9 |  |  | 25 | MTCU | 1 |  |  |  | K1LGDA0023 |  |  |  |  | K1LGD | A0023 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 47 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0025 |  |  |  |  | K1LGD | A0025 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 43 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0026 |  |  |  |  | K1LGD | A0026 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LGD | C1 SPV | A |  | 1LGD 0401 | 1LGC 0701 | A | 46 |  |  | 400 | MTAL | 1 |  |  |  | K1LGDA0027 |  |  |  |  | K1LGD | A0027 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | LHA | C3 | A |  | 1LHP 001AR | 1LHA 0401 | A | 1 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0001 |  |  |  |  | K1LHA | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 1LHP 001AR | 1LHA 0401 | A | 44 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0002 |  |  |  |  | K1LHA | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 1LHP 001AR | 1LHA 0401 | A | 44 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0003 |  |  |  |  | K1LHA | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 1LGB 0601 | 1LHA 0101 | A | 25 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0004 |  |  |  |  | K1LHA | A0004 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 1LGB 0601 | 1LHA 0101 | A | 23 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0005 |  |  |  |  | K1LHA | A0005 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 1LGB 0601 | 1LHA 0101 | A | 25 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0006 |  |  |  |  | K1LHA | A0006 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 9LHC 0201 | 1LHA 0701 | A | 69 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0007 |  |  |  |  | K1LHA | A0007 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 9LHC 0201 | 1LHA 0701 | A | 73 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0008 |  |  |  |  | K1LHA | A0008 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHA | C3 | A |  | 9LHC 0201 | 1LHA 0701 | A | 69 |  |  | 400 | MTAL | 1 |  |  |  | K1LHAA0009 |  |  |  |  | K1LHA | A0009 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LHQ 001AR | 1LHB 0401 | B | 156 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0001 |  |  |  |  | K1LHB | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LHQ 001AR | 1LHB 0401 | B | 158 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0002 |  |  |  |  | K1LHB | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LHQ 001AR | 1LHB 0401 | B | 157 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0003 |  |  |  |  | K1LHB | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LGC 0401 | 1LHB 0101 | B | 30 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0004 |  |  |  |  | K1LHB | A0004 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LGC 0401 | 1LHB 0101 | B | 30 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0005 |  |  |  |  | K1LHB | A0005 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 1LGC 0401 | 1LHB 0101 | B | 30 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0006 |  |  |  |  | K1LHB | A0006 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 9LHC 0101 | 1LHB 0801 | B | 15 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0007 |  |  |  |  | K1LHB | A0007 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 9LHC 0101 | 1LHB 0801 | B | 18 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0008 |  |  |  |  | K1LHB | A0008 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHB | C3 | A |  | 9LHC 0101 | 1LHB 0801 | B | 13 |  |  | 400 | MTAL | 1 |  |  |  | K1LHBA0009 |  |  |  |  | K1LHB | A0009 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHP | C3 | A |  | 1LHP 001GA | 1LHP 001AR | A | 13 |  |  | 400 | MTAL | 1 |  |  |  | K1LHPA0001 |  |  |  |  | K1LHP | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHP | C3 | A |  | 1LHP 001GA | 1LHP 001AR | A | 13 |  |  | 400 | MTAL | 1 |  |  |  | K1LHPA0002 |  |  |  |  | K1LHP | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHP | C3 | A |  | 1LHP 001GA | 1LHP 001AR | A | 14 |  |  | 400 | MTAL | 1 |  |  |  | K1LHPA0003 |  |  |  |  | K1LHP | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHQ | C3 | A |  | 1LHQ 001GA | 1LHQ 001AR | B | 14 |  |  | 400 | MTAL | 1 |  |  |  | K1LHQA0001 |  |  |  |  | K1LHQ | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHQ | C3 | A |  | 1LHQ 001GA | 1LHQ 001AR | B | 14 |  |  | 400 | MTAL | 1 |  |  |  | K1LHQA0002 |  |  |  |  | K1LHQ | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LHQ | C3 | A |  | 1LHQ 001GA | 1LHQ 001AR | B | 14 |  |  | 400 | MTAL | 1 |  |  |  | K1LHQA0003 |  |  |  |  | K1LHQ | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LKA | C9 | A |  | 1LGA 0303 | 1LKA 001TR | A | 16 |  |  | 50 | MTAL | 3 |  |  |  | K1LKAA0001 |  |  |  |  | K1LKA | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKB | C9 | A |  | 1LGD 0203 | 1LKB 001TR | A | 49 |  |  | 50 | MTAL | 3 |  |  |  | K1LKBA0001 |  |  |  |  | K1LKB | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKC | C9 | A |  | 1LGD 0202 | 1LKC 001TR | A | 28 |  |  | 50 | MTAL | 3 |  |  |  | K1LKCA0001 |  |  |  |  | K1LKC | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKD | C9 | A |  | 1LGB 0203 | 1LKD 001TR | A | 24 |  |  | 50 | MTAL | 3 |  |  |  | K1LKDA0001 |  |  |  |  | K1LKD | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKE | C9 | A |  | 1LGB 0202 | 1LKE 001TR | A | 36 |  |  | 50 | MTAL | 3 |  |  |  | K1LKEA0001 |  |  |  |  | K1LKE | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKF | C9 | A |  | 1LGC 0303 | 1LKF 001TR | A | 27 |  |  | 50 | MTAL | 3 |  |  |  | K1LKFA0001 |  |  |  |  | K1LKF | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKG | C9 | A |  | 1LGC 0803 | 1LKG 001TR | A | 312 |  |  | 50 | MTAL | 3 |  |  |  | K1LKGA0001 |  |  |  |  | K1LKG | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKH | C9 | A |  | 1LGC 0802 | 1LKH 001TR | A | 41 |  |  | 50 | MTAL | 3 |  |  |  | K1LKHA0001 |  |  |  |  | K1LKH | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKJ | C9 | A |  | 1LGC 0301 | 1LKJ 001TR | A | 129 |  |  | 50 | MTAL | 3 |  |  |  | K1LKJA0001 |  |  |  |  | K1LKJ | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LKS | C9 | A |  | 1LGC 0302 | 1LKS 001TR | A | 46 |  |  | 50 | MTAL | 3 |  |  |  | K1LKSA0001 |  |  |  |  | K1LKS | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | LLA | C3 | A |  | 1LHA 0603 | 1LLA 001TR | A | 13 |  |  | 50 | MTAL | 3 |  |  |  | K1LLAA0001 |  |  |  |  | K1LLA | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLB | C3 | A |  | 1LHB 0603 | 1LLB 001TR | B | 25 |  |  | 50 | MTAL | 3 |  |  |  | K1LLBA0001 |  |  |  |  | K1LLB | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLC | C3 | A |  | 1LHA 0602 | 1LLC 001TR | A | 26 |  |  | 50 | MTAL | 3 |  |  |  | K1LLCA0001 |  |  |  |  | K1LLC | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLD | C3 | A |  | 1LHB 0602 | 1LLD 001TR | B | 19 |  |  | 50 | MTAL | 3 |  |  |  | K1LLDA0001 |  |  |  |  | K1LLD | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLE | C3 | A |  | 1LHA 0503 | 1LLE 001TR | A | 47 |  |  | 50 | MTAL | 3 |  |  |  | K1LLEA0001 |  |  |  |  | K1LLE | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLI | C3 | A |  | 1LHA 0502 | 1LLI 001TR | A | 18 |  |  | 50 | MTAL | 3 |  |  |  | K1LLIA0001 |  |  |  |  | K1LLI | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | LLJ | C3 | A |  | 1LHB 0703 | 1LLJ 001TR | B | 31 |  |  | 50 | MTAL | 3 |  |  |  | K1LLJA0001 |  |  |  |  | K1LLJ | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RCP | C1 SPV | A |  | 1LGA 1101 | ABC | A | 46 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0001 |  |  |  |  | K1RCP | A0001 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGA 1101 | ABC | A | 48 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0002 |  |  |  |  | K1RCP | A0002 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGA 1101 | ABC | A | 46 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0003 |  |  |  |  | K1RCP | A0003 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0701 | ABC | A | 56 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0004 |  |  |  |  | K1RCP | A0004 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0701 | ABC | A | 57 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0005 |  |  |  |  | K1RCP | A0005 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0701 | ABC | A | 56 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0006 |  |  |  |  | K1RCP | A0006 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0801 | ABC | A | 66 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0007 |  |  |  |  | K1RCP | A0007 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0801 | ABC | A | 61 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0008 |  |  |  |  | K1RCP | A0008 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | 1LGD 0801 | ABC | A | 61 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0009 |  |  |  |  | K1RCP | A0009 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 001PO | A | 41 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0011 |  |  |  |  | K1RCP | A0011 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 001PO | A | 48 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0012 |  |  |  |  | K1RCP | A0012 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 001PO | A | 43 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0013 |  |  |  |  | K1RCP | A0013 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 002PO | A | 41 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0014 |  |  |  |  | K1RCP | A0014 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 002PO | A | 41 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0015 |  |  |  |  | K1RCP | A0015 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 002PO | A | 41 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0016 |  |  |  |  | K1RCP | A0016 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 003PO | A | 82 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0017 |  |  |  |  | K1RCP | A0017 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 003PO | A | 80 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0018 |  |  |  |  | K1RCP | A0018 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCP | C1 SPV | A |  | ABC | 1RCP 003PO | A | 75 |  |  | 500 | MTAL | 1 |  |  |  | K1RCPA0019 |  |  |  |  | K1RCP | A0019 | VLF-TD | 4RO | 125 | PD | 4 Yearly | 2018 | Visual & Tactile Inspections | 4RO | 124
1 | RCV | C3 | A |  | 1LHA 0202 | 1RCV 001PO | A | 102 |  |  | 50 | MTAL | 3 |  |  |  | K1RCVA0001 |  |  |  |  | K1RCV | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RCV | C3 | A |  | 1LHB 0302 | 1RCV 002PO | B | 75 |  |  | 50 | MTAL | 3 |  |  |  | K1RCVA0002 |  |  |  |  | K1RCV | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RCV | C3 | A |  | 1LHA 0302 | 1RCV 003PO | A | 108 |  |  | 50 | MTAL | 3 |  |  |  | K1RCVA0003 |  |  |  |  | K1RCV | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RIS | C3 | A |  | 1LHA 0301 | 1RIS 001PO | A | 220 |  |  | 50 | MTAL | 3 |  |  |  | K1RISA0001 |  |  |  |  | K1RIS | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RIS | C3 | A |  | 1LHB 0301 | 1RIS 002PO | B | 138 |  |  | 50 | MTAL | 3 |  |  |  | K1RISA0002 |  |  |  |  | K1RIS | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RRA | C3 | A |  | 1LHA 0501 | ABC | A | 33 |  |  | 50 | MTAL | 3 |  |  |  | K1RRAA0001 |  |  |  |  | K1RRA | A0001 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RRA | C3 | A |  | 1LHB 0601 | ABC | B | 41 |  |  | 50 | MTAL | 3 |  |  |  | K1RRAA0002 |  |  |  |  | K1RRA | A0002 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RRA | C3 | A |  | ABC | 1RRA 001MO | A | 79 |  |  | 50 | ADR | 3 |  |  |  | K1RRAA0003 |  |  |  |  | K1RRA | A0003 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RRA | C3 | A |  | ABC | 1RRA 002MO | B | 106 |  |  | 50 | ADR | 3 |  |  |  | K1RRAA0004 |  |  |  |  | K1RRA | A0004 | VLF-TD | 4RO | 127 | PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4RO | 126
1 | RRI | C9 | A |  | 1LHA 0903 | 1RRI 001PO | A | 150 |  |  | 50 | MTAL | 3 |  |  |  | K1RRIA0001 |  |  |  |  | K1RRI | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | RRI | C9 | A |  | 1LHB 0903 | 1RRI 002PO | B | 108 |  |  | 50 | MTAL | 3 |  |  |  | K1RRIA0002 |  |  |  |  | K1RRI | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | RRI | C9 | A |  | 1LHA 1003 | 1RRI 003PO | A | 152 |  |  | 50 | MTAL | 3 |  |  |  | K1RRIA0003 |  |  |  |  | K1RRI | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | RRI | C9 | A |  | 1LHB 1003 | 1RRI 004PO | B | 108 |  |  | 50 | MTAL | 3 |  |  |  | K1RRIA0004 |  |  |  |  | K1RRI | A0004 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | SAP | S | A |  | 1LGC 0801 | 1SAP 001CO | A | 128 |  |  | 50 | MTAL | 3 |  |  |  | K1SAPA0001 |  |  |  |  | K1SAP | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | SEC | C6 | A |  | 1LHA 0902 | 1SEC 001PO | A | 284 |  |  | 50 | MTAL | 3 |  |  |  | K1SECA0001 |  |  |  |  | K1SEC | A0001 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | SEC | C6 | A |  | 1LHB 0902 | 1SEC 002PO | B | 254 |  |  | 50 | MTAL | 3 |  |  |  | K1SECA0002 |  |  |  |  | K1SEC | A0002 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | SEC | C6 | A |  | 1LHA 1002 | 1SEC 003PO | A | 279 |  |  | 50 | MTAL | 3 |  |  |  | K1SECA0003 |  |  |  |  | K1SEC | A0003 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
1 | SEC | C6 | A |  | 1LHB 1002 | 1SEC 004PO | B | 248 |  |  | 50 | MTAL | 3 |  |  |  | K1SECA0004 |  |  |  |  | K1SEC | A0004 | VLF-TD | 4RO | 129 | PD | 4 Yearly | 2020 | Visual & Tactile Inspections | 4RO | 128
9 | CTE | S | A | 1 | 9LGE 0601 | 9CTE 101AR |  | 417 | 385 |  | 240 | MTAL | 3 |  |  |  | K9CTEA0001 |  |  |  |  | K9CTE | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | CTE | S | A | 2 | 9CTE 102AR | 9CTE 001TR |  | 12 | 17 |  | 240 | MTAL | 3 |  |  |  | K9CTEA0002 |  |  |  |  | K9CTE | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | CTE | S | A | 3 | 9LGF 0601 | 9CTE 201AR |  | 430 | 392 |  | 240 | MTAL | 3 |  |  |  | K9CTEA0003 |  |  |  |  | K9CTE | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | CTE | S | A | 4 | 9CTE 202AR | 9CTE 002TR |  | 13 | 17 |  | 240 | MTAL | 3 |  |  |  | K9CTEA0004 |  |  |  |  | K9CTE | A0004 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 1 | 9LGR 001TA | 9LGE 0401 |  | 20 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0001 |  |  |  |  | K9LGE | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 2 | 9LGR 001TA | 9LGE 0401 |  | 0 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0002 |  |  |  |  | K9LGE | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 3 | 9LGR 001TA | 9LGE 0401 |  | 0 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0003 |  |  |  |  | K9LGE | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 4 | 9LGR 001TA | 9LGE 0401 |  | 20 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0004 |  |  |  |  | K9LGE | A0004 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 5 | 9LGR 001TA | 9LGE 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0005 |  |  |  |  | K9LGE | A0005 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 6 | 9LGR 001TA | 9LGE 0401 |  | 0 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0006 |  |  |  |  | K9LGE | A0006 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 7 | 9LGR 001TA | 9LGE 0401 |  | 20 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0007 |  |  |  |  | K9LGE | A0007 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 8 | 9LGR 001TA | 9LGE 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0008 |  |  |  |  | K9LGE | A0008 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 9 | 9LGR 001TA | 9LGE 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0009 |  |  |  |  | K9LGE | A0009 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 10 | 9LGR 001TA | 9LGE 0401 |  | 20 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0010 |  |  |  |  | K9LGE | A0010 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 11 | 9LGR 001TA | 9LGE 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0011 |  |  |  |  | K9LGE | A0011 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 12 | 9LGR 001TA | 9LGE 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGEA0012 |  |  |  |  | K9LGE | A0012 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 13 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0013 |  |  |  |  | K9LGE | A0013 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 14 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0014 |  |  |  |  | K9LGE | A0014 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 15 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0015 |  |  |  |  | K9LGE | A0015 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 16 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0016 |  |  |  |  | K9LGE | A0016 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 17 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0017 |  |  |  |  | K9LGE | A0017 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 18 | 9LGE 0501 | 9LGF 0501 |  | 6 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0018 |  |  |  |  | K9LGE | A0018 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 19 | 9LGE 0501 | 9LGF 0501 |  | 7 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0019 |  |  |  |  | K9LGE | A0019 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 20 | 9LGE 0501 | 9LGF 0501 |  | 7 | 12 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0020 |  |  |  |  | K9LGE | A0020 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 21 | 9LGE 0501 | 9LGF 0501 |  | 7 | 11 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0021 |  |  |  |  | K9LGE | A0021 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 22 | 9LGR 001TA | 9LGE 001TR |  | 23 | 22 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0022 |  |  |  |  | K9LGE | A0022 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 23 | 9LGR 001TA | 9LGE 001TR |  | 23 | 22 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0023 |  |  |  |  | K9LGE | A0023 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 24 | 9LGR 001TA | 9LGE 001TR |  | 23 | 22 |  | 400 | MTAL | 1 |  |  |  | K9LGEA0024 |  |  |  |  | K9LGE | A0024 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 25 | 9LGE 001TR | 9LGE 001AR |  | 20 | 7 |  | 50 | MTAL | 3 |  |  |  | K9LGEA0025 |  |  |  |  | K9LGE | A0025 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGE | C3 | A | 26 | 9LGE 001AR | 9LGE TT8 |  | 20 | 10 |  | 50 | MTAL | 3 |  |  |  | K9LGEA0026 |  |  |  |  | K9LGE | A0026 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 1 | 9LGR 002TA | 9LGF 0401 |  | 20 | 12 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0001 |  |  |  |  | K9LGF | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 2 | 9LGR 002TA | 9LGF 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0002 |  |  |  |  | K9LGF | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 3 | 9LGR 002TA | 9LGF 0401 |  | 0 | 13 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0003 |  |  |  |  | K9LGF | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 4 | 9LGR 002TA | 9LGF 0401 |  | 20 | 16 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0004 |  |  |  |  | K9LGF | A0004 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 5 | 9LGR 002TA | 9LGF 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0005 |  |  |  |  | K9LGF | A0005 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 6 | 9LGR 002TA | 9LGF 0401 |  | 0 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0006 |  |  |  |  | K9LGF | A0006 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 7 | 9LGR 002TA | 9LGF 0401 |  | 20 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0007 |  |  |  |  | K9LGF | A0007 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 8 | 9LGR 002TA | 9LGF 0401 |  | 0 | 16 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0008 |  |  |  |  | K9LGF | A0008 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 9 | 9LGR 002TA | 9LGF 0401 |  | 0 | 16 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0009 |  |  |  |  | K9LGF | A0009 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 10 | 9LGR 002TA | 9LGF 0401 |  | 20 | 14 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0010 |  |  |  |  | K9LGF | A0010 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 11 | 9LGR 002TA | 9LGF 0401 |  | 0 | 5 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0011 |  |  |  |  | K9LGF | A0011 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 12 | 9LGR 002TA | 9LGF 0401 |  | 0 | 15 |  | 500 | MTAL | 1 |  |  |  | K9LGFA0012 |  |  |  |  | K9LGF | A0012 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 13 | 9LGR 002TA | 9LGF 001TR |  | 21 | 21 |  | 400 | MTAL | 1 |  |  |  | K9LGFA0013 |  |  |  |  | K9LGF | A0013 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 14 | 9LGR 002TA | 9LGF 001TR |  | 21 | 21 |  | 400 | MTAL | 1 |  |  |  | K9LGFA0014 |  |  |  |  | K9LGF | A0014 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 15 | 9LGR 002TA | 9LGF 001TR |  | 21 | 23 |  | 400 | MTAL | 1 |  |  |  | K9LGFA0015 |  |  |  |  | K9LGF | A0015 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 16 | 9LGF 001TR | 9LGF 001AR |  | 20 | 5 |  | 50 | MTAL | 3 |  |  |  | K9LGFA0016 |  |  |  |  | K9LGF | A0016 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGF | C3 | A | 17 | 9LGF 001AR | 9LGF TT9 |  | 20 | 9 |  | 50 | MTAL | 3 |  |  |  | K9LGFA0017 |  |  |  |  | K9LGF | A0017 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 1 | 1LGC 0201 | 9LGI 0101 |  | 75 | 77 |  | 240 | MTAL | 3 |  |  |  | K9LGIA0001 |  |  |  |  | K9LGI | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 2 | 2LGC 0201 | 9LGI 0501 |  | 55 | 62 |  | 240 | MTAL | 3 |  |  |  | K9LGIA0002 |  |  |  |  | K9LGI | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 3 | 1LGC 0201 | 9LGI 0101 |  | 77 | 81 |  | 240 | MTAL | 3 |  |  |  | K9LGIA0003 |  |  |  |  | K9LGI | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 4 | 2LGC 0201 | 9LGI 0501 |  | 71 | 69 |  | 240 | MTAL | 3 |  |  |  | K9LGIA0004 |  |  |  |  | K9LGI | A0004 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 5 | 9LGI 0301 | 9LHC 0801 |  | 28 | 33 |  | 400 | MTAL | 1 |  |  |  | K9LGIA0005 |  |  |  |  | K9LGI | A0005 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 6 | 9LGI 0301 | 9LHC 0801 |  | 28 | 32 |  | 400 | MTAL | 1 |  |  |  | K9LGIA0006 |  |  |  |  | K9LGI | A0006 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LGI | C3 | A | 7 | 9LGI 0301 | 9LHC 0801 |  | 28 | 32 |  | 400 | MTAL | 1 |  |  |  | K9LGIA0007 |  |  |  |  | K9LGI | A0007 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHC | C3 | A | 1 | 9LHS 001AR | 9LHC 0501 |  | 156 | 159 |  | 400 | MTAL | 1 |  |  |  | K9LHCA0001 |  |  |  |  | K9LHC | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHC | C3 | A | 2 | 9LHS 001AR | 9LHC 0501 |  | 156 | 167 |  | 400 | MTAL | 1 |  |  |  | K9LHCA0002 |  |  |  |  | K9LHC | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHC | C3 | A | 3 | 9LHS 001AR | 9LHC 0501 |  | 156 | 143 |  | 400 | MTAL | 1 |  |  |  | K9LHCA0003 |  |  |  |  | K9LHC | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHS | C3 | A | 1 | 9LHS 001GA | 9LHS 001AR |  | 11 | 15 |  | 400 | MTAL | 1 |  |  |  | K9LHSA0001 |  |  |  |  | K9LHS | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHS | C3 | A | 2 | 9LHS 001GA | 9LHS 001AR |  | 11 | 15 |  | 400 | MTAL | 1 |  |  |  | K9LHSA0002 |  |  |  |  | K9LHS | A0002 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LHS | C3 | A | 3 | 9LHS 001GA | 9LHS 001AR |  | 11 | 20 |  | 400 | MTAL | 1 |  |  |  | K9LHSA0003 |  |  |  |  | K9LHS | A0003 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKI | C3 | A | 1 | 9LGI 0203 | 9LKI 001TR |  | 99 | 94 |  | 50 | MTAL | 3 |  |  |  | K9LKIA0001 |  |  |  |  | K9LKI | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKK | C3 | A | 1 | 9LGI 0201 | 9LKK 001TR |  | 14 | 20 |  | 50 | MTAL | 3 |  |  |  | K9LKKA0001 |  |  |  |  | K9LKK | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKM | C3 | A | 1 | 9LGI 0402 | 9LKM 001TR |  | 342 | 255 |  | 50 | MTAL | 3 |  |  |  | K9LKMA0001 |  |  |  |  | K9LKM | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKN | C3 | A | 1 | 9LGI 0202 | 9LKN 001TR |  | 253 | 258 |  | 50 | MTAL | 3 |  |  |  | K9LKNA0001 |  |  |  |  | K9LKN | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKP | C3 | A | 1 | 9LGI 0401 | 9LKP 001TR |  | 482 | 393 |  | 50 | MTAL | 3 |  |  |  | K9LKPA0001 |  |  |  |  | K9LKP | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LKZ | S | A | 1 | 9LGI 0601 | 9LKZ 001TR |  | 88 | 104 |  | 50 | MTAL | 3 |  |  |  | K9LKZA0001 |  |  |  |  | K9LKZ | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
9 | LLZ | E | A | 1 | 9LHC 0602 | 9LLZ 001TR |  | 14 | 16 |  | 50 | MTAL | 3 |  |  |  | K9LLZA0001 |  |  |  |  | K9LLZ | A0001 | VLF-TD | 4 Yearly | 2019 | Online PD | 4 Yearly | 2019 | Visual & Tactile Inspections | 4 Yearly | 2018
2 | ACO | S | A | 1 | 2LGD 0301 | 2ACO 001PO | A | 77 | 80 | 80 | 240 | MTAL | 3 |  |  |  | K2ACOA0001 |  |  |  |  | K2ACO | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0301 | 2M1D1 64F | A | N
2 | ACO | S | A | 2 | 2LGD 0101 | 2ACO 002PO | A | 78 | 83 | 83 | 240 | MTAL | 3 |  |  |  | K2ACOA0002 |  |  |  |  | K2ACO | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0101 | 2M1D1 64F | A | N
2 | APA | S | A | 1 | 9LGF 0101 | 2APA 003PO | A | 334 | 246 | 346 | 400 | MTAL | 1 |  |  |  | K2APAA0001 |  |  |  |  | K2APA | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0101 | 2M1G1 72H | A | N
2 | APA | S | A | 2 | 9LGF 0101 | 2APA 003PO | A | 334 | 343 | 343 | 400 | MTAL | 1 |  |  |  | K2APAA0002 |  |  |  |  | K2APA | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0101 | 2M1G1 72H | A | N
2 | APA | S | A | 3 | 9LGF 0101 | 2APA 003PO | A | 334 | 346 | 346 | 400 | MTAL | 1 |  |  |  | K2APAA0003 |  |  |  |  | K2APA | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0101 | 2M1G1 72H | A | N
2 | ASG | C3 | A | 1 | 2LHA 0601 | 2ASG 001PO | A | 65 | 86 | 86 | 50 | MTAL | 3 |  |  |  | K2ASGA0001 |  |  |  |  | K2ASG | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0601 | W269 68Q | A | N
2 | ASG | C3 | A | 2 | 2LHB 0701 | 2ASG 002PO | B | 83 | 98 | 98 | 50 | MTAL | 3 |  |  |  | K2ASGA0002 |  |  |  |  | K2ASG | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0701 | W269 68Q | A | N
2 | ATE | S | A | 1 | 2LGD 0901 | 2ATE 901PO | A | 198 | 204 | 204 | 50 | MTAL | 3 |  |  |  | K2ATEA0001 |  |  |  |  | K2ATE | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0901 | 2Y0A 66BY | A | N
2 | ATE | S | A | 2 | 2LGD 0902 | 2ATE 902PO | A | 198 | 204 | 204 | 50 | MTAL | 3 |  |  |  | K2ATEA0002 |  |  |  |  | K2ATE | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0902 | 2Y0A 66BY | A | N
2 | ATE | S | A | 3 | 2LGD 0903 | 2ATE 903PO | A | 193 | 204 | 204 | 50 | MTAL | 3 |  |  |  | K2ATEA0003 |  |  |  |  | K2ATE | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0903 | 2Y0A 66BZ | A | N
2 | CEX | C9 | A | 1 | 2LGA 1001 | 2CEX 001PO | A | 82 | 81 | 81 | 240 | MTAL | 3 |  |  |  | K2CEXA0001 |  |  |  |  | K2CEX | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGA 1001 | 2M1D2 71F | A | N
2 | CEX | C9 | A | 2 | 2LGA 0701 | 2CEX 002PO | A | 84 | 82 | 82 | 240 | MTAL | 3 |  |  |  | K2CEXA0002 |  |  |  |  | K2CEX | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGA 0701 | 2M1D2 72F | A | N
2 | CEX | C9 | A | 3 | 2LGA 0501 | 2CEX 003PO | A | 93 | 93 | 93 | 240 | MTAL | 3 |  |  |  | K2CEXA0003 |  |  |  |  | K2CEX | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGA 0501 | 2M1D2 73F | A | N
2 | CRF | C2 SPV | A |  | 2LGA 0401 | 2CRF 001PO | A | 351 | 353 | 353 | 240 | MTAL | 3 |  |  |  | K2CRFA0001 |  |  |  |  | K2CRF | A0001 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0401 | 2C1A 39CZ | A | N
2 | CRF | C2 SPV | A |  | 2LGA 0201 | 2CRF 002PO | A | 335 | 337 | 337 | 240 | MTAL | 3 |  |  |  | K2CRFA0002 |  |  |  |  | K2CRF | A0002 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0201 | 2C1A 42CZ | A | N
2 | CRF | C2 SPV | A |  | 2LGA 0101 | 2CRF 003PO | A | 328 | 348 | 348 | 240 | MTAL | 3 |  |  |  | K2CRFA0003 |  |  |  |  | K2CRF | A0003 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0101 | 2C1A 44CZ | A | N
2 | DEG | E | A | 1 | 2LHB 0901 | 2DEG 101CO | B | 138 | 175 | 175 | 50 | MTAL | 3 |  |  |  | K2DEGA0001 |  |  |  |  | K2DEG | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0901 | W455 64CA | C | N
2 | DEG | E | A | 2 | 2LHA 0901 | 2DEG 201CO | A | 224 | 231 | 231 | 50 | MTAL | 3 |  |  |  | K2DEGA0002 |  |  |  |  | K2DEG | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0901 | W555 64CA | C | N
2 | DEG | E | A | 3 | 2LHB 1001 | 2DEG 301CO | B | 139 | 176 | 176 | 50 | MTAL | 3 |  |  |  | K2DEGA0003 |  |  |  |  | K2DEG | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 1001 | W455 64Z | C | N
2 | DEG | E | A | 4 | 2LHA 1001 | 2DEG 401CO | A | 230 | 253 | 253 | 50 | MTAL | 3 |  |  |  | K2DEGA0004 |  |  |  |  | K2DEG | A0004 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 1001 | W555 64Z | C | N
2 | EAS | C3 | A | 1 | 2LHA 0201 | 2EAS 001PO | A | 235 | 246 | 246 | 50 | MTAL | 3 |  |  |  | K2EASA0001 |  |  |  |  | K2EAS | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0201 | K150 71CA | B | N
2 | EAS | C3 | A | 2 | 2LHB 0201 | 2EAS 002PO | B | 165 | 183 | 183 | 50 | MTAL | 3 |  |  |  | K2EASA0002 |  |  |  |  | K2EAS | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0201 | K151 69CA | B | N
2 | GGR | S | A | 1 | 2LGB 0101 | 2GGR 001TR | A | 97 | 103 | 103 | 240 | MTAL | 3 |  |  |  | K2GGRA0001 |  |  |  |  | K2GGR | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0101 | 2M2D2 72D | A | N
2 | LGA | C1 SPV | A | 1 | 2GEV 001TS | 2LGA 0801 | A | 148 | 152 | 152 | 500 | MTAL | 1 |  |  |  | K2LGAA0001 |  |  |  |  | K2LGA | A0001 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 2 | 2GEV 001TS | 2LGA 0801 | A | 148 | 155 | 155 | 500 | MTAL | 1 |  |  |  | K2LGAA0002 |  |  |  |  | K2LGA | A0002 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 3 | 2GEV 001TS | 2LGA 0801 | A | 148 | 154 | 154 | 500 | MTAL | 1 |  |  |  | K2LGAA0003 |  |  |  |  | K2LGA | A0003 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 4 | 2GEV 001TS | 2LGA 0801 | A | 148 | 155 | 155 | 500 | MTAL | 1 |  |  |  | K2LGAA0004 |  |  |  |  | K2LGA | A0004 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 5 | 2GEV 001TS | 2LGA 0801 | A | 148 | 154 | 154 | 500 | MTAL | 1 |  |  |  | K2LGAA0005 |  |  |  |  | K2LGA | A0005 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 6 | 2GEV 001TS | 2LGA 0801 | A | 148 | 156 | 156 | 500 | MTAL | 1 |  |  |  | K2LGAA0006 |  |  |  |  | K2LGA | A0006 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 7 | 2GEV 001TS | 2LGA 0801 | A | 145 | 155 | 155 | 500 | MTAL | 1 |  |  |  | K2LGAA0007 |  |  |  |  | K2LGA | A0007 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 8 | 2GEV 001TS | 2LGA 0801 | A | 145 | 155 | 155 | 500 | MTAL | 1 |  |  |  | K2LGAA0008 |  |  |  |  | K2LGA | A0008 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 9 | 2GEV 001TS | 2LGA 0801 | A | 145 | 155 | 155 | 500 | MTAL | 1 |  |  |  | K2LGAA0009 |  |  |  |  | K2LGA | A0009 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 10 | 2GEV 001TS | 2LGA 0801 | A | 145 | 149 | 149 | 500 | MTAL | 1 |  |  |  | K2LGAA0010 |  |  |  |  | K2LGA | A0010 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 11 | 2GEV 001TS | 2LGA 0801 | A | 145 | 156 | 156 | 500 | MTAL | 1 |  |  |  | K2LGAA0011 |  |  |  |  | K2LGA | A0011 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 12 | 2GEV 001TS | 2LGA 0801 | A | 145 | 156 | 156 | 500 | MTAL | 1 |  |  |  | K2LGAA0012 |  |  |  |  | K2LGA | A0012 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 0801 | D | N
2 | LGA | C1 SPV | A | 13 | 2LGA 0601 | 2LGB 0301 | A | 28 | 32 | 32 | 500 | MTAL | 1 |  |  |  | K2LGAA0013 |  |  |  |  | K2LGA | A0013 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0601 | 2LGB 0301 | B | N
2 | LGA | C1 SPV | A | 14 | 2LGA 0601 | 2LGB 0301 | A | 28 | 36 | 36 | 500 | MTAL | 1 |  |  |  | K2LGAA0014 |  |  |  |  | K2LGA | A0014 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0601 | 2LGB 0301 | B | N
2 | LGA | C1 SPV | A | 15 | 2LGA 0601 | 2LGB 0301 | A | 28 | 33 | 33 | 500 | MTAL | 1 |  |  |  | K2LGAA0015 |  |  |  |  | K2LGA | A0015 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 0601 | 2LGB 0301 | B | N
2 | LGA | C1 SPV | A | 16 | 2GEV 001TS | 2LGA 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGAA0016 |  |  |  |  | K2LGA | A0016 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 001TR | E | N
2 | LGA | C1 SPV | A | 17 | 2GEV 001TS | 2LGA 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGAA0017 |  |  |  |  | K2LGA | A0017 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 001TR | E | N
2 | LGA | C1 SPV | A | 18 | 2GEV 001TS | 2LGA 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGAA0018 |  |  |  |  | K2LGA | A0018 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGA 001TR | E | N
2 | LGA | C1 SPV | A | 19 | 2LGA 001TR | 2LGA 001AR | A | 20 | 10 | 14 | 25 | MTCU | 1 |  |  |  | K2LGAA0019 |  |  |  |  | K2LGA | A0019 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 001TR | 2LGA 001AR | D | N
2 | LGA | C1 SPV | A | 20 | 2LGA 001AR | 2LGA TT19 | A | 20 | 12 | 12 | 25 | MTCU | 1 |  |  |  | K2LGAA0020 |  |  |  |  | K2LGA | A0020 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 001AR | 2T2X 73BZ | F | N
2 | LGB | C3 | A | 1 | 9LGF 0201 | 2LGB 0401 | A | 302 | 301 | 302 | 500 | MTAL | 1 |  |  |  | K2LGBA0001 |  |  |  |  | K2LGB | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGB | C3 | A | 2 | 9LGF 0201 | 2LGB 0401 | A | 302 | 302 | 302 | 500 | MTAL | 1 |  |  |  | K2LGBA0002 |  |  |  |  | K2LGB | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGB | C3 | A | 3 | 9LGF 0201 | 2LGB 0401 | A | 302 | 302 | 302 | 500 | MTAL | 1 |  |  |  | K2LGBA0003 |  |  |  |  | K2LGB | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGB | C3 | A | 4 | 9LGF 0201 | 2LGB 0401 | A | 302 | 302 | 302 | 500 | MTAL | 1 |  |  |  | K2LGBA0004 |  |  |  |  | K2LGB | A0004 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGB | C3 | A | 5 | 9LGF 0201 | 2LGB 0401 | A | 302 | 301 | 301 | 500 | MTAL | 1 |  |  |  | K2LGBA0005 |  |  |  |  | K2LGB | A0005 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGB | C3 | A | 6 | 9LGF 0201 | 2LGB 0401 | A | 302 | 300 | 300 | 500 | MTAL | 1 |  |  |  | K2LGBA0006 |  |  |  |  | K2LGB | A0006 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGF 0201 | 2LGB 0401 | B | N
2 | LGC | C3 | A | 4 | 9LGE 0301 | 2LGC 0601 | A | 293 | 293 | 293 | 400 | MTAL | 1 |  |  |  | K2LGCA0004 |  |  |  |  | K2LGC | A0004 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGC | C3 | A | 5 | 9LGE 0301 | 2LGC 0601 | A | 293 | 293 | 293 | 400 | MTAL | 1 |  |  |  | K2LGCA0005 |  |  |  |  | K2LGC | A0005 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGC | C3 | A | 6 | 9LGE 0301 | 2LGC 0601 | A | 293 | 293 | 293 | 400 | MTAL | 1 |  |  |  | K2LGCA0006 |  |  |  |  | K2LGC | A0006 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGC | C3 | A | 7 | 9LGE 0301 | 2LGC 0601 | A | 293 | 293 | 293 | 400 | MTAL | 1 |  |  |  | K2LGCA0007 |  |  |  |  | K2LGC | A0007 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGC | C3 | A | 8 | 9LGE 0301 | 2LGC 0601 | A | 293 | 293 | 293 | 400 | MTAL | 1 |  |  |  | K2LGCA0008 |  |  |  |  | K2LGC | A0008 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGC | C3 | A | 9 | 9LGE 0301 | 2LGC 0601 | A | 293 | 291 | 291 | 400 | MTAL | 1 |  |  |  | K2LGCA0009 |  |  |  |  | K2LGC | A0009 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LGE 0301 | 2LGC 0601 | B | N
2 | LGD | C1 SPV | A | 1 | 2GEV 001TS | 2LGD 0501 | A | 164 | 170 | 170 | 500 | MTAL | 1 |  |  |  | K2LGDA0001 |  |  |  |  | K2LGD | A0001 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 2 | 2GEV 001TS | 2LGD 0501 | A | 164 | 176 | 176 | 500 | MTAL | 1 |  |  |  | K2LGDA0002 |  |  |  |  | K2LGD | A0002 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 3 | 2GEV 001TS | 2LGD 0501 | A | 164 | 174 | 174 | 500 | MTAL | 1 |  |  |  | K2LGDA0003 |  |  |  |  | K2LGD | A0003 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 4 | 2GEV 001TS | 2LGD 0501 | A | 164 | 173 | 173 | 500 | MTAL | 1 |  |  |  | K2LGDA0004 |  |  |  |  | K2LGD | A0004 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 5 | 2GEV 001TS | 2LGD 0501 | A | 164 | 173 | 173 | 500 | MTAL | 1 |  |  |  | K2LGDA0005 |  |  |  |  | K2LGD | A0005 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 6 | 2GEV 001TS | 2LGD 0501 | A | 164 | 180 | 180 | 500 | MTAL | 1 |  |  |  | K2LGDA0006 |  |  |  |  | K2LGD | A0006 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 7 | 2GEV 001TS | 2LGD 0501 | A | 163 | 171 | 171 | 500 | MTAL | 1 |  |  |  | K2LGDA0007 |  |  |  |  | K2LGD | A0007 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 8 | 2GEV 001TS | 2LGD 0501 | A | 163 | 178 | 178 | 500 | MTAL | 1 |  |  |  | K2LGDA0008 |  |  |  |  | K2LGD | A0008 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 9 | 2GEV 001TS | 2LGD 0501 | A | 163 | 174 | 174 | 500 | MTAL | 1 |  |  |  | K2LGDA0009 |  |  |  |  | K2LGD | A0009 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 10 | 2GEV 001TS | 2LGD 0501 | A | 163 | 176 | 176 | 500 | MTAL | 1 |  |  |  | K2LGDA0010 |  |  |  |  | K2LGD | A0010 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 11 | 2GEV 001TS | 2LGD 0501 | A | 163 | 177 | 177 | 500 | MTAL | 1 |  |  |  | K2LGDA0011 |  |  |  |  | K2LGD | A0011 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 12 | 2GEV 001TS | 2LGD 0501 | A | 163 | 178 | 178 | 500 | MTAL | 1 |  |  |  | K2LGDA0012 |  |  |  |  | K2LGD | A0012 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 0501 | D | N
2 | LGD | C1 SPV | A | 13 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0013 |  |  |  |  | K2LGD | A0013 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 14 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0014 |  |  |  |  | K2LGD | A0014 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 15 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0015 |  |  |  |  | K2LGD | A0015 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 16 | 2LGD 0401 | 2LGC 0701 | A | 40 | 44 | 44 | 400 | MTAL | 1 |  |  |  | K2LGDA0016 |  |  |  |  | K2LGD | A0016 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 17 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0017 |  |  |  |  | K2LGD | A0017 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 18 | 2LGD 0401 | 2LGC 0701 | A | 40 | 44 | 44 | 400 | MTAL | 1 |  |  |  | K2LGDA0018 |  |  |  |  | K2LGD | A0018 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | B | N
2 | LGD | C1 SPV | A | 19 | 2GEV 001TS | 2LGD 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGDA0019 |  |  |  |  | K2LGD | A0019 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 001TR | E | N
2 | LGD | C1 SPV | A | 20 | 2GEV 001TS | 2LGD 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGDA0020 |  |  |  |  | K2LGD | A0020 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 001TR | E | N
2 | LGD | C1 SPV | A | 21 | 2GEV 001TS | 2LGD 001TR | A | 8 | 17 | 17 | 400 | MTAL | 1 |  |  |  | K2LGDA0021 |  |  |  |  | K2LGD | A0021 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2GEV 001TS | 2LGD 001TR | E | N
2 | LGD | C1 SPV | A | 22 | 2LGD 001TR | 2LGD 001AR | A | 20 | 10 | 10 | 25 | MTCU | 1 |  |  |  | K2LGDA0022 |  |  |  |  | K2LGD | A0022 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 001TR | 2LGD 001AR | D | N
2 | LGD | C1 SPV | A | 23 | 2LGD 001AR | 2LGA TT19 | A | 20 | 11 | 11 | 25 | MTCU | 1 |  |  |  | K2LGDA0023 |  |  |  |  | K2LGD | A0023 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 001AR | 2T2X 73BZ | I | N
2 | LGD | C1 SPV | A | 25 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0025 |  |  |  |  | K2LGD | A0025 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | H | N
2 | LGD | C1 SPV | A | 26 | 2LGD 0401 | 2LGC 0701 | A | 40 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LGDA0026 |  |  |  |  | K2LGD | A0026 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | H | N
2 | LGD | C1 SPV | A | 27 | 2LGD 0401 | 2LGC 0701 | A | 40 | 44 | 44 | 400 | MTAL | 1 |  |  |  | K2LGDA0027 |  |  |  |  | K2LGD | A0027 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0401 | 2LGC 0701 | H | N
2 | LHA | C3 | A | 1 | 2LHP 001AR | 2LHA 0401 | A | 33 | 35 | 33 | 400 | MTAL | 1 |  |  |  | K2LHAA0001 |  |  |  |  | K2LHA | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001AR | 2LHA 0401 | B | N
2 | LHA | C3 | A | 2 | 2LHP 001AR | 2LHA 0401 | A | 33 | 43 | 43 | 400 | MTAL | 1 |  |  |  | K2LHAA0002 |  |  |  |  | K2LHA | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001AR | 2LHA 0401 | B | N
2 | LHA | C3 | A | 3 | 2LHP 001AR | 2LHA 0401 | A | 33 | 44 | 44 | 400 | MTAL | 1 |  |  |  | K2LHAA0003 |  |  |  |  | K2LHA | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001AR | 2LHA 0401 | B | N
2 | LHA | C3 | A | 4 | 2LGB 0601 | 2LHA 0101 | A | 21 | 27 | 27 | 400 | MTAL | 1 |  |  |  | K2LHAA0004 |  |  |  |  | K2LHA | A0004 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0601 | 2LHA 0101 | B | N
2 | LHA | C3 | A | 5 | 2LGB 0601 | 2LHA 0101 | A | 21 | 27 | 27 | 400 | MTAL | 1 |  |  |  | K2LHAA0005 |  |  |  |  | K2LHA | A0005 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0601 | 2LHA 0101 | B | N
2 | LHA | C3 | A | 6 | 2LGB 0601 | 2LHA 0101 | A | 21 | 29 | 29 | 400 | MTAL | 1 |  |  |  | K2LHAA0006 |  |  |  |  | K2LHA | A0006 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0601 | 2LHA 0101 | B | N
2 | LHA | C3 | A | 7 | 9LHC 0301 | 2LHA 0701 | A | 85 | 92 | 92 | 400 | MTAL | 1 |  |  |  | K2LHAA0007 |  |  |  |  | K2LHA | A0007 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0301 | 2LHA 0701 | B | N
2 | LHA | C3 | A | 8 | 9LHC 0301 | 2LHA 0701 | A | 85 | 100 | 100 | 400 | MTAL | 1 |  |  |  | K2LHAA0008 |  |  |  |  | K2LHA | A0008 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0301 | 2LHA 0701 | B | N
2 | LHA | C3 | A | 9 | 9LHC 0301 | 2LHA 0701 | A | 85 | 100 | 100 | 400 | MTAL | 1 |  |  |  | K2LHAA0009 |  |  |  |  | K2LHA | A0009 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0301 | 2LHA 0701 | B | N
2 | LHB | C3 | A | 1 | 2LHQ 001AR | 2LHB 0401 | B | 170 | 172 | 172 | 400 | MTAL | 1 |  |  |  | K2LHBA0001 |  |  |  |  | K2LHB | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001AR | 2LHB 0401 | B | N
2 | LHB | C3 | A | 2 | 2LHQ 001AR | 2LHB 0401 | B | 170 | 172 | 172 | 400 | MTAL | 1 |  |  |  | K2LHBA0002 |  |  |  |  | K2LHB | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001AR | 2LHB 0401 | B | N
2 | LHB | C3 | A | 3 | 2LHQ 001AR | 2LHB 0401 | B | 170 | 172 | 172 | 400 | MTAL | 1 |  |  |  | K2LHBA0003 |  |  |  |  | K2LHB | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001AR | 2LHB 0401 | B | N
2 | LHB | C3 | A | 4 | 2LGC 0401 | 2LHB 0101 | B | 34 | 40 | 40 | 400 | MTAL | 1 |  |  |  | K2LHBA0004 |  |  |  |  | K2LHB | A0004 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0401 | 2LHB 0101 | B | N
2 | LHB | C3 | A | 5 | 2LGC 0401 | 2LHB 0101 | B | 34 | 40 | 40 | 400 | MTAL | 1 |  |  |  | K2LHBA0005 |  |  |  |  | K2LHB | A0005 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0401 | 2LHB 0101 | B | N
2 | LHB | C3 | A | 6 | 2LGC 0401 | 2LHB 0101 | B | 34 | 40 | 40 | 400 | MTAL | 1 |  |  |  | K2LHBA0006 |  |  |  |  | K2LHB | A0006 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0401 | 2LHB 0101 | B | N
2 | LHB | C3 | A | 7 | 9LHC 0701 | 2LHB 0801 | B | 19 | 37 | 37 | 400 | MTAL | 1 |  |  |  | K2LHBA0007 |  |  |  |  | K2LHB | A0007 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0701 | 2LHB 0801 | B | N
2 | LHB | C3 | A | 8 | 9LHC 0701 | 2LHB 0801 | B | 19 | 38 | 38 | 400 | MTAL | 1 |  |  |  | K2LHBA0008 |  |  |  |  | K2LHB | A0008 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0701 | 2LHB 0801 | B | N
2 | LHB | C3 | A | 9 | 9LHC 0701 | 2LHB 0801 | B | 19 | 36 | 36 | 400 | MTAL | 1 |  |  |  | K2LHBA0009 |  |  |  |  | K2LHB | A0009 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 9LHC 0701 | 2LHB 0801 | B | N
2 | LHP | C3 | A | 1 | 2LHP 001GA | 2LHP 001AR | A | 12 | 15 | 15 | 400 | MTAL | 1 |  |  |  | K2LHPA0001 |  |  |  |  | K2LHP | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001GA | 2LHP 001AR | A | N
2 | LHP | C3 | A | 2 | 2LHP 001GA | 2LHP 001AR | A | 12 | 15 | 15 | 400 | MTAL | 1 |  |  |  | K2LHPA0002 |  |  |  |  | K2LHP | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001GA | 2LHP 001AR | A | N
2 | LHP | C3 | A | 3 | 2LHP 001GA | 2LHP 001AR | A | 12 | 15 | 15 | 400 | MTAL | 1 |  |  |  | K2LHPA0003 |  |  |  |  | K2LHP | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHP 001GA | 2LHP 001AR | A | N
2 | LHQ | C3 | A | 1 | 2LHQ 001GA | 2LHQ 001AR | B | 14 | 14 | 14 | 400 | MTAL | 1 |  |  |  | K2LHQA0001 |  |  |  |  | K2LHQ | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001GA | 2LHQ 001AR | A | N
2 | LHQ | C3 | A | 2 | 2LHQ 001GA | 2LHQ 001AR | B | 14 | 13 | 13 | 400 | MTAL | 1 |  |  |  | K2LHQA0002 |  |  |  |  | K2LHQ | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001GA | 2LHQ 001AR | A | N
2 | LHQ | C3 | A | 3 | 2LHQ 001GA | 2LHQ 001AR | B | 14 | 13 | 13 | 400 | MTAL | 1 |  |  |  | K2LHQA0003 |  |  |  |  | K2LHQ | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHQ 001GA | 2LHQ 001AR | A | N
2 | LKA | C9 | A | 1 | 2LGA 0303 | 2LKA 001TR | A | 13 | 14 | 14 | 50 | MTAL | 3 |  |  |  | K2LKAA0001 |  |  |  |  | K2LKA | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGA 0303 | 2LKA 001TR | A | N
2 | LKB | C9 | A | 1 | 2LGD 0203 | 2LKB 001TR | A | 48 | 53 | 53 | 50 | MTAL | 3 |  |  |  | K2LKBA0001 |  |  |  |  | K2LKB | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0203 | 2LKB 001TR | B | N
2 | LKC | C9 | A | 1 | 2LGD 0202 | 2LKC 001TR | A | 22 | 24 | 24 | 50 | MTAL | 3 |  |  |  | K2LKCA0001 |  |  |  |  | K2LKC | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGD 0202 | 2LKC 001TR | A | N
2 | LKD | C9 | A | 1 | 2LGB 0203 | 2LKD 001TR | A | 14 | 19 | 19 | 50 | MTAL | 3 |  |  |  | K2LKDA0001 |  |  |  |  | K2LKD | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0203 | 2LKD 001TR | A | N
2 | LKE | C9 | A | 1 | 2LGB 0202 | 2LKE 001TR | A | 37 | 42 | 42 | 50 | MTAL | 3 |  |  |  | K2LKEA0001 |  |  |  |  | K2LKE | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGB 0202 | 2LKE 001TR | A | N
2 | LKG | C9 | A | 1 | 2LGC 0803 | 2LKG 001TR | A | 383 | 381 | 381 | 50 | MTAL | 3 |  |  |  | K2LKGA0001 |  |  |  |  | K2LKG | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0803 | 2LKG 001TR | B | N
2 | LKH | C9 | A | 1 | 2LGC 0802 | 2LKH 001TR | A | 44 | 53 | 53 | 50 | MTAL | 3 |  |  |  | K2LKHA0001 |  |  |  |  | K2LKH | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0802 | 2LKH 001TR | A | N
2 | LKJ | C9 | A | 1 | 2LGC 0301 | 2LKJ 001TR | A | 0 | 125 | 125 | 50 | MTAL | 3 |  |  |  | K2LKJA0001 |  |  |  |  | K2LKJ | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0301 | 2LKJ 001TR | A | N
2 | LKS | C9 | A | 1 | 2LGC 0302 | 2LKS 001TR | A | 46 | 52 | 52 | 50 | MTAL | 3 |  |  |  | K2LKSA0001 |  |  |  |  | K2LKS | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0302 | 2LKS 001TR | A | N
2 | LLA | C3 | A | 1 | 2LHA 0603 | 2LLA 001TR | A | 9 | 8 | 8 | 50 | MTAL | 3 |  |  |  | K2LLAA0001 |  |  |  |  | K2LLA | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0603 | 2LLA 001TR | A | N
2 | LLB | C3 | A | 1 | 2LHB 0603 | 2LLB 001TR | B | 30 | 29 | 29 | 50 | MTAL | 3 |  |  |  | K2LLBA0001 |  |  |  |  | K2LLB | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0603 | 2LLB 001TR | A | N
2 | LLC | C3 | A | 1 | 2LHA 0602 | 2LLC 001TR | A | 25 | 28 | 28 | 50 | MTAL | 3 |  |  |  | K2LLCA0001 |  |  |  |  | K2LLC | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0602 | 2LLC 001TR | A | N
2 | LLD | C3 | A | 1 | 2LHB 0602 | 2LLD 001TR | B | 16 | 15 | 21 | 50 | MTAL | 3 |  |  |  | K2LLDA0001 |  |  |  |  | K2LLD | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0602 | 2LLD 001TR | A | N
2 | LLE | C3 | A | 1 | 2LHA 0503 | 2LLE 001TR | A | 50 | 50 | 50 | 50 | MTAL | 3 |  |  |  | K2LLEA0001 |  |  |  |  | K2LLE | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0503 | 2LLE 001TR | A | N
2 | LLI | C3 | A | 1 | 2LHA 0502 | 2LLI 001TR | A | 9 | 13 | 13 | 50 | MTAL | 3 |  |  |  | K2LLIA0001 |  |  |  |  | K2LLI | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0502 | 2LLI 001TR | A | N
2 | LLJ | C3 | A | 1 | 2LHB 0703 | 2LLJ 001TR | B | 22 | 29 | 29 | 50 | MTAL | 3 |  |  |  | K2LLJA0001 |  |  |  |  | K2LLJ | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0703 | 2LLJ 001TR | A | N
2 | RCP | C1 SPV | A | 1 | 2LGA 1101 | ABC | A | 41 | 51 | 51 | 500 | MTAL | 1 |  |  |  | K2RCPA0001 |  |  |  |  | K2RCP | A0001 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 1101 | PN2L324 | A | N
2 | RCP | C1 SPV | A | 2 | 2LGA 1101 | ABC | A | 41 | 50 | 50 | 500 | MTAL | 1 |  |  |  | K2RCPA0002 |  |  |  |  | K2RCP | A0002 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 1101 | PN2L324 | A | N
2 | RCP | C1 SPV | A | 3 | 2LGA 1101 | ABC | A | 41 | 50 | 50 | 500 | MTAL | 1 |  |  |  | K2RCPA0003 |  |  |  |  | K2RCP | A0003 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGA 1101 | PN2L324 | A | N
2 | RCP | C1 SPV | A | 4 | 2LGD 0701 | ABC | A | 54 | 68 | 68 | 500 | MTAL | 1 |  |  |  | K2RCPA0004 |  |  |  |  | K2RCP | A0004 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0701 | PN2L326 | A | N
2 | RCP | C1 SPV | A | 5 | 2LGD 0701 | ABC | A | 54 | 68 | 68 | 500 | MTAL | 1 |  |  |  | K2RCPA0005 |  |  |  |  | K2RCP | A0005 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0701 | PN2L326 | A | N
2 | RCP | C1 SPV | A | 6 | 2LGD 0701 | ABC | A | 54 | 68 | 68 | 500 | MTAL | 1 |  |  |  | K2RCPA0006 |  |  |  |  | K2RCP | A0006 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0701 | PN2L326 | A | N
2 | RCP | C1 SPV | A | 7 | 2LGD 0801 | ABC | A | 53 | 67 | 67 | 500 | MTAL | 1 |  |  |  | K2RCPA0007 |  |  |  |  | K2RCP | A0007 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0801 | PN2L325 | A | N
2 | RCP | C1 SPV | A | 8 | 2LGD 0801 | ABC | A | 53 | 67 | 67 | 500 | MTAL | 1 |  |  |  | K2RCPA0008 |  |  |  |  | K2RCP | A0008 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0801 | PN2L325 | A | N
2 | RCP | C1 SPV | A | 9 | 2LGD 0801 | ABC | A | 53 | 67 | 67 | 500 | MTAL | 1 |  |  |  | K2RCPA0009 |  |  |  |  | K2RCP | A0009 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | 2LGD 0801 | PN2L325 | A | N
2 | RCP | C1 SPV | A | 11 | ABC | 2RCP 001PO | A | 82 | 91 | 91 | 500 | MTAL | 1 |  |  |  | K2RCPA0011 |  |  |  |  | K2RCP | A0011 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L324 | R551 66Y | A | N
2 | RCP | C1 SPV | A | 12 | ABC | 2RCP 001PO | A | 82 | 91 | 91 | 500 | MTAL | 1 |  |  |  | K2RCPA0012 |  |  |  |  | K2RCP | A0012 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L324 | R551 66Y | A | N
2 | RCP | C1 SPV | A | 13 | ABC | 2RCP 001PO | A | 82 | 89 | 89 | 500 | MTAL | 1 |  |  |  | K2RCPA0013 |  |  |  |  | K2RCP | A0013 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L324 | R551 66Y | A | N
2 | RCP | C1 SPV | A | 14 | ABC | 2RCP 002PO | A | 41 | 44 | 39 | 500 | MTAL | 1 |  |  |  | K2RCPA0014 |  |  |  |  | K2RCP | A0014 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L326 | R561 70V | A | N
2 | RCP | C1 SPV | A | 15 | ABC | 2RCP 002PO | A | 41 | 44 | 51 | 500 | MTAL | 1 |  |  |  | K2RCPA0015 |  |  |  |  | K2RCP | A0015 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L326 | R561 70V | A | N
2 | RCP | C1 SPV | A | 16 | ABC | 2RCP 002PO | A | 41 | 52 | 51 | 500 | MTAL | 1 |  |  |  | K2RCPA0016 |  |  |  |  | K2RCP | A0016 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L326 | R561 70V | A | N
2 | RCP | C1 SPV | A | 17 | ABC | 2RCP 003PO | A | 21 | 26 | 26 | 500 | MTAL | 1 |  |  |  | K2RCPA0017 |  |  |  |  | K2RCP | A0017 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L325 | R571 66T | A | N
2 | RCP | C1 SPV | A | 18 | ABC | 2RCP 003PO | A | 21 | 24 | 24 | 500 | MTAL | 1 |  |  |  | K2RCPA0018 |  |  |  |  | K2RCP | A0018 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L325 | R571 66T | A | N
2 | RCP | C1 SPV | A | 19 | ABC | 2RCP 003PO | A | 21 | 26 | 26 | 500 | MTAL | 1 |  |  |  | K2RCPA0019 |  |  |  |  | K2RCP | A0019 | VLF-TD | 4RO | 223 | PD | 4 YEARLY | 2019 | Visual & Tactile Inspections | 4RO | 223 | [9 empty] | PN2L325 | R571 66T | A | N
2 | RCV | C3 | A | 1 | 2LHA 0202 | 2RCV 001PO | A | 90 | 110 | 110 | 50 | MTAL | 3 |  |  |  | K2RCVA0001 |  |  |  |  | K2RCV | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0202 | N2B27 62S | A | N
2 | RCV | C3 | A | 2 | 2LHB 0302 | 2RCV 002PO | B | 83 | 86 | 86 | 50 | MTAL | 3 |  |  |  | K2RCVA0002 |  |  |  |  | K2RCV | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0302 | N2B28 61S | A | N
2 | RCV | C3 | A | 3 | 2LHA 0302 | 2RCV 003PO | A | 103 | 102 | 102 | 50 | MTAL | 3 |  |  |  | K2RCVA0003 |  |  |  |  | K2RCV | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0302 | N2B29 60S | A | N
2 | RIS | C3 | A | 1 | 2LHA 0301 | 2RIS 001PO | A | 221 | 223 | 223 | 50 | MTAL | 3 |  |  |  | K2RISA0001 |  |  |  |  | K2RIS | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0301 | K152 68CA | A | N
2 | RIS | C3 | A | 2 | 2LHB 0301 | 2RIS 002PO | B | 155 | 162 | 162 | 50 | MTAL | 3 |  |  |  | K2RISA0002 |  |  |  |  | K2RIS | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0301 | K153 67CA | A | N
2 | RRA | C3 | A | 1 | 2LHA 0501 | ABC | A | 41 | 50 | 50 | 50 | MTAL | 3 |  |  |  | K2RRAA0001 |  |  |  |  | K2RRA | A0001 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0501 | PN2L305 | A | N
2 | RRA | C3 | A | 2 | 2LHB 0601 | ABC | B | 41 | 46 | 46 | 50 | MTAL | 3 |  |  |  | K2RRAA0002 |  |  |  |  | K2RRA | A0002 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0601 | PN2L349 | A | N
2 | RRA | C3 | A | 3 | ABC | 2RRA 001MO | A | 80 | 84 | 84 | 50 | ADR | 3 |  |  |  | K2RRAA0003 |  |  |  |  | K2RRA | A0003 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | PN2L305 | R285 68Y | B | N
2 | RRA | C3 | A | 4 | ABC | 2RRA 002MO | B | 52 | 60 | 60 | 50 | ADR | 3 |  |  |  | K2RRAA0004 |  |  |  |  | K2RRA | A0004 | VLF-TD | 4RO | 225 | PD | 4 YEARLY | 2020 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | PN2L349 | R286 67Y | B | N
2 | RRI | C9 | A | 1 | 2LHA 0903 | 2RRI 001PO | A | 154 | 167 | 167 | 50 | MTAL | 3 |  |  |  | K2RRIA0001 |  |  |  |  | K2RRI | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 0903 | N0D20 59Z | A | N
2 | RRI | C9 | A | 2 | 2LHB 0903 | 2RRI 002PO | B | 111 | 123 | 123 | 50 | MTAL | 3 |  |  |  | K2RRIA0002 |  |  |  |  | K2RRI | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 0903 | N0D22 59W | A | N
2 | RRI | C9 | A | 3 | 2LHA 1003 | 2RRI 003PO | A | 154 | 167 | 167 | 50 | MTAL | 3 |  |  |  | K2RRIA0003 |  |  |  |  | K2RRI | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHA 1003 | N0D20 59Z | A | N
2 | RRI | C9 | A | 4 | 2LHB 1003 | 2RRI 004PO | B | 112 | 118 | 118 | 50 | MTAL | 3 |  |  |  | K2RRIA0004 |  |  |  |  | K2RRI | A0004 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LHB 1003 | N0D22 59V | A | N
2 | SAP | S | A | 1 | 2LGC 0801 | 2SAP 001CO | A | 107 | 118 | 118 | 50 | MTAL | 3 |  |  |  | K2SAPA0001 |  |  |  |  | K2SAP | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2LGC 0801 | 2M1E1 59G | B | N
2 | SEC | C6 | A |  | 2LHA 0902 | 2SEC 001PO | A |  |  | 267 | 50 | MTAL | 3 |  |  |  | K2SECA0001 |  |  |  |  | K2SEC | A0001 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226
2 | SEC | C6 | A |  | 2LHB 0902 | 2SEC 002PO | B |  |  | 239 | 50 | MTAL | 3 |  |  |  | K2SECA0002 |  |  |  |  | K2SEC | A0002 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226
2 | SEC | C6 | A | 3 | 2LHA 1002 | 2SEC 003PO | A |  |  | 268 | 50 | MTAL | 3 |  |  |  | K2SECA0003 |  |  |  |  | K2SEC | A0003 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226
2 | SEC | C6 | A | A | 2LHB 1002 | 2SEC 004PO | B | 2P0A 62DA | 236 | 240 | 50 | MTAL | 3 |  |  |  | K2SECA0004 |  |  |  |  | K2SEC | A0004 | VLF-TD | 4RO | 227 | PD | 4 YEARLY | 2021 | Visual & Tactile Inspections | 4RO | 226 | [9 empty] | 2SEC 002PO | 2LHB 0902 | 239 | A

## CAMP LV (hidden)
UNIT | SYSTEM | ER CLASS | CATEG | RGNB | EQUIPMENT MARK_FROM | EQUIPMENT MARK_TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | CORE | Dimensions (mm2) | Cable Size & Core | CBTYP | CABLE NUMBER | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) / FDR TEST | FREQ. | START DATE | TYPE OF TEST (ONLINE) | FREQ. | START DATE | V&T INSPECTIONS | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | SAMPLE SELCTED FOR V&T | SAMPLE SELCTED FOR IR | SAMPLE SELCTED FOR VLF-TD | SAMPLE SELCTED FOR PD | MANUFACTURER | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE
0 | DSG |  |  |  | 1DSM001AR | 0DSGA01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | When Required |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM | Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
0 | LZZ |  |  |  | 1LKS0105 | 0LZZ001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | When Required |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Transformer Function: To reduce 6,6 kV to 380 V Failure analysis and classification: Component supplies power to charge batteries used to manipulate the 400 kV breakers. Component failure would eventually lead to the inability to manipulate the 400 kV breakers. Therefore the loss of 0LZZ001TR shall have the same classification as 1/2GEV001JA => C2,C9,S1,S4,E2,E5,E6,I1,I4 | CHM
0 | LZZ |  |  |  | 2LKS0105 | 0LZZ002TR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | When Required |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Transformer Function: To reduce 6,6 kV to 380 V Failure analysis and classification: Component supplies power to charge batteries used to manipulate the 400 kV breakers. Component failure would eventually lead to the inability to manipulate the 400 kV breakers. Therefore the loss of 0LZZ002TR shall have the same classification as 1/2GEV001JA => C2,C9,S1,S4,E2,E5,E6,I1,I4 | CHM
1 | KRG |  |  |  | 1KRG024CR | 1KRG023AR | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
1 | KRG |  |  |  | 1KRG035CR | 1KRG034AR | [10 empty] | B0901 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
1 | KRG |  |  |  | 1KRG046CR | 1KRG042AR | [10 empty] | B0902 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
1 | KRT |  |  |  | 1KRT129CR | 1KRT905MA | [10 empty] | B0908 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | C9-impaired monitoring ability of SGTR. S4-reduction of defence-in-depth with 002 MA. I1-continuously in service. A1-high ambient temperature I4-continuously energised. | CHS
1 | KRT |  |  |  | 1KRT129CR | 1KRT906MA | [10 empty] | B0909 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | C9-impaired monitoring ability of SGTR. S4-reduction of defence-in-depth with 003 MA. I1-continuously in service. A1-high ambient temperature I4-continuously energised. | CHS
1 | KRT |  |  |  | 1KRT129CR | 1KRT907MA | [10 empty] | B0910 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | C9-impaired monitoring ability of SGTR. S4-reduction of defence-in-depth with 004 MA. I1-continuously in service. A1-high ambient temperature I4-continuously energised. | CHS
1 | LNE |  |  |  | 1LNE100CR | 1PTR100EN | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet - supply to 1KSC desk recorders. All cabinets are classified as RTF. | RTM | Recorder for SFP level/temperature/heat exchanger temperature. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LTP |  |  |  | 1LTP001TB | 1LTP007TB | [10 empty] | B0904 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM | Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM
1 | LTP |  |  |  | 1LTP001TB | 1LTP008TB | [10 empty] | B0905 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM | Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM
1 | ASG |  |  |  | 1ASG065UB | 1ASG055CR | [10 empty] | B0644 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Sensor supply (Sn ..) -> Consideration of the worst case. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP214VA | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP214VA | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP215VA | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h=> C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP215VA | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h=> C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP216VA | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP216VA | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP201AR | 1EPP220VA | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | EPP |  |  |  | 1EPP201AR | 1EPP220VA | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | EPP |  |  |  | 1EPP101AR | 1EPP114VA | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP114VA | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP115VA | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP115VA | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP116VA | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP116VA | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | EPP |  |  |  | 1EPP101AR | 1EPP120VA | [10 empty] | B0334 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | EPP |  |  |  | 1EPP101AR | 1EPP120VA | [10 empty] | B0335 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | KRG |  |  |  | 1KRG032AR | 1KRG031AR | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet Function: To house specified instrumentation and control equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified instrumentation and control equipment (with trigrammes) are classified => RTM | RTM | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
1 | KRG |  |  |  | 1KRG032AR | 1KRG034AR | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet Function: To house specified instrumentation and control equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified instrumentation and control equipment (with trigrammes) are classified => RTM | RTM | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
1 | KRT |  |  |  | 1KRT045CR | 1KRT003PO | [10 empty] | B0701 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply samples to radiation detector Failure analysis and classification: Component always in service => I1,I4 Failure will result in loss of post accident sampling => C9,E6 | CHM
1 | KRT |  |  |  | 1KRT001AR | 1KRT001TB | [10 empty] | B0798 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RCV403EN | [10 empty] | B0305 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for RCP pumps seal leakoff. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RRA401EN | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for RRA heat exchanger inlet and outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1KSC401EN | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG1 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1KSC402EN | [10 empty] | B0310 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG2 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1KSC403EN | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG3 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1LNA001DL | 1KPR401EN | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 MG inverters are obsolete and have a significant history of failures=> E1 and E3 | CHM | Recorder for RCP pressure, Hot and Cold leg, and RRA exchanger outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RGL401EN | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for rod bank A/B travel limitation and demand position. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RGL402EN | [10 empty] | B0316 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for rod bank C/D travel limitation and demand position. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RGL403EN | [10 empty] | B0317 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for auctioneered T-AVG and T-REF. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1KSC405EN | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Loop 1 temp gradient and RCP deviation temperature. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1ARE401EN | [10 empty] | B0319 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG1 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1ARE402EN | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG2 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1ARE403EN | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for SG3 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RCV401EN | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for VCT level and pressure. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1KSC404EN | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for charging and letdown temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1LNA001DL | 1RPN001AR | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 MG inverters are obsolete and have a significant history of failures=> E1 and E3 | CHM | The cabinet houses the following channels and components: 1. Source Range - 014MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 013MA (1oo2 trip logic when in service below P10) 3. Power Range - 010MA (2 oo 4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 010MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
1 | LNI |  |  |  | 1LNA001DL | 1RPN001AR | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 MG inverters are obsolete and have a significant history of failures=> E1 and E3 | CHM | The cabinet houses the following channels and components: 1. Source Range - 014MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 013MA (1oo2 trip logic when in service below P10) 3. Power Range - 010MA (2 oo 4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 010MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
1 | LNI |  |  |  | 1LNB001DL | 1RPN002AR | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNB feeder diagram indicates that loss of LNB001DL will result in loss of LNB001TB. Therefore the loss of LNB001DL shall have the same classification as LNB001TB => C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4. E3=>YES as per the System Engineer's review. | CHM | The cabinet houses the following channels and components: 1. Source Range - 024MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 023MA (1oo2 trip logic when in service below P10) 3. Power Range - 020MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 020MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
1 | LNI |  |  |  | 1LNB001DL | 1RPN002AR | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNB feeder diagram indicates that loss of LNB001DL will result in loss of LNB001TB. Therefore the loss of LNB001DL shall have the same classification as LNB001TB => C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4. E3=>YES as per the System Engineer's review. | CHM | The cabinet houses the following channels and components: 1. Source Range - 024MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 023MA (1oo2 trip logic when in service below P10) 3. Power Range - 020MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 020MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
1 | LNI |  |  |  | 1LNC001DL | 1RPN003AR | [10 empty] | B0339 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the the following channels and components: 1. Power Distribution 036MA 2. Power Comparison 035MA 3. Power Range - 030MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 030MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNI |  |  |  | 1LNC001DL | 1RPN003AR | [10 empty] | B0340 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the the following channels and components: 1. Power Distribution 036MA 2. Power Comparison 035MA 3. Power Range - 030MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 030MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNI |  |  |  | 1LND001DL | 1RPN004AR | [10 empty] | B0348 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the following channels and components: 1. Audio Countrate 045MA 2. Power Range - 040MA (2oo4 trip logic when in service) . 3. HV supply for CBL-15 Ionisation chamber - 040MA. 4. 48V power supply for protection outputs. 5. 48V power supply for control outputs 6. Relay panels. 7. Electromagnetic solenoids for interlocking the channel draws. 8. Selector switches and indications 9. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNI |  |  |  | 1LND001DL | 1RPN004AR | [10 empty] | B0349 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the following channels and components: 1. Audio Countrate 045MA 2. Power Range - 040MA (2oo4 trip logic when in service) . 3. HV supply for CBL-15 Ionisation chamber - 040MA. 4. 48V power supply for protection outputs. 5. 48V power supply for control outputs 6. Relay panels. 7. Electromagnetic solenoids for interlocking the channel draws. 8. Selector switches and indications 9. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN402EN | [10 empty] | B0351 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Upper Neutron Flux Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN403EN | [10 empty] | B0352 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Upper Neutron Flux Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN404EN | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Lower Neutron Flux Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN405EN | [10 empty] | B0354 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Lower Neutron Flux Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN406EN | [10 empty] | B0355 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Average Flux Power Range Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC001CR | 1RPN407EN | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Average Flux Power Range Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RPN401EN | [10 empty] | B0357 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Delta Neutron Flux A 1 or 3 and B 2 or 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RPN408EN | [10 empty] | B0358 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for Reactor Power and Delta Flux - Delta Flux Ref. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP473ID | [10 empty] | B0359 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Panel indicator Function: Indication Failure analysis and classification: Component permanently in service. => I1 Fails to provide information required by for incident/accident procedure(s) => C9 Maintenance is required to prevent degradation of the component. => E6 | CHM
1 | LNI |  |  |  | 1KSC001CR | 1KSC412EN | [10 empty] | B0362 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Recorder for RRA/RCV safety valve outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
1 | LNI |  |  |  | 1LNA001DL | 1RIC011AR | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 MG inverters are obsolete and have a significant history of failures=> E1 and E3 | CHM | Core Cooling Monitor Train A. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
1 | LNI |  |  |  | 1LND001DL | 1RIC012AR | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | Core Cooling Monitor Train B. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
1 | LNI |  |  |  | 1RIC001AR | 1RIC011AR | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM | Core Cooling Monitor Train A. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
1 | LNI |  |  |  | 1RIC001AR | 1RIC012AR | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM | Core Cooling Monitor Train B. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0304 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0305 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0306 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0307 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM002TB | [10 empty] | B0310 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RGL001AR | 1RAM002TB | [10 empty] | B0314 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RGL003AR | 1RAM002TB | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RGL004AR | 1RAM002TB | [10 empty] | B0316 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RGL005AR | 1RAM002TB | [10 empty] | B0317 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RGL006AR | 1RAM002TB | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM501BN | 1RAM002TB | [10 empty] | B0319 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002TB | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RAM |  |  |  | 1RAM501BN | 1RAM002TB | [10 empty] | B0338 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
1 | RGL |  |  |  | 1RGL001PJ | 1RGL001BK | [10 empty] | B0300 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL002PJ | 1RGL002BK | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL003PJ | 1RGL003BK | [10 empty] | B0306 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL004PJ | 1RGL004BK | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL017PJ | 1RGL017BK | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL018PJ | 1RGL018BK | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL019PJ | 1RGL019BK | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL020PJ | 1RGL020BK | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL033PJ | 1RGL033BK | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL034PJ | 1RGL034BK | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL035PJ | 1RGL035BK | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL036PJ | 1RGL036BK | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL005AR | 1RGL002AR | [10 empty] | B0336 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL002AR | [10 empty] | B0337 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL002AR | [10 empty] | B0338 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL001AR | [10 empty] | B0342 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0343 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0344 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0345 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0346 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0347 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0348 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0349 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL021PJ | 1RGL021BK | [10 empty] | B0350 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL022PJ | 1RGL022BK | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL023PJ | 1RGL023BK | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL024PJ | 1RGL024BK | [10 empty] | B0359 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL005PJ | 1RGL005BK | [10 empty] | B0362 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL006PJ | 1RGL006BK | [10 empty] | B0365 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL007PJ | 1RGL007BK | [10 empty] | B0368 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL008PJ | 1RGL008BK | [10 empty] | B0371 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL037PJ | 1RGL037BK | [10 empty] | B0374 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL038PJ | 1RGL038BK | [10 empty] | B0377 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL039PJ | 1RGL039BK | [10 empty] | B0380 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL040PJ | 1RGL040BK | [10 empty] | B0383 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0386 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0387 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0388 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0389 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0390 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0391 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0392 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0393 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0394 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0395 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0396 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0397 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0398 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0399 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL041PJ | 1RGL041BK | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL042PJ | 1RGL042BK | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL043PJ | 1RGL043BK | [10 empty] | B0406 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL044PJ | 1RGL044BK | [10 empty] | B0409 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL025PJ | 1RGL025BK | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL026PJ | 1RGL026BK | [10 empty] | B0415 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL027PJ | 1RGL027BK | [10 empty] | B0418 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL028PJ | 1RGL028BK | [10 empty] | B0421 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL009PJ | 1RGL009BK | [10 empty] | B0424 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL010PJ | 1RGL010BK | [10 empty] | B0427 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL011PJ | 1RGL011BK | [10 empty] | B0430 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL012PJ | 1RGL012BK | [10 empty] | B0433 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL013PJ | 1RGL013BK | [10 empty] | B0436 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL014PJ | 1RGL014BK | [10 empty] | B0439 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL015PJ | 1RGL015BK | [10 empty] | B0442 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL016PJ | 1RGL016BK | [10 empty] | B0445 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0448 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0449 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL029PJ | 1RGL029BK | [10 empty] | B0462 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL030PJ | 1RGL030BK | [10 empty] | B0465 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL031PJ | 1RGL031BK | [10 empty] | B0468 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL032PJ | 1RGL032BK | [10 empty] | B0471 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL045PJ | 1RGL045BK | [10 empty] | B0474 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL046PJ | 1RGL046BK | [10 empty] | B0477 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL047PJ | 1RGL047BK | [10 empty] | B0480 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL048PJ | 1RGL048BK | [10 empty] | B0483 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0489 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0490 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0491 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0492 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0493 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0494 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0495 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0496 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0497 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0498 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0499 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL003AR | [10 empty] | B0500 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL003AR | [10 empty] | B0501 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0504 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0505 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL004AR | 1RGL006AR | [10 empty] | B0506 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RGL |  |  |  | 1RGL005AR | 1RGL006AR | [10 empty] | B0507 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RPB |  |  |  | 1RPB001TB | 1RGL002AR | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RPB |  |  |  | 1RPB001TB | 1RGL002AR | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | RPB |  |  |  | 1RPB001TB | 1RGL002AR | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | APG |  |  |  | 1LKC0412 | 1APG010VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate APG when required - downstream of 001 RF Failure analysis and classification: Valve Failure to close on:- Demin high temp (>60ºC) = damage to resins => E5,E6. High pressure (P>14bar) or Temp (80ºC) => E5,E6. Valve Failure to open therefore no APG available leads to challenging Chemistry limits => S4,E5,E6. Chemistry spec's exceeded due to no APG flow => C2,C3,S4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | APP |  |  |  | 1APP003CR | 1APP001VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED And synoptic information on the KIT VALVE POSITION -> RTF | RTM | Motor operated isolation valve Function: 001 PO suction - upstream 001 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
1 | APP |  |  |  | 1APP004CR | 1APP003VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 001PO suction - downstream 001 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable =>C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6,E5. -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
1 | APP |  |  |  | 1APP007CR | 1APP005VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 001PO discharge - feed line after 004 VL Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6,E5. -- Isolation valves normally open/closed during unit operation on high pressure systems (above 7 MPa), and not intended for operation other than PTW isolation are classified as E6,A2 | CLS
1 | APP |  |  |  | 1APP005CR | 1APP011VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 002 PO suction - upstream 002 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E5,E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
1 | APP |  |  |  | 1APP006CR | 1APP013VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 002 PO suction - downstream 002 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as=> E5, E6 | CLM
1 | APP |  |  |  | 1APP008CR | 1APP015VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 002 PO discharge - feed line after 014 VL Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E5,E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 7 MPa), and not intended for operation other than PTW isolation are classified as E6,A2 | CLS
1 | ARE |  |  |  | 1ARE103CR | 1ARE029VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 002 GV (upstream control valve 032 VL). Failure analysis and classification: Locally operated valve from 103 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
1 | ARE |  |  |  | 1ARE102CR | 1ARE028VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 001 GV (upstream control valve 031 VL). Failure analysis and classification: Locally operated valve from 102 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
1 | ARE |  |  |  | 1ARE101CR | 1ARE030VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 003 GV (upstream control valve 033 VL). Failure analysis and classification: Locally operated valve from 101 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
1 | ARE |  |  |  | 1LKA0405 | 1ARE036VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 003 GV - downstream of 033VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
1 | ARE |  |  |  | 1LKC0411 | 1ARE034VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 001 GV - downstream of 031 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
1 | ARE |  |  |  | 1LKA0407 | 1ARE035VL | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 002 GV - downstream of 032 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
1 | ARE |  |  |  | 1LKA0406 | 1ARE247VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 003 GV - downstream of 244 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
1 | ARE |  |  |  | 1LKC0408 | 1ARE245VL | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 001 GV - downstream of 242 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
1 | ARE |  |  |  | 1LKA0408 | 1ARE246VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 002 GV - downstream of 243 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
1 | ASG |  |  |  | 1LLA0312 | 1ASG012PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG001 PO. Function: Supplies lube oil to 001PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
1 | ASG |  |  |  | 1LLB0310 | 1ASG022PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG002 PO. Function: Supplies lube oil to 002 PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
1 | ASG |  |  |  | 1LKH0202 | 1ASG032PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG003 PO. Function: Supplies lube oil to 003 PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
1 | CFI |  |  |  | 9LKX002CR | 1CFI111VC | [10 empty] | B0061 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 001 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | CFI |  |  |  | 9LKX002CR | 1CFI112VC | [10 empty] | B0062 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 002 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | CFI |  |  |  | 9LKX002CR | 1CFI113VC | [10 empty] | B0063 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 003 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | CFI |  |  |  | 9LKX002CR | 1CFI111VC | [10 empty] | B0064 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 001 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | CFI |  |  |  | 9LKX002CR | 1CFI112VC | [10 empty] | B0065 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 002 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | CFI |  |  |  | 9LKX002CR | 1CFI113VC | [10 empty] | B0066 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 003 TF Valve refered to accidents/incidents procedures =>C9 | CLS
1 | DEG |  |  |  | 1LLB0308 | 1DEG013VD | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG supply line to containment - outside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
1 | DEG |  |  |  | 1LLB0307 | 1DEG045VD | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG return line from containment - outside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
1 | DEG |  |  |  | D0911 | 1DEG044VD | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG return line from containment - inside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
1 | DMK |  |  |  | 1DMK003BX | 1DMK003PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. 2017/11/07 The failure of the DMK crane can have dire consequences for the spent-fuel pool if it drops a cask.=>C6 (Emmanuel Lamprecht - 26 October 2017) A PSA study done for the cask-licensing project for cask-drop accidents indicate that the failure of the DMK crane is a major risk at Koeberg, because – contrary to popular belief – the fuel building is not designed to handle cask drops into the cask-loading cell or cask-cleaning cell. Certain documents (e.g., KBA00A1C01027) state that the floors of these cells are designed for drops from maximum height into these cells, but then they also state that these drops are not design loads for the building because of the safety features built into the crane. However, minutes of a technical meeting held at Velizy (Koeberg Document Number 20624) between representatives from ESCOM, the AEB, FRAMATEG and SPIE-Batignolles, confirm that ESCOM accepted that the abovementioned drop incidents are not design loads for the building. Hence, we cannot rely on the building to retain the integrity of the SFP in the event of drops from the maximum height into these cells. A 0.5 m (yes, fifty centimeters) drop is included in the load-cases for the building because the crane overspeed detection & braking mechanisms are ineffective at low heights like this. | CLM
1 | DSC |  |  |  | 1DSP002AR | 1DSC001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
1 | DSD |  |  |  | 1LLO001TR | 1DSDB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSD |  |  |  | 1LLN001TR | 1DSDA01CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSG |  |  |  | 1LLN001TR | 1DSGV01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSK |  |  |  | 1LLO001TR | 1DSKA01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSK |  |  |  | 1LLO001TR | 1DSKE02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLN001TR | 1DSLB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLN001TR | 1DSLE02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLO001TR | 1DSLE03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLN001TR | 1DSLH04CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLN001TR | 1DSLH05CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLO001TR | 1DSLH06CR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSL |  |  |  | 1LLO001TR | 1DSLA01CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSM |  |  |  | 1DSM001AR | 1DSMB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSM |  |  |  | 1DSM001AR | 1DSMC02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSM |  |  |  | 1LLN001TR | 1DSM001AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSP |  |  |  | 1DSP001AR | 1DSP001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
1 | DSP |  |  |  | 1DSP002AR | 1DSP002CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
1 | DSP |  |  |  | 1LLN001TR | 1DSP001AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
1 | DSP |  |  |  | 1LLO001TR | 1DSP002AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
1 | DSR |  |  |  | 1DSR001AR | 1DSRB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => RTM | RTM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSR |  |  |  | 1DSR001AR | 1DSRG03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => RTM | RTM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSR |  |  |  | 1DSR001AR | 1DSRB01CR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => RTM | RTM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DSR |  |  |  | 1DSRE02CR | 1DSRG03CR | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DST |  |  |  | 1DSM001AR | 1DST001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DTL |  |  |  | 1DTL004CR | 1DSRB01CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DTL |  |  |  | 1DTL007CR | 1DSRB01CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DTL |  |  |  | 1DTL009CR | 1DSRB01CR | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DTL |  |  |  | 1DTL009CR | 1DSRB01CR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
1 | DVG |  |  |  | 1LLI0307 | 1DVG001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fresh Air Supply Fan - ASG pumps room ventilation inlet fan - Train A Function:Provide cool air o ASG pump room. Failure analsis: Component not in service. Fails to run on request/demand (or during PT) - entry into OTS => C3 SRSM requirement for auto + manual start PSA Significant Component => S6. | CLM
1 | DVG |  |  |  | 1LLJ0311 | 1DVG002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fresh Air Supply Fan - ASG pumps room ventilation inlet fan - Train A Function:Provide cool air o ASG pump room. Failure analsis: Component not in service. Fails to run on request/demand (or during PT) - entry into OTS => C3 SRSM requirement for auto + manual start PSA Significant Component => S6. | CLM
1 | DVG |  |  |  | 1LLI0306 | 1DVG003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
1 | DVG |  |  |  | 1LLJ0310 | 1DVG004ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
1 | DVG |  |  |  | 1LLI0412 | 1DVG003ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
1 | DVG |  |  |  | 1LLJ0411 | 1DVG004ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
1 | DVH |  |  |  | 1LLA0103 | 1DVH001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - air supply to RCV pump rooms - Train A. Function: To supply cooled air to RCV pump rooms. Failure analysis: Fan 50% in service. Fan failure will result in over-heating of RCV motors/pumps.=>E5 SRSM test requirement - 2 monthly - auto start during RPR PT => C3 | CLM
1 | DVH |  |  |  | 1LLB0105 | 1DVH002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - air supply to RCV pump rooms - Train A. Function: To supply cooled air to RCV pump rooms. Failure analysis: Fan 50% in service. Fan failure will result in over-heating of RCV motors/pumps.=>E5 SRSM test requirement - 2 monthly - auto start during RPR PT => C3 | CLM
1 | DVK |  |  |  | 1LLI0304 | 1DVK005ZV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Iodine exhaust fan - Train A Function:Evacuate air from the fuel building through a Iodine filter system. Failure analysis: Component fails to start;standby fans stars automatically= C9 SRSM requirement - 1RO starting test from manual actuation => NO C3, but => S3 SRSM requirement - 1RO starting test from Train A SI signal SRSM requirement - 1RO starting test from Hi activity KRT 013 or 014 MA => NO C2, but => E6 | CLM
1 | DVK |  |  |  | 1LLJ0308 | 1DVK006ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Iodine exhaust fan - Train B Function:Evacuate air from the fuel building through a Iodine filter system. Failure analysis: Component fails to start;standby fans stars automatically= C9 SRSM requirement - 1RO starting test from manual actuation => NO C3, but => S3 SRSM requirement - 1RO starting test from Train A SI signal SRSM requirement - 1RO starting test from Hi activity KRT 013 or 014 MA => NO C2, but => E6 | CLM
1 | DVS |  |  |  | 1LLA0406 | 1DVS001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air supply fan to EAS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
1 | DVS |  |  |  | 1LLB0409 | 1DVS002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air supply fan to EAS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
1 | DVS |  |  |  | 1LLA0407 | 1DVS003ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air supply fan to RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
1 | DVS |  |  |  | 1LLB0410 | 1DVS004ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air supply fan to RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
1 | DWS |  |  |  | 1LLI0403 | 1DWS001RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater electric. Entry into OTS if inoperable => C3,E6. Cycled frequently =>I2. Exposed to sea air => A6. | CHS
1 | DWS |  |  |  | 1LLD0305 | 1DWS002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater electric. Entry into OTS if inoperable => C3,E6. Cycled frequently =>I2. Exposed to sea air => A6. | CHS
1 | DWS |  |  |  | 1LLI0404 | 1DWS001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
1 | DWS |  |  |  | 1LLJ0307 | 1DWS002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
1 | DWS |  |  |  | 1LLA0307 | 1DWS003ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
1 | DWS |  |  |  | 1LLB0304 | 1DWS004ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
1 | EAS |  |  |  | 1LLD0304 | 1EAS002VB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate 001 PO suction from 001 BA - train A - suction from PTR 001 BA. Failure analysis and classification: - Failure to open/remain open will result in unavailabiliry of Train A and if in "when require operating state", OTS entry will require => C3 - Failure to close when PTR tank level reaches 2.1m (during CS if 013 VB open) will result in loss of suction head to 001 PO making Train A unavailable => C6,C7,C9 - SRSM requirement - 2 mthly - verify valve operation (any domain) - PT failure will require entry into OTS => C3,S4 Failure to function during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | EAS |  |  |  | 1LLC0305 | 1EAS001VB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate 001 PO suction from 001 BA - train A - suction from PTR 001 BA. Failure analysis and classification: - Failure to open/remain open will result in unavailabiliry of Train A and if in "when require operating state", OTS entry will require => C3 - Failure to close when PTR tank level reaches 2.1m (during CS if 013 VB open) will result in loss of suction head to 001 PO making Train A unavailable => C6,C7,C9 - SRSM requirement - 2 mthly - verify valve operation (any domain) - PT failure will require entry into OTS => C3,S4 Failure to function during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | EAS |  |  |  | 1LLD0303 | 1EAS008VB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train B EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | EAS |  |  |  | 1LLC0304 | 1EAS007VB | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train A EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | EAS |  |  |  | 1LLD0302 | 1EAS010VB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train B EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 -- SRSM requirement - 1 RO PT - outage - LLRT PT is performed -failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C3 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | EAS |  |  |  | 1LLC0303 | 1EAS009VB | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train A EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | EAS |  |  |  | 1LLD0301 | 1EAS014VB | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve Function: Suction line to 002 PO from cont. sump 002 PS - outside cont. Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into OTS => C3 - Failure to open upon CS (recirc signal) => C7,C9,S1,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening time & maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | EAS |  |  |  | 1LLC0302 | 1EAS013VB | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve Function: Suction line to 001 PO from cont. sump 001 PS - outside cont. Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into OTS => C3 - Failure to open upon CS (recirc signal) => C7,C9,S1,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening time & maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | ETY |  |  |  | 1LKH0403 | 1ETY001RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | O/C - electric heater in the air duct upstream iodine filtration Component energized manually by an operator while placing iodine filtration in service. Component interlocked by 003 SD (lack of flow) and 001 ST (temp Hi). Component failure to energize (KIT 037 EC - OFF) will render iodine line inoperable => C3 Component failure to heat will reduce efficiency of the iodine filter 001 PI => E5 (no temp Lo alarm). SRSM requirement - 1RO verify energizing SRSM requirement - 1RO verify tripping SRSM requirement - 4RO tripping @ 70°C on 001 ST SRSM requirement - 4RO tripping @ Q<1000m³/h (low flow) on 003 SD SRSM requirement - 5RO verify heating capacity | CHM
1 | ETY |  |  |  | 1LLJ0305 | 1ETY002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment air circulation and exhaust fan. Function: Circulate and exhaust containment air. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Component failure when in use will require OTS entry. => C3 Component tested during monthly KWB-PT ETY-070 - failure => C3 | CLM
1 | ETY |  |  |  | 1LLI0406 | 1ETY001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment air circulation and exhaust fan. Function: Circulate and exhaust containment air. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Component failure when in use will require OTS entry. => C3 Component tested during monthly KWB-PT ETY-070 - failure => C3 | CLM
1 | GCT |  |  |  | 1LKH0404 | 1GCT100VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 1 & 3 (110,111,118 & 119 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | GCT |  |  |  | 1LKH0405 | 1GCT101VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 2 & 4 (114,115,122 & 123 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | GCT |  |  |  | 1LKH0406 | 1GCT102VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 2 & 4 (112,113,120 & 121 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | GCT |  |  |  | 1LKH0407 | 1GCT103VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 1 & 3 (116,117,108 & 109 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 | CLS
1 | GCT |  |  |  | 1LLA0510 | 1GCT128VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 1 Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 131 VV . Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 131 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
1 | GCT |  |  |  | 1LLC0405 | 1GCT129VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 2. Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 132 VV. Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 132 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
1 | GCT |  |  |  | 1LLI0407 | 1GCT130VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 2. Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 133 VV. Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 133 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
1 | GEX |  |  |  | 1GEX001AR | 1GEX002AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: All enclosures and cabinets hosting components with individual trigramme (and not classified at least A6) are classifies as RTM. Component has been re-classified based on information that " it is the parent for the AVR system, which is a priority from CIP and a priority 1 from RE’s list" => C2. | CLM
1 | GEX |  |  |  | 1GEX002AP | 1GEX001AR | [10 empty] | B0601 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation generator Function: To provide the excitation current to the main generator Failure analysis and classification: Loss of the excitation generator will result in the loss of GEX001GA Therefore the loss of GEX001AP shall have the same classification as GEX001GA => C2,C4,C5,C6,C8,C9,S4,E5,E6,I1,I4 (But NO S1) NOTE: In evaluating the failure of this component it is assumed that the unit is in House Load Configuration. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX002AP | 1GEX001AR | [10 empty] | B0602 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation generator Function: To provide the excitation current to the main generator Failure analysis and classification: Loss of the excitation generator will result in the loss of GEX001GA Therefore the loss of GEX001AP shall have the same classification as GEX001GA => C2,C4,C5,C6,C8,C9,S4,E5,E6,I1,I4 (But NO S1) NOTE: In evaluating the failure of this component it is assumed that the unit is in House Load Configuration. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX003AP | 1GEX001AR | [10 empty] | B0603 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Load angle generator Function: To supply the load angle to the excitation circuit Failure analysis and classification: Component permanently in service. -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX001TR | 1GEX002TR | [10 empty] | B0604 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM
1 | GEX |  |  |  | 1GEX002TR | 1GEX003TR | [10 empty] | B0605 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM
1 | GEX |  |  |  | 1GEX001TR | 1GEX002TR | [10 empty] | B0606 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM
1 | GEX |  |  |  | 1GEX002TR | 1GEX003TR | [10 empty] | B0607 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM
1 | GEX |  |  |  | 1GEX001TR | 1GEX003TR | [10 empty] | B0608 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM
1 | GEX |  |  |  | 1GEX020CR | 1GEX001AR | [10 empty] | B0609 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX020CR | 1GEX001AR | [10 empty] | B0610 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX003TR | 1GEX001AR | [10 empty] | B0611 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service and enefgised => I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GEX |  |  |  | 1GEX020CR | 1GEX001AR | [10 empty] | B0612 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | GGR |  |  |  | 1GGR002BX | 1GGR002PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lubrication oil to the main turbo-alternator when the main pump cannot Failure analysis and classification: Component on standby during turbine operation. In service during turbine shutdown and start up. - Failure to function when the turbine is in service will result in a turbine trip => C2 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 First stand by pump, receives auto start order on lo lub oil pressure. Defence in depth. => S4, E6 | CLM
1 | GGR |  |  |  | 1GGR059CR | 1GGR001MO | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM | Motor Function: To drive 001 PO Failure analysis and classification: Component continuously in service and energized => I1,I4 Failure can have the following consequences: - Failure to function during normal operation will result in no load loss. The stand-by pump 002 PO will take over. To overhaul or exchange the pump requires a turbine outage as the motor is supplied from a generator on the turbine shaft. =>C2, E6 - Outage repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities. Therefore NO C2. | CHM
1 | GGR |  |  |  | 1GGR059CR | 1GGR001MO | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM | Motor Function: To drive 001 PO Failure analysis and classification: Component continuously in service and energized => I1,I4 Failure can have the following consequences: - Failure to function during normal operation will result in no load loss. The stand-by pump 002 PO will take over. To overhaul or exchange the pump requires a turbine outage as the motor is supplied from a generator on the turbine shaft. =>C2, E6 - Outage repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities. Therefore NO C2. | CHM
1 | GSE |  |  |  | 1DNLG151BC | 1GSE002AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | This cabinet is to performed control functions for the GGR jacking oil, slow rotation, GSS, CET, CAR and other auxiliary systems to the turbine. | CHM
1 | GSS |  |  |  | 1LKC0801 | 1GSS221VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve . Function: 200 & 400 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | CLM
1 | JPP |  |  |  | 1JPP002BX | 1JPP002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply fire fighting water Failure analysis and classification: Failure will result in loss of redundancy => C9,S4,E6,A6 | CLS
1 | JPP |  |  |  | 1JPP001BX | 1JPP001PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply fire fighting water Failure analysis and classification: Failure will result in loss of redundancy => C9,S4,E6,A6 | CLS
1 | KRT |  |  |  | 1LLA0501 | 1KRT001TB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
1 | LAA |  |  |  | 1LLE0105 | 1LAA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor scram as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA001RD will result in loss of LAA001TB. Therefore the loss of LAA001RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Chargers obsolete and high failure history => E1 and E3 yes | CHM
1 | LAA |  |  |  | 1LLI0107 | 1LAA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor shut down as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA002RD will result in loss of LAA001TB. Therefore the loss of LAA002RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 High failure history and RSI chargers are obsolete E1 and E3 => YES | CHM
1 | LAA |  |  |  | 1LLE0105 | 1LAA001RD | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor scram as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA001RD will result in loss of LAA001TB. Therefore the loss of LAA001RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Chargers obsolete and high failure history => E1 and E3 yes | CHM
1 | LAA |  |  |  | 1LLI0107 | 1LAA002RD | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor shut down as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA002RD will result in loss of LAA001TB. Therefore the loss of LAA002RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 High failure history and RSI chargers are obsolete E1 and E3 => YES | CHM
1 | LAA |  |  |  | 1LAA0242 | 1LNE001DL | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAA |  |  |  | 1LAA0242 | 1LNE001DL | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAA |  |  |  | 1LAA0231 | 1LNE002DL | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAA |  |  |  | 1LAA0231 | 1LNE002DL | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAA |  |  |  | 1LAA0232 | 1LNE003DL | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAA |  |  |  | 1LAA0232 | 1LNE003DL | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LAB |  |  |  | 1LAB03 | 1GGR004PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
1 | LAB |  |  |  | 1LAB03 | 1GGR004PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
1 | LAB |  |  |  | 1LAB03 | 1GGR004PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
1 | LAC |  |  |  | 1LAC04 | 1GGR003PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
1 | LAC |  |  |  | 1LAC04 | 1GGR003PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
1 | LAC |  |  |  | 1LAC04 | 1GGR003PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
1 | LBC |  |  |  | 1LLA0509 | 1LBC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBC feeder diagram indicates that loss of LBC001RD will result in loss of LBC001TB. Therefore the loss of LBC001RD shall have the same classification as LBC001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LBD |  |  |  | 1LLB0508 | 1LBD001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBD feeder diagram indicates that loss of LBD001DL will result in loss of LBD001TB. Therefore the loss of LBD001DL shall have the same classification as LBD001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LBE |  |  |  | 1LLA0508 | 1LBE001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBE feeder diagram indicates that loss of LBE001RD will result in loss of LBE001TB. Therefore the loss of LBE001RD shall have the same classification as LBE001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LBF |  |  |  | 1LLB0507 | 1LBF001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBF feeder diagram indicates that loss of LBF001RD will result in loss of LBF001TB. Therefore the loss of LBF001RD shall have the same classification as LBF001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LBJ |  |  |  | 1LLC0409 | 1LBJ001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBJ feeder diagram indicates that loss of LBJ001RD will result in loss of LBJ001TB. Therefore the loss of LBJ001RD shall have the same classification as LBJ001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LBJ |  |  |  | 1LLI0409 | 1LBJ002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBJ feeder diagram indicates that loss of LBJ001RD will result in loss of LBJ001TB. Therefore the loss of LBJ001RD shall have the same classification as LBJ001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LDA |  |  |  | 1LLA0504 | 1LDA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LDA feeder diagram indicates that loss of LDA001RD will result in loss of LDA001TB. Therefore the loss of LDA001RD shall have the same classification as LDA001TB => C1,C2,C6,C8,C9,S4,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LDA |  |  |  | 1LLC0411 | 1LDA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LDA feeder diagram indicates that loss of LDA001RD will result in loss of LDA001TB. Therefore the loss of LDA001RD shall have the same classification as LDA001TB => C1,C2,C6,C8,C9,S4,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHP |  |  |  | 1LLG0103 | 1LHP004MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Motor Function: Lube Oil Pre-lube Failure analysis and classification: -- Pump failure will result in loss of engine pre-heat. => C3, S5, I1 | CHM
1 | LHP |  |  |  | 1LLG0203 | 1LHP005PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: Oil Filling Failure analysis and classification: -- Pump failure will result in inability to fill oil storage tank and replenish consumption at 7kg/s. Estimated mission time of 30 days. => C8, C9, S1, S5. | CLM
1 | LHP |  |  |  | 1LLG0204 | 1LHP001RE | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater Function: Pre-heat Water Heating Failure analysis and classification: Loss of engine pre-heat will result in slow starts and increased engine wear. => C3, E6 | CLM
1 | LHP |  |  |  | 1LLG0205 | 1LHP002RE | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater Function: Generator anti condensation heater. Failure analysis and classification: Maintain generator stator temperature to prevent ingress of moisture. Heater failure could result in moisture ingress and subsequent degradation of stator insulation which could result in unavailability of the EDG. => C3, C8, C9, S6, E5, I1, I4 | CHM
1 | LHP |  |  |  | 1LLG0107 | 1LHP001ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
1 | LHP |  |  |  | 1LLG0105 | 1LHP002ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
1 | LHP |  |  |  | 1LHP002AR | 1LHP001GA | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHP |  |  |  | 1LHP002AR | 1LHP001GA | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHP |  |  |  | 1LHP002AR | 1LHP001GA | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHP |  |  |  | 1LHP002AR | 1LHP001GA | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHP |  |  |  | 1LLG0204 | 1LHP004RE | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Electric heater Function: Pre-heating sub-system. Failure analysis and classification: Failure of the pre-heating system does not immediately render the EDG inoperable. The EDG will however be considered inoperable in accordance with OTS if the pre-heat temperature drop down to the alarm level of 40¿C. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, | CLM
1 | LHP |  |  |  | 1LHP003AR | 1LHP002AR | [10 empty] | B0117 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: EDG relaying control cabinet. Function: Relaying for local EDG start/stop and protection control functions. Failure analysis and classification: Relaying failure could result in failure of the EDG to start or failure to run. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM
1 | LHQ |  |  |  | 1LLW0103 | 1LHQ004MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Motor Function: Lube Oil Pre-lube Failure analysis and classification: -- Pump failure will result in loss of engine pre-heat. => C3, S5, I1 | CHM
1 | LHQ |  |  |  | 1LLW0203 | 1LHQ005PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: Oil Filling Failure analysis and classification: -- Pump failure will result in inability to fill oil storage tank and replenish consumption at 7kg/s. Estimated mission time of 30 days. => C8, C9, S1, S5. | CLM
1 | LHQ |  |  |  | 1LLW0204 | 1LHQ001RE | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater Function: Pre-heat Water Heating Failure analysis and classification: Loss of engine pre-heat will result in slow starts and increased engine wear. => C3, E6 | CLM
1 | LHQ |  |  |  | 1LLW0205 | 1LHQ002RE | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Heater Function: Generator anti condensation heater. Failure analysis and classification: Maintain generator stator temperature to prevent ingress of moisture. Heater failure could result in moisture ingress and subsequent degradation of stator insulation which could result in unavailability of the EDG. => C3, C8, C9, S6, E5, I1, I4 | CHM
1 | LHQ |  |  |  | 1LLW0107 | 1LHQ001ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
1 | LHQ |  |  |  | 1LLW0105 | 1LHQ002ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
1 | LHQ |  |  |  | 1LHQ002AR | 1LHQ001GA | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHQ |  |  |  | 1LHQ002AR | 1LHQ001GA | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHQ |  |  |  | 1LHQ002AR | 1LHQ001GA | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHQ |  |  |  | 1LHQ002AR | 1LHQ001GA | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LHQ |  |  |  | 1LLW0204 | 1LHQ004RE | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Electric heater Function: Pre-heating sub-system. Failure analysis and classification: Failure of the pre-heating system does not immediately render the EDG inoperable. The EDG will however be considered inoperable in accordance with OTS if the pre-heat temperature drop down to the alarm level of 40¿C. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, | CLM
1 | LHQ |  |  |  | 1LHQ003AR | 1LHQ002AR | [10 empty] | B0117 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: EDG relaying control cabinet. Function: Relaying for local EDG start/stop and protection control functions. Failure analysis and classification: Relaying failure could result in failure of the EDG to start or failure to run. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM
1 | LKL |  |  |  | 1LKD0103 | 1LKL001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKL001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C6,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LKL |  |  |  | 1LKD0103 | 1LKL001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKL001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C6,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LLG |  |  |  | 1LLI0103 | 1LLG001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLG001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LLG |  |  |  | 1LLI0103 | 1LLG001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLG001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LLW |  |  |  | 1LLJ0105 | 1LLW001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLW001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LLW |  |  |  | 1LLJ0105 | 1LLW001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLW001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL001AR | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL002AR | [10 empty] | B0102 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL003AR | [10 empty] | B0103 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL004AR | [10 empty] | B0104 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL005AR | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | LMA |  |  |  | 1LMA100CR | 1RGL006AR | [10 empty] | B0106 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
1 | LNA |  |  |  | 1LLC0412 | 1LNA001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Transformer. Function: Power transformer Failure analysis and classification: Review of theLNA feeder diagram indicates that loss of LNA001TR will result in loss of LNA001TB. Therefore the loss of LNA001TR shall have the same classification as LNA001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 Major components like the transformer are obsolete =>E3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNB |  |  |  | 1LLD0408 | 1LNB001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Transformer. Function: Power transformer Failure analysis and classification: Review of theLNB feeder diagram indicates that loss of LNB001TR will result in loss of LNB001TB. Therefore the loss of LNB001TR shall have the same classification as LNB001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4 Major components like the transformer are obsolete =>E3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNC |  |  |  | 1LLC0512 | 1LNC001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Transformer. Function: Power transformer Failure analysis and classification: Review of theLNC feeder diagram indicates that loss of LNC001TR will result in loss of LNC001TB. Therefore the loss of LNC001TR shall have the same classification as LNC001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 Major components like the transformer are obsolete =>E3 | CHM
1 | LND |  |  |  | 1LLD0409 | 1LND001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Transformer. Function: Power transformer Failure analysis and classification: Review of theLND feeder diagram indicates that loss of LND001TR will result in loss of LND001TB. Therefore the loss of LND001TR shall have the same classification as LND001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 Major components like the transformer are obsolete =>E3 | CHM
1 | LNE |  |  |  | 1LLI0310 | 1LNE001DL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LNE |  |  |  | 1LNE001DL | 1LNE002DL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LNE |  |  |  | 1LNE002DL | 1LNE003DL | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
1 | LNE |  |  |  | 1LNE0234 | 1GPA003AR | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet hosting electrical protection equipment Function: To host protection circuits Failure analysis and classification: Component permanently in service => I1, I4 Failure to function 'when required’ could result in a turbine trip, Pn >20% Loss, outage delay => C2, S4, S7, E6 | CHM
1 | LNE |  |  |  | 1LNE0223 | 1GPA004AR | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet hosting electrical protection equipment Function: To host protection circuits Failure analysis and classification: Component permanently in service => I1, I4 Failure to function 'when required’ could result in a turbine trip, Pn >20% Loss, outage delay => C2, S4, S7, E6 | CHM
1 | LNE |  |  |  | 1LNE0351 | 1RGL010AR | [10 empty] | B0045 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | In the worst case when all redundancy is lost in the Processing Logic will mean that the system will not be able to perform rod cluster position monitoring and comparison. Functional failure of the cabinet will affect the comparison of rods and banks and the position display on RGL 001 HV. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement. If comparison only is affected then RGL 5 Group 2 applies. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNE |  |  |  | 1LNE0341 | 1RGL009AR | [10 empty] | B0049 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017/08/25 Classification updated - Not SPV, C2 removed. | CHM
1 | LNE |  |  |  | 1LNE0342 | 1RGL009AR | [10 empty] | B0050 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017/08/25 Classification updated - Not SPV, C2 removed. | CHM
1 | LNE |  |  |  | 1LNE0343 | 1RGL009AR | [10 empty] | B0051 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017/08/25 Classification updated - Not SPV, C2 removed. | CHM
1 | LNE |  |  |  | 1LNE0333 | 1RIC001AR | [10 empty] | B0055 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM
1 | LNE |  |  |  | 1LNE0322 | 1RAM001TB | [10 empty] | B0058 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | AC Switchboard Function: AC switchboard for RAM sets. Failure analysis and classification: Switchboard continuously in service and energized => I1,I4 - Failure of the switchboard will/could make both RAM motor/alternator sets inoperable => C1,C2,C8,C9,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | LNE |  |  |  | 1LNE0453 | 1ASG055CR | [10 empty] | B0071 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Sensor supply (Sn ..) -> Consideration of the worst case. | CHM
1 | LNE |  |  |  | 1LNE0344 | 1GEX001AR | [10 empty] | B0076 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
1 | LNE |  |  |  | 1GSE001AR | 1GSE002AR | [10 empty] | B0081 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | This cabinet houses the Bently racks for the turbine expansion and vibration sensors. It also houses the acquisition rack for the RCP system. The vibration measurerment circuit now produces an automated 2oo20 protection trip. =>S4,E5 This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM | This cabinet is to performed control functions for the GGR jacking oil, slow rotation, GSS, CET, CAR and other auxiliary systems to the turbine. | CHM
1 | LNE |  |  |  | 1LNE180CR | 1GPB002AR | [10 empty] | B0183 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet - supply to auto time switch. All cabinets are classified as RTF. | RTM | Function: Sub-Synchronization Resonance Protection GPB001AR is the parent component for the SSR protection. C2 - A failure of the SSR protection (GPB) can initiate tripping of the 400kV breaker. This will house load the unit resulting in 900MW load loss. S4 - See above comment. E4 - Long lead time for spares I-1 - Always in service when unit online. I-4 - VT and CT inputs with speed signals measured from tooth wheels on turbine end and exciter end. | CHM
1 | LNE |  |  |  | 1LNE320CR | 1VVP010MP | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet - supply to 1SAS supply. All cabinets are classified as RTF. | RTM | Line 1 steam pressure TX - Prot. channel - 2/3 logic - SIP III. Loss of PROTECTION FUNCTION => C5-To RPR - STEAMLINE BREAK PROTECTION - To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6 - To ID & EN in C/room-To EU | CHS
1 | LNE |  |  |  | 1LNE320CR | 1VVP011MP | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet - supply to 1SAS supply. All cabinets are classified as RTF. | RTM | Line 1 steam pressure TX - Prot. channel - 2/3 logic - SIP IV. Loss of PROTECTION FUNCTION => C5 - To RPR - STEAMLINE BREAK PROTECTION - To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6 - To - VVV 001 VV OPENING ENABLE - To ID in C/room - To EU | CHS
1 | LNE |  |  |  | 1LNE320CR | 1VVP012MP | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Cabinet - supply to 1SAS supply. All cabinets are classified as RTF. | RTM | Line 3 steam pressure TX - Prot. channel - 2/3 logic - SIP III. Loss of PROTECTION FUNCTION => C5-To RPR - STEAMLINE BREAK PROTECTION-To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6-To ID in C/room-To EU | CHS
1 | PMC |  |  |  | 1LKL0107 | 1PMC002TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in Fuel bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment => S4,E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | CLM
1 | PMC |  |  |  | 1LKL0107 | 1PMC002TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in Fuel bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment => S4,E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | CLM
1 | PMC |  |  |  | CGE | 1PMC001TB | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in RX bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment => S4,E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | CLM
1 | PTR |  |  |  | 1PTR001BX | 1PTR001PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | PTR recirc pump. Function: Pump used to recirculate the SFP as well as do various water transfers within the PTR system. Failure analysis: Component runs 50% during normal SFP recirculation.S4,E5,E6 Component used under varying workload conditions as 1PTR001PO is used for various transfers with varying suction heads and flowrates => E6 Component required for SFP cooling during RO when all the fuel is stored in the SFP. Both cooling trains to the SFP are required at this time. PSA Significant Component => S6. | CLM
1 | PTR |  |  |  | 1PTR002BX | 1PTR002PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | PTR recirc pump. Function: Pump used to recirculate the SFP as well as do various water transfers within the PTR system. Component used as RRA back-up during fuel unload/reload. Failure analysis: When in RRA back-up mode, the loss of 002PO results in loss of redundancy.=>S4. Component used under varying workload conditions as 1PTR002PO is used for various transfers with varying suction heads and flowrates =>C6,E5, E6 Component required for SFP cooling during RO when all the fuel is stored in the SFP. Both cooling trains to the SFP are required at this time. =>C6 PSA Significant Component => S6. Duty cycle remains low as the running regime is changing from 1 month on 2 months off, to 2 months on 2 months off. This change is to align with the testing of the emergency diesel generators. | CLM
1 | RAM |  |  |  | 1LKC0205 | 1RAM001TB | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | AC Switchboard Function: AC switchboard for RAM sets. Failure analysis and classification: Switchboard continuously in service and energized => I1,I4 - Failure of the switchboard will/could make both RAM motor/alternator sets inoperable => C1,C2,C8,C9,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | RAM |  |  |  | 1LKA0201 | 1RAM001TB | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | AC Switchboard Function: AC switchboard for RAM sets. Failure analysis and classification: Switchboard continuously in service and energized => I1,I4 - Failure of the switchboard will/could make both RAM motor/alternator sets inoperable => C1,C2,C8,C9,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
1 | RCP |  |  |  | B0103 | 1RCP011PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 001 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 001 PO is running. Required only during start-up and shut-down. -- Failure to function during 001 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The equipment is required to perform steps in the incident/accident procedures or severe accident management guidelines. =>C9 | CLM
1 | RCP |  |  |  | B0103 | 1RCP021PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 002 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 002 PO is running. Required only during start-up and shut-down. -- Failure to function during 002 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Equipment required to perform steps required by incident/accident procedures or severe accident management guidelines.=>C9 | CLM
1 | RCP |  |  |  | B0103 | 1RCP031PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 003 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 003 PO is running. Required only during start-up and shut-down. -- Failure to function during 003 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Equipment required to perform steps required by incident/accident procedures or severe accident management guidelines.=>C9 | CLM
1 | RCP |  |  |  | J2527 | 1RCP005VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 008 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 008 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 008 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 Update, Wed 2017/11/29. Change 1/2 RCP 005/6/7/VP from C2 to C1, C2 The block valves are left open during power. However, should a PORV open and then fail to close, the relevant block valve is required to close. Therefore, the failure of the block valve on its own will have no direct plant consequences but there are OTS limitations as the plant may have to fallback to SD / RRA within 1 hour. However, if there is a failure of the block valve to close when it is required with a PORV stuck open, then it can result in an immediate reactor trip. Therefore, the ER classification of 1/2 RCP 005/006/007 VP should be changed from C2 to C1/C2. | CHS
1 | RCP |  |  |  | E1315 | 1RCP007VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 010 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 010 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 010 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 Update, Wed 2017/11/29. Change 1/2 RCP 005/6/7/VP from C2 to C1, C2 The block valves are left open during power. However, should a PORV open and then fail to close, the relevant block valve is required to close. Therefore, the failure of the block valve on its own will have no direct plant consequences but there are OTS limitations as the plant may have to fallback to SD / RRA within 1 hour. However, if there is a failure of the block valve to close when it is required with a PORV stuck open, then it can result in an immediate reactor trip. Therefore, the ER classification of 1/2 RCP 005/006/007 VP should be changed from C2 to C1/C2. | CHS
1 | RCP |  |  |  | J2830 | 1RCP006VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 009 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 009 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 009 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 Update, Wed 2017/11/29. Change 1/2 RCP 005/6/7/VP from C2 to C1, C2 The block valves are left open during power. However, should a PORV open and then fail to close, the relevant block valve is required to close. Therefore, the failure of the block valve on its own will have no direct plant consequences but there are OTS limitations as the plant may have to fallback to SD / RRA within 1 hour. However, if there is a failure of the block valve to close when it is required with a PORV stuck open, then it can result in an immediate reactor trip. Therefore, the ER classification of 1/2 RCP 005/006/007 VP should be changed from C2 to C1/C2. | CHS
1 | RCP |  |  |  | E0709 | 1RCP215VP | [10 empty] | B0046 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: RCP to RRA train A interconnection valve Failure analysis and classification: Valve used when entering (or leaving RRA) conditions Valve exposed to high pressure => A2 - Failure to function or pass leak tightness test on start up could/will require outage repair time > 12h => C2,C8,C9,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RCP |  |  |  | D0103 | 1RCP212VP | [10 empty] | B0047 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: RCP to RRA train B interconnection valve Failure analysis and classification: Valve used when entering (or leaving RRA) conditions Valve exposed to high pressure => A2 - Failure to function or pass leak tightness test on start up could/will require outage repair time > 12h => C2,C8,C9,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RCV |  |  |  | 1LLD0412 | 1RCV005PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 002 PO Failure analysis and classification: Analysis based on RCV 002 PO is the standby Train B pump. Component seldom in service Component required when 002 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => C3 RPR test requirement - 2 monthly, any domain - 005 PO start test - failure => C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
1 | RCV |  |  |  | 1LLD0512 | 1RCV034VP | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To CLOSE/OPEN charging pumps suction from 002 BA. Failure analysis and classification: Valve normally OPEN. - Failure to CLOSE when require will result in incorrect valves configuration during SI and on 002 BA level LO3 => C3,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 RPR test requirement - 2 monthly, any domain - cLosure test - failure => C3,S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | 1LLC0508 | 1RCV004PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 001 PO Failure analysis and classification: Analysis based on 001 PO AND that 003 PO is operable Component required when 001 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => NO C3 RPR test requirement - 2 monthly, any domain - 004 PO start test - failure => NO C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
1 | RCV |  |  |  | 1LLD0511 | 1RCV048VP | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate charging line - CI - outside containment, pen 260 Valve normally OPEN and under high pressure. Require to CLOSE on SI train B => A2 - Valve failure to OPEN during outage, normal ops and during incident/accident => C3,C8,C9,S4,E5,E6 - Valve failure to CLOSE on SI will result in safety function degradation and impair ability to preform steps from incident/accident procedure => C6,C7,C8,C9,S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM test requirement - 1 or 3RO LLRT test - outage => C2 Component tested - 1 RO - SHUTDOWN IN PROGRESS, RCP AT 300 kPa, OPS PT KWB-PT-RCV-285 "AUTOMATIC LETDOWN LINE ISOLATION TEST" => C3 Component tested - 1 RO - Temp < 60°C - OPS PT KWB-PT-RIS-259 "SAFETY INJECTION SYSTEM OVERALL TEST FOR TRAIN B" => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
1 | RCV |  |  |  | 1LLC0507 | 1RCV006PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 003 PO Failure analysis and classification: Analysis based on 003 PO AND that 001 PO is operable Component required when 003 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => NO C3 RPR test requirement - 2 monthly, any domain - 006 PO start test - failure => NO C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
1 | RCV |  |  |  | 1LLC0506 | 1RCV033VP | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To CLOSE/OPEN charging pumps suction from 002 BA. Failure analysis and classification: Valve normally OPEN. - Failure to CLOSE when require will result in incorrect valves configuration during SI and on 002 BA level LO3 => C3,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 RPR test requirement - 2 monthly, any domain - cLosure test - failure => C3,S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | 1LKC0309 | 1RCV076VP | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 001 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | J1921 | 1RCV050VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate charging line - downstream of 001 EX - inside containment Failure analysis and classification: Valve normally OPEN and under high pressure. Require to CLOSE on SI train A => A2 - Valve failure to OPEN during outage, normal ops and during incident/accident => C3,C8,C9,S4,E5,E6 - Valve failure to CLOSE on SI will result in safety function degradation and impair ability to preform steps from incident/accident procedure =>C6,C8,C9,S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM test requirement - 1RO - outage - stroke time check - S4,E6 Valve tested - 1 RO OPS PT in state 4 - 050 VP AND 227 VP both CLOSED = L/D isolation (007, 008, 009 VP)=> S4 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CHS
1 | RCV |  |  |  | 1LKC0508 | 1RCV077VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 002 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | J2224 | 1RCV088VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: CI - to isolate RCP pumps seal leakoff return line - outside containment Failure analysis and classification: Valve normally OPEN. Require to CLOSE upon CI A - train A - Failure to CLOSE upon CI A train B => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing on CI Ph A - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing time test - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | 1LKC0507 | 1RCV078VP | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 003 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | 1LLC0503 | 1RCV060VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate common seal injection line to RCP pumps - upstream 003/004 FI Failure analysis and classification: Valve under high pressure, normally OPEN - manually controled from 016 TL, used chiefly during outage => A2 - Valve failure to CLOSE or passing - instruction in procedure I-RRI and LAS 21 where valve is require to CLOSE => C9,S4,E5,E6 - Valve failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
1 | RCV |  |  |  | 1LLD0505 | 1RCV089VP | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: CI - to isolate RCP pumps seal leakoff return line - inside containment Failure analysis and classification: Valve normally OPEN. Require to CLOSE upon CI A - train B - Failure to CLOSE upon CI A train B => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing on CI Ph A - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing time test - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RCV |  |  |  | 1LLD0504 | 1RCV222VP | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HH pumps miniflow line Failure analysis and classification: Valve normally OPEN. Under high pressure. - Failure to CLOSE upon SI signal => C6,C8,C9 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 RPR test requirement - 2 monthly, any domain - closure test - failure => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RCV |  |  |  | 1LLC0602 | 1RCV223VP | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HH pumps miniflow valve Failure analysis and classification: Valve normally OPEN. Under high pressure. - Failure to CLOSE upon SI signal => C6,C8,C9 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 RPR test requirement - 2 monthly, any domain - closure test - failure => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | REA |  |  |  | 1LLD0502 | 1REA210VB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate direct boration line to RCV Failure analysis and classification: Valve normally closed. Require to OPEN upon opening order from TPL. - Failure to open (jammed closed) when require will impair ability to perform steps required by incident/accident procedures => C6,C9,S4,E5,E6 SRSM test requirements - 1 RO - manoeuvrability test from TPL during outage - failure => S4 Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
1 | REA |  |  |  | 1REA001BX | 1REA003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: Boric acid pump Failure analysis and classification: - Pump failure to supply boric acid will require entry into OTS => C3 Failure to function correctly may require outage repair time < 36hrs based on Maintenances repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
1 | REA |  |  |  | 1REA002BX | 1REA004PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: Boric acid pump Failure analysis and classification: - Pump failure to supply boric acid will require entry into OTS => C3 Failure to function correctly may require outage repair time < 36hrs based on Maintenances repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
1 | RIC |  |  |  | B0406 | 1RIC002AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | RIC control panel in the chain of flux at 3.5 m in the BR including the 5 channel paths and associated monitoring. Used to make the monthly flux map. On a failure => Unable to make the flux map => OTS group 2, decrease of power below 50% (C2, C3). Following update of class criteria on 19 Dec 2011, changed S4 to 0 because OTS implication is accounted for by C3. This is applicable to RIC 001 AR as well. | CHM
1 | RIS |  |  |  | C0103 | 1RIS001VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 001 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | G0103 | 1RIS003VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 003 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | C0406 | 1RIS002VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 002 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLE0408 | 1RIS075VB | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump suction line from PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Valve receives confirmation OPENING order upon Train A SI signal. Valve require to CLOSE for second phase of SI (on the recirculation signal from RPR train A and 051 VP fully open). - Failure to OPEN (when require) will result in incorrect valve configuration for normal operation and it will require entry into OTS, with any fallback constraint and during first phase of SI making suction from PTR 001 BA via Train A unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C3,C6,C9,S4,E5,E6 - Failure to CLOSE will result in incorrect valves configuration during SI phase 2. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 ****************************** SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 | CLM
1 | RIS |  |  |  | 1LLD0603 | 1RIS085VB | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump suction line from PTR 001 BA - Train B Failure analysis and classification: Valve normally CLOSED. Valve receives confirmation OPENING order upon Train B SI signal. Valve require to CLOSE for second phase of SI (on the recirculation signal from RPR train B and 052 VP fully open). - Failure to OPEN will result in incorrect valve configuration for normal operation and it will require entry into OTS, with any fallback constraint and during first phase of SI making suction from PTR 001 BA via Train B unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C3,C6,C9,S4,E5,E6 - Failure to CLOSE will result in incorrect valves configuration during SI phase 2. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLE0512 | 1RIS012VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HHSI pumps suction from PTR 001 BA - Train A Failure analysis and classification: Valve normally CLOSED. Require to AUTO OPEN upon SI, RCV 011 MN level Lo3 and ANTIDILUTION from REA. Require to AUTO CLOSE on RPR boosting signal and 077 VP fully OPEN. - Failure to OPEN will result in incorrect valves configuration during SI making suction from PTR 001 BA via Train A unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to CLOSE will result in incorrect valves configuration during SI in boosting mode. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLD0606 | 1RIS013VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HHSI pumps suction from PTR 001 BA - Train B Failure analysis and classification: Valve normally CLOSED. Require to AUTO OPEN upon SI, RCV 012 MN level Lo3 and ANTIDILUTION from REA. Require to AUTO CLOSE on RPR boosting signal and 078 VP fully OPEN. - Failure to OPEN will result in incorrect valves configuration during SI making suction from PTR 001 BA via Train B unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to CLOSE will result in incorrect valves configuration during SI in boosting mode. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLE0511 | 1RIS020VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - HHSI (BIT by-pass) line towards cold legs - penetration 262 - outside containment Valve closed during normal operation. There are no RIS auto actions associated with this valve. High operating pre Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RIS |  |  |  | 1LLD0712 | 1RIS144VP | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train B Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo3 (2.1m) for "Recirculation Configuration". - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon recirculating signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLC0604 | 1RIS021VP | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - HHSI (BIT by-pass) line towards hot legs - penetration 263 - outside containment Valve closed during normal operation. There are no RIS auto actions associated with this valve. High operating pres Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RIS |  |  |  | 1LLD0711 | 1RIS145VP | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 002 PO miniflow line to PTR 001 BA - Train B Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration" (if 078 VP fully OPEN). - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon boosting signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLE0510 | 1RIS032VP | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | HHSI discharge line towards cold legs via 004 BA inlet motorized valve - normally closed Function: To isolate 004BA and open on SI signal. Failure analysis: Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Valve fails to operate as required(open on SI signal).=>C6,C8,C9,E5,E6. Component is tested during the outage; test failure => C2 Component is tested during at power operation for passing; test failure => entry into OTS => C3 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe - (outage) => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLD0607 | 1RIS033VP | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | HHSI discharge line towards cold legs via 004 BA inlet motorized valve - normally closed Function: To isolate 004BA and open on SI signal. Failure analysis: Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Valve fails to operate as required(open on SI signal).=>C6,C8,C9,E5,E6. Component is tested during the outage; test failure => C2 Component is tested during at power operation for passing; test failure => entry into OTS => C3 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe - (outage) => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLE0509 | 1RIS034VP | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 004 BA outlet - penetration 266 - outside containment Valve permanently closed during normal operation. Valve require to open on SI signal. High operating pressure => A2 Valve failure to open Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RIS |  |  |  | 1LLD0608 | 1RIS035VP | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 004 BA outlet - penetration 266 - outside containment Valve permanently closed during normal operation. Valve require to open on SI signal. High operating pressure => A2 Valve failure to open Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RIS |  |  |  | 1LLE0508 | 1RIS051VP | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO suction from 005 BA - penetration 105 - outside containment Valve permanently closed during normal operation. On SI initiation valve remain closed. It is required to open during later stages for SI recircirculation line-up. Function: To provide SI flow (re-circulation)to RCP in event of Safety Injection. Failure analysis: Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLD0609 | 1RIS052VP | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 002 PO suction from 006 BA - penetration 103 - inside containment Valve permanently closed during normal operation. On SI initiation valve remain closed. It require to open during later stage for SI recircirculation line-up. Function: To provide SI flow (re-circulation)to RCP in event of Safety Injection. Failure analysis: Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLE0507 | 1RIS061VP | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO discharge towards RCP cold legs - penetration 104 - outside containment Valve permanently closed during normal operation. Valve is manipulated open/closed while in accident/SAMG proced Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLD0610 | 1RIS062VP | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 002 PO discharge towards RCP cold legs - penetration 207 - outside containment Valve permanently closed during normal operation. Valve is manipulated open/closed while in accident/SAMG proced Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLE0506 | 1RIS063VP | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO discharge towards RCP hot legs - penetration 102 - outside containment. Valve closed during normal operation. It receives opening order on SI signal. Function: To provide SI flow to RCP in event of Safety Injection. Failure analysis: Subject to Hi Press.=>A2. Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLD0611 | 1RIS064VP | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 002 PO discharge towards RCP hot legs - penetration 101 - outside containment Valve permanently closed during normal operation. Valve receives opening order during SI. Function: To provide SI flow to RCP in event of Safety Injection. Failure analysis: Subject to Hi Press.=>A2. Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLE0505 | 1RIS077VP | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump 001 PO discharge line from HHSI pumps suction. Failure analysis and classification: Valve normally CLOSED. Require to OPEN upon Train A SI signal. Valve receives confirmation OPENING order from RPR upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration". - Failure to OPEN will result in degradation of critical safety function or parameter control and it will impair ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C8,C9,S4,S6 - Failure to CLOSE upon manual order from TPL will result in incorrect line-up of the critcal safety function component => C3,S4 - Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM testing requirement - 2 monthly & 1RO - valve correct operation on SI signal with PTR 001 BA Lo2 - Boost phase - (any domain) => C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLD0612 | 1RIS078VP | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump 002 PO discharge line from HHSI pumps suction. Failure analysis and classification: Valve normally CLOSED. Require to OPEN upon Train B SI signal. Valve receives confirmation OPENING order from RPR upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration". - Failure to OPEN will result in degradation of critical safety function or parameter control and it will impair ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C8,C9,S4,S6 - Failure to CLOSE upon manual order from TPL will result in incorrect line-up of the critcal safety function component => C3,S4 - Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM testing requirement - 2 monthly & 1RO - valve correct operation on SI signal with PTR 001 BA Lo2 - Boost phase - (any domain) => C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RIS |  |  |  | 1LLE0504 | 1RIS132VP | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration" (if 077 VP fully OPEN). - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon boosting signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RIS |  |  |  | 1LLE0503 | 1RIS133VP | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo3 (2.1m) for "Recirculation Configuration". - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon recirculating signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RPE |  |  |  | E0709 | 1RPE014PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Pump Function: Discharge from 003 BA Failure analysis and classification: -- Pump failure to function correctly during outage (draining or venting) could be repaired > 36 h => therefore NO C2 -- Pump failure to function correctly during normal operation will make defeat purpose of 003 BA (to collect, quantify and evacuate the effluence) => C9 (003 BA intended for leaks calculations - referenced in accident/incident procedures) When is service the bushes wear and if not maintained lead to shaft shear and impellor damage => E6 | CLM
1 | RRA |  |  |  | D0406 | 1RRA001VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate inlet line from RCP - Train A Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 SRSM test requirement - 1 RO - verify closed interlock @ P>2,8MPa - outage => S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RRA |  |  |  | E0103 | 1RRA015VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate discharge line towards RCP loop 3 cold leg - Train B Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 Valve used duriung outages - evident failure Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RRA |  |  |  | D1416 | 1RRA014VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate discharge line towards RCP loop 1 cold leg - Train A Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 Valve used duriung outages - evident failure Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RRA |  |  |  | E1012 | 1RRA021VP | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate inlet line from RCP - Train B Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 SRSM test requirement - 1 RO - verify closed interlock @ P>2,8MPa - outage => S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
1 | RRI |  |  |  | 1LLJ0303 | 1RRI040VN | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train B RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0302 | 1RRI059VN | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train B RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0301 | 1RRI170VN | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RRM coolers - outside containment Component permanently open during normal operation. SRSM requirement - Closing on CIB + stroke time - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLJ0401 | 1RRI177VN | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line to RRM coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | B0103 | 1RRI019VN | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate outlet line from RRA 001 RF - CI - inside containment, pen 215 Failure analysis and classification: Valve normally CLOSED. - Valve failure to OPEN when RRA require during incident/accident condition will result in degradation of critical safety function or parameter control => C6,C8,C9,S4,E5,E6 - Valve failure to OPEN when RRA require for cooldown will result in an unplanned OTS event, with any fallback constraint => C3 - Valve failure to remain CLOSED (leak tight) will result in degradation of containment (penetration) integrity => C7 - Valve malfunction during the outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly closing test (RPR)KWB-PT-12-RPR-125 - normal operation - PT failure => C3 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | E0406 | 1RRI020VN | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate outlet line from RRA 002 RF - CI - inside containment, pen 216 Failure analysis and classification: Valve normally CLOSED. - Valve failure to OPEN when RRA require during incident/accident condition will result in degradation of critical safety function or parameter control => C6,C8,C9,S4,E5,E6 - Valve failure to OPEN when RRA require for cooldown will result in an unplanned OTS event, with any fallback constraint => C3 - Valve failure to remain CLOSED (leak tight) will result in degradation of containment (penetration) integrity => C7 - Valve malfunction during the outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly closing test (RPR)KWB-PT-12-RPR-125 - normal operation - PT failure => C3 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | J0103 | 1RRI189VN | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RRM return line - penetration 211 - inside containment Function: Normally open. Used for RRM operations, CI valve. Failure analysis: Valve fails to open:=>C8,C9,E5,E6 Valve fails to close/pass PT's/remain leak tight as required:=>C3,C7,E5,E6 Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | 1LLJ0402 | 1RRI210VN | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 001 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | J0406 | 1RRI280VN | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 001 PO return line - penetration 202a - inside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0403 | 1RRI211VN | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 002 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | J0709 | 1RRI281VN | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 002 POreturn line - penetration 202b - inside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0404 | 1RRI212VN | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 003 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | J1012 | 1RRI282VN | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 003 PO return line - penetration 209 - inside containment Function: Cont isol valve. To supply RRI to RCP motor cooling Failure analysis: Valve fails to open:=>C3,C6,C7,E5,E6,I4. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,E5,E6,I4. Failure to function correctly should need an outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0405 | 1RRI283VN | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 001 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB + stroke time - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLJ0406 | 1RRI284VN | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 002 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLJ0407 | 1RRI285VN | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 003 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLE0501 | 1RRI041VN | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train A RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0408 | 1RRI300VN | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 002 BA & 021 RF - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - LLRT - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLE0601 | 1RRI058VN | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train A RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLJ0409 | 1RRI304VN | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 002 BA - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | 1LLE0602 | 1RRI146VN | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate RRI flow to DEG. Failure analysis and classification: Valve permanently OPEN. Used for leak finding and maintenence activity. - Valve failure to OPEN valve will result in loss of RRI cooling to DEG and suseqent EVC and EVR temperatures increase => S4,E5,E6. - Valve failure to function OPERN/CLOSED will impaire ability to perform steps required by incident/accident procedures => C9 - Valve failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | 1LLJ0410 | 1RRI313VN | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 021 RF - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
1 | RRI |  |  |  | J1315 | 1RRI318VN | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 002 BA return line - penetration 208b - inside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRI |  |  |  | 1LLD0706 | 1RRI551VN | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate RRI flow to DEG. Failure analysis and classification: Valve permanently OPEN. Used for leak finding and maintenence activity. - Valve failure to OPEN valve will result in loss of RRI cooling to DEG and suseqent EVC and EVR temperatures increase => S4,E5,E6. - Valve failure to function OPERN/CLOSED will impaire ability to perform steps required by incident/accident procedures => C9 - Valve failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | J1618 | 1RRI319VN | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCV 021 RF return line - penetration 208c - outside containment Normal operation - valve OPEN. Function: Cont isol valve. To supply RRI to RCP/RCV cooling Failure analysis: Valve fails to open:=>C3,C6,C7,E5,E6,I4. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,E5,E6,I4. Failure to function correctly should need an outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
1 | RRI |  |  |  | 1LLE0609 | 1RRI465VN | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve RRI465VN Function: To isolate RRI common inlet line to the REN/RCV coolers Failure analysis and classification: Failure of valve to operate = unable to isolate sections of supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair operations required by accident/incident procedures (I-RRI) => C9,E6 | CLM
1 | RRI |  |  |  | 1LLE0610 | 1RRI466VN | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve RRI466VN Function: To isolate RRI common inlet line to the REN/RCV coolers Failure analysis and classification: Failure of valve to operate = unable to isolate sections of supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair operations required by accident/incident procedures (I-RRI) => C9,E6 | CLM
1 | RRM |  |  |  | DKH | 1RRM001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRM |  |  |  | DFH | 1RRM002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRM |  |  |  | DHF | 1RRM003ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | RRM |  |  |  | ADG | 1RRM004ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | SAP |  |  |  | 1LLI0201 | 1SAP101CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air compressor - train A, emergency, piston. Unavailability will result in loss of redundancy and defence in depth => S4. Component failure could impair steps in the incident and accident procedures. => C9 | CLM
1 | SAP |  |  |  | 1LLJ0201 | 1SAP102CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Air compressor - train B, emergency, piston. Unavailability will result in loss of redundancy and defence in depth => S4. Component failure could impair steps in the incident and accident procedures. => C9 | CLM
1 | SAR |  |  |  | 1LLB0503 | 1SAR432VA | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - supply line - penetration 203a - outside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could cause outage delay (repair time) > Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
1 | SEC |  |  |  | 1LLE0612 | 1SEC001MO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
1 | SEC |  |  |  | 1LLB0501 | 1SEC002MO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
1 | SEC |  |  |  | 1LLE0712 | 1SEC003MO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
1 | SEC |  |  |  | 1LLB0601 | 1SEC004MO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
1 | SEC |  |  |  | 9LKX002CR | 1SEC201VE | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve Function: CFI isolation to both units SEC Train A & B pumps suction manifold. Failure analysis and classification: Valve closed during normal operation. Installed in corrosive environment => A6 -- Failure to open will impair ability to perform steps required by incident/accident procedures => C9 -- Failure to isolate will effect interconnection manifold dry conservation => E5 | CLS
1 | SEC |  |  |  | 9LKX002CR | 1SEC201VE | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2019/124 |  | 2 RO | 124 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve Function: CFI isolation to both units SEC Train A & B pumps suction manifold. Failure analysis and classification: Valve closed during normal operation. Installed in corrosive environment => A6 -- Failure to open will impair ability to perform steps required by incident/accident procedures => C9 -- Failure to isolate will effect interconnection manifold dry conservation => E5 | CLS
2 | ASG |  |  |  | 2ASG005CR | 2ASG055CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Sensor supply (Sn ..) -> Consideration of the worst case. | CHM
2 | KRG |  |  |  | 2KRG024CR | 2KRG023AR | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
2 | KRG |  |  |  | 2KRG035CR | 2KRG034AR | [10 empty] | B0901 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
2 | KRG |  |  |  | 2KRG046CR | 2KRG042AR | [10 empty] | B0902 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
2 | LNE |  |  |  | 2LNE100CR | 2PTR100EN | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet - supply to 1KSC desk recorders. All cabinets are classified as RTF. | RTM | Recorder for SFP level/temperature/heat exchanger temperature. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LTP |  |  |  | 2LTP001TB | 2LTP007TB | [10 empty] | B0904 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM | Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM
2 | LTP |  |  |  | 2LTP001TB | 2LTP008TB | [10 empty] | B0905 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM | Switchboard Function: Auxiliary power network. Failure analysis and classification: Switchboard used during outages(Assumption that board is in use during an outage) -- Failure to supply essential equipment during outage will result in outage repair time > 12 h => C2,S4 | CLM
2 | ASG |  |  |  | 2ASG065UB | 2ASG055CR | [10 empty] | B0644 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Sensor supply (Sn ..) -> Consideration of the worst case. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP214VA | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP214VA | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP215VA | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h=> C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP215VA | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h=> C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP216VA | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP216VA | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP201AR | 2EPP220VA | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | EPP |  |  |  | 2EPP201AR | 2EPP220VA | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | EPP |  |  |  | 2EPP101AR | 2EPP114VA | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP114VA | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for main control air supply to 8m airlock control mechanism. Valve used to isolate control air supply to airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP115VA | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP115VA | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for control air exhaust from 8m airlock control mechanism. Valve used to exhaust control air from the airlock. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP116VA | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP116VA | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Solenoid valve for door seal test between containment and 8m airlock door seals. Valve used for testing of the airlock door seals. Valve cycled frequently during RO as long as airlock is in use. => I2 SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | EPP |  |  |  | 2EPP101AR | 2EPP120VA | [10 empty] | B0334 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | EPP |  |  |  | 2EPP101AR | 2EPP120VA | [10 empty] | B0335 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM | Isolation solenoid valve on 8m airlock safety valve . Valve isolates the airlock safety valve line inside the airlock. SRSM requirement - 1RO LLRT- outage repair time > 12 h => C2 Valve failure could degrade containment integrity OTS. => C3,C7 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | KRG |  |  |  | 2KRG032AR | 2KRG031AR | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet Function: To house specified instrumentation and control equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified instrumentation and control equipment (with trigrammes) are classified => RTM | RTM | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
2 | KRG |  |  |  | 2KRG032AR | 2KRG034AR | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet Function: To house specified instrumentation and control equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified instrumentation and control equipment (with trigrammes) are classified => RTM | RTM | TRICASTIN CLASSIFICATION USED SIP protection cabinet Concerns also conversion circuits. Contains racks and backplane connectors Distribution of 28V fuse on failure -> On Partial loss -> Arming of a reactor protection -> C5 On Failure -> risk of AAR by loss of a control signal (eg Leve | CLM
2 | KRT |  |  |  | 2KRT045CR | 2KRT003PO | [10 empty] | B0701 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply samples to radiation detector Failure analysis and classification: Component always in service => I1,I4 Failure will result in loss of post accident sampling => C9,E6 | CHM
2 | KRT |  |  |  | 2KRT001AR | 2KRT001TB | [10 empty] | B0798 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RCV403EN | [10 empty] | B0305 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for RCP pumps seal leakoff. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RRA401EN | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for RRA heat exchanger inlet and outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2KSC401EN | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG1 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2KSC402EN | [10 empty] | B0310 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG2 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2KSC403EN | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG3 steam and feedwater flowrate. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2LNA001DL | 2KPR401EN | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 | CHM | Recorder for RCP pressure, Hot and Cold leg, and RRA exchanger outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RGL401EN | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for rod bank A/B travel limitation and demand position. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RGL402EN | [10 empty] | B0316 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for rod bank C/D travel limitation and demand position. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RGL403EN | [10 empty] | B0317 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for auctioneered T-AVG and T-REF. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2KSC405EN | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Loop 1 temp gradient and RCP deviation temperature. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2ARE401EN | [10 empty] | B0319 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG1 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2ARE402EN | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG2 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2ARE403EN | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for SG3 narrow and wide range level. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RCV401EN | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for VCT level and pressure. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2KSC404EN | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for charging and letdown temperature. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2LNA001DL | 2RPN001AR | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 | CHM | The cabinet houses the following channels and components: 1. Source Range - 014MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 013MA (1oo2 trip logic when in service below P10) 3. Power Range - 010MA (2 oo 4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 010MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
2 | LNI |  |  |  | 2LNA001DL | 2RPN001AR | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 | CHM | The cabinet houses the following channels and components: 1. Source Range - 014MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 013MA (1oo2 trip logic when in service below P10) 3. Power Range - 010MA (2 oo 4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 010MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
2 | LNI |  |  |  | 2LNB001DL | 2RPN002AR | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNB feeder diagram indicates that loss of LNB001DL will result in loss of LNB001TB. Therefore the loss of LNB001DL shall have the same classification as LNB001TB => C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. | CHM | The cabinet houses the following channels and components: 1. Source Range - 024MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 023MA (1oo2 trip logic when in service below P10) 3. Power Range - 020MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 020MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
2 | LNI |  |  |  | 2LNB001DL | 2RPN002AR | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNB feeder diagram indicates that loss of LNB001DL will result in loss of LNB001TB. Therefore the loss of LNB001DL shall have the same classification as LNB001TB => C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. | CHM | The cabinet houses the following channels and components: 1. Source Range - 024MA (1oo2 trip logic when in service below P6) 2. Intermediate Range - 023MA (1oo2 trip logic when in service below P10) 3. Power Range - 020MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 020MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals | CHM
2 | LNI |  |  |  | 2LNC001DL | 2RPN003AR | [10 empty] | B0339 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the the following channels and components: 1. Power Distribution 036MA 2. Power Comparison 035MA 3. Power Range - 030MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 030MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNI |  |  |  | 2LNC001DL | 2RPN003AR | [10 empty] | B0340 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per the System Engineer's review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the the following channels and components: 1. Power Distribution 036MA 2. Power Comparison 035MA 3. Power Range - 030MA (2oo4 trip logic when in service) . 4. HV supply for CBL-15 Ionisation chamber - 030MA. 5. 48V power supply for protection outputs. 6. 48V power supply for control outputs 7. Relay panels. 8. Electromagnetic solenoids for interlocking the channel draws. 9. Selector switches and indications 10. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNI |  |  |  | 2LND001DL | 2RPN004AR | [10 empty] | B0348 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per System Engineer review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the following channels and components: 1. Audio Countrate 045MA 2. Power Range - 040MA (2oo4 trip logic when in service) . 3. HV supply for CBL-15 Ionisation chamber - 040MA. 4. 48V power supply for protection outputs. 5. 48V power supply for control outputs 6. Relay panels. 7. Electromagnetic solenoids for interlocking the channel draws. 8. Selector switches and indications 9. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNI |  |  |  | 2LND001DL | 2RPN004AR | [10 empty] | B0349 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per System Engineer review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | The cabinet houses the following channels and components: 1. Audio Countrate 045MA 2. Power Range - 040MA (2oo4 trip logic when in service) . 3. HV supply for CBL-15 Ionisation chamber - 040MA. 4. 48V power supply for protection outputs. 5. 48V power supply for control outputs 6. Relay panels. 7. Electromagnetic solenoids for interlocking the channel draws. 8. Selector switches and indications 9. Input and output terminals Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN402EN | [10 empty] | B0351 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Upper Neutron Flux Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN403EN | [10 empty] | B0352 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Upper Neutron Flux Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN404EN | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Lower Neutron Flux Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN405EN | [10 empty] | B0354 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Lower Neutron Flux Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN406EN | [10 empty] | B0355 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Average Flux Power Range Channel 1 and 2. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC001CR | 2RPN407EN | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Average Flux Power Range Channel 3 and 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RPN401EN | [10 empty] | B0357 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Delta Neutron Flux A 1 or 3 and B 2 or 4. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RPN408EN | [10 empty] | B0358 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for Reactor Power and Delta Flux - Delta Flux Ref. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP473ID | [10 empty] | B0359 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Panel indicator Function: Indication Failure analysis and classification: Component permanently in service. => I1 Fails to provide information required by for incident/accident procedure(s) => C9 Maintenance is required to prevent degradation of the component. => E6 | CHM
2 | LNI |  |  |  | 2KSC001CR | 2KSC412EN | [10 empty] | B0362 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Recorder for RRA/RCV safety valve outlet temperatures. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. The recorder is required for monitoring during the application of incident/accident procedures or SAMGs => C9. | CHM
2 | LNI |  |  |  | 2LNA001DL | 2RIC011AR | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNA feeder diagram indicates that loss of LNA001DL will result in loss of LNA001TB. Therefore the loss of LNA001DL shall have the same classification as LNA001TB => C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 | CHM | Core Cooling Monitor Train A. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
2 | LNI |  |  |  | 2LND001DL | 2RIC012AR | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Review of the LNC feeder diagram indicates that loss of LNC001DL will result in loss of LNC001TB. Therefore the loss of LNC001DL shall have the same classification as LNC001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 E3=>YES as per System Engineer review. C1=>YES (following SPV evaluation by System Engineering - SPV 35971) | CHM | Core Cooling Monitor Train B. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
2 | LNI |  |  |  | 2RIC001AR | 2RIC011AR | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM | Core Cooling Monitor Train A. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
2 | LNI |  |  |  | 2RIC001AR | 2RIC012AR | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM | Core Cooling Monitor Train B. Not included in OTS. All 51 thermocouples from the vessel head as well as Cold Junction temperatures 1 RIC 053 to 058 feed into CCM (26 Train A, 26 Train B). Total Failure of the CCM (i.e. both trains) means operator does not have an immediate display of the Tsat. Burden on Operator who would need to perform manual calculations during an accident or incident, hence C9. CCM spares are obsolete and replacement is costly, very little maintenance possible to maintain long term health and reliability E1, E3, E4 & I-1. | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0304 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0305 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0306 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0307 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM002TB | [10 empty] | B0310 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM002TB | 2RGL001AR | [10 empty] | B0314 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | RAM |  |  |  | 2RAM002TB | 2RGL003AR | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RAM |  |  |  | 2RAM002TB | 2RGL004AR | [10 empty] | B0316 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RAM |  |  |  | 2RAM002TB | 2RGL005AR | [10 empty] | B0317 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RAM |  |  |  | 2RAM002TB | 2RGL006AR | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RAM |  |  |  | 2RAM501BN | 2RAM002TB | [10 empty] | B0319 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0320 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002TB | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RAM |  |  |  | 2RAM501BN | 2RAM002TB | [10 empty] | B0338 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM
2 | RGL |  |  |  | 2RGL001PJ | 2RGL001BK | [10 empty] | B0300 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL002PJ | 2RGL002BK | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL003PJ | 2RGL003BK | [10 empty] | B0306 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL004PJ | 2RGL004BK | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL017PJ | 2RGL017BK | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL018PJ | 2RGL018BK | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL019PJ | 2RGL019BK | [10 empty] | B0318 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL020PJ | 2RGL020BK | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL009PJ | 2RGL009BK | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL010PJ | 2RGL010BK | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL011PJ | 2RGL011BK | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL012PJ | 2RGL012BK | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL005AR | 2RGL002AR | [10 empty] | B0336 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL002AR | [10 empty] | B0337 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL002AR | [10 empty] | B0338 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL001AR | [10 empty] | B0342 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0343 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0344 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0345 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0346 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0347 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0348 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0349 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL021PJ | 2RGL021BK | [10 empty] | B0350 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL022PJ | 2RGL022BK | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL023PJ | 2RGL023BK | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL024PJ | 2RGL024BK | [10 empty] | B0359 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL005PJ | 2RGL005BK | [10 empty] | B0362 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL006PJ | 2RGL006BK | [10 empty] | B0365 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL007PJ | 2RGL007BK | [10 empty] | B0368 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL008PJ | 2RGL008BK | [10 empty] | B0371 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL013PJ | 2RGL013BK | [10 empty] | B0374 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL014PJ | 2RGL014BK | [10 empty] | B0377 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL015PJ | 2RGL015BK | [10 empty] | B0380 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL016PJ | 2RGL016BK | [10 empty] | B0383 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0386 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0387 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0388 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0389 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0390 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0391 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0392 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0393 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0394 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0395 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0396 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0397 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0398 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0399 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL041PJ | 2RGL041BK | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL042PJ | 2RGL042BK | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL043PJ | 2RGL043BK | [10 empty] | B0406 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL044PJ | 2RGL044BK | [10 empty] | B0409 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL025PJ | 2RGL025BK | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL026PJ | 2RGL026BK | [10 empty] | B0415 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL027PJ | 2RGL027BK | [10 empty] | B0418 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL028PJ | 2RGL028BK | [10 empty] | B0421 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL033PJ | 2RGL033BK | [10 empty] | B0424 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL034PJ | 2RGL034BK | [10 empty] | B0427 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL035PJ | 2RGL035BK | [10 empty] | B0430 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL036PJ | 2RGL036BK | [10 empty] | B0433 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL037PJ | 2RGL037BK | [10 empty] | B0436 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL038PJ | 2RGL038BK | [10 empty] | B0439 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL039PJ | 2RGL039BK | [10 empty] | B0442 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL040PJ | 2RGL040BK | [10 empty] | B0445 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0448 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0449 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL029PJ | 2RGL029BK | [10 empty] | B0462 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL030PJ | 2RGL030BK | [10 empty] | B0465 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL031PJ | 2RGL031BK | [10 empty] | B0468 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL032PJ | 2RGL032BK | [10 empty] | B0471 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL045PJ | 2RGL045BK | [10 empty] | B0474 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL046PJ | 2RGL046BK | [10 empty] | B0477 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL047PJ | 2RGL047BK | [10 empty] | B0480 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL048PJ | 2RGL048BK | [10 empty] | B0483 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Coil Function: Control. Failure analysis and classification: A functional failure of the component may result in an immediate automatic Reactor trip, from any standard operating state => C1 A functional failure of the component may result in an immediate production loss of greater than 20% power =>C2 A functional failure of the component result in degradation of the capability to shut down the reactor, or to maintain the reactor at cold shutdown =>C8 A functional failure of the component may result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines =>C9 A functional failure of the component may result in a continuous overload/burden for the operating personnel (In the control room or at local plant or equipment =>S2 A functional failure of the component may result in an unplanned power transient (sustained generation loss), or a reduction in necessary redundancies (not periodically tested), or a reduction of “defence in depth” =>S4 A functional failure of the component result may in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 There are economic reasons to perform preventive maintenance on the component, rather than to let it degrade => E6. The component is continuously in service and cycled frequently => I1,I2 The component is under electric tension, frequently or continuously => I-4 The component exposed to continuous irradiation in excess of 10 mSv/h, during normal operation => A5 | CHS
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0489 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0490 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0491 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0492 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0493 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0494 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0495 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0496 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0497 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0498 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0499 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL003AR | [10 empty] | B0500 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL003AR | [10 empty] | B0501 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0504 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0505 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL004AR | 2RGL006AR | [10 empty] | B0506 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RGL |  |  |  | 2RGL005AR | 2RGL006AR | [10 empty] | B0507 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RPB |  |  |  | 2RPB001TB | 2RGL002AR | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RPB |  |  |  | 2RPB001TB | 2RGL002AR | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | RPB |  |  |  | 2RPB001TB | 2RGL002AR | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: 260 Vac Switchboard Function: Scram breaker - 260 Vac to RGL - TRAIN B. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 260 Vac to RGL will result in RX Trip => C1,C2,C9,S4,E6 | CHM | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | APG |  |  |  | 2LKC0412 | 2APG010VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate APG when required - downstream of 001 RF Failure analysis and classification: Valve should close upon the following:- Demin high temp (>60ºC) = damage to resins => E5,E6. High pressure (P>14bar) or Temp (80ºC) => E5,E6. Shall valve fail to open, APG will not be in available - chemistry limits and spec's exceeded => C2,C3,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | APP |  |  |  | 2APP003CR | 2APP001VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED And synoptic information on the KIT VALVE POSITION -> RTF | RTM | Motor operated isolation valve Function: 001 PO suction - upstream 001 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
2 | APP |  |  |  | 2APP004CR | 2APP003VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 001PO suction - downstream 001 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable =>C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6,E5. -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
2 | APP |  |  |  | 2APP007CR | 2APP005VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 001PO discharge - feed line after 004 VL Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6,E5. -- Isolation valves normally open/closed during unit operation on high pressure systems (above 7 MPa), and not intended for operation other than PTW isolation are classified as E6,A2 | CLS
2 | APP |  |  |  | 2APP005CR | 2APP011VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 002 PO suction - upstream 002 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6,E5 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as E6 | CLM
2 | APP |  |  |  | 2APP006CR | 2APP013VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED Box (static device and visually identifiable default) -> RTF | RTM | Motor operated isolation valve Function: 002 PO suction - downstream 002 FI Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 4 MPa), and not intended for operation other than PTW isolation are classified as=> E5, E6 | CLM
2 | APP |  |  |  | 2APP008CR | 2APP015VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 002 PO discharge - feed line after 014 VL Failure analysis and classification: Valve open in normal operation. -- Failure to open after maintenance activity will render pump unavailable => C9,S4 -- Failure to close for maintenance will delay PTW implementation => E5,E6 -- Isolation valves normally open/closed during unit operation on high pressure systems (above 7 MPa), and not intended for operation other than PTW isolation are classified as E6,A2 | CLS
2 | ARE |  |  |  | 2ARE103CR | 2ARE029VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 002 GV (upstream control valve 032 VL). Failure analysis and classification: Locally operated valve from 103 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
2 | ARE |  |  |  | 2ARE102CR | 2ARE028VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 001 GV (upstream control valve 031 VL). Failure analysis and classification: Locally operated valve from 102 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
2 | ARE |  |  |  | 2ARE101CR | 2ARE030VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor isolation valve Function: Isolates main feed line to 003 GV (upstream control valve 033 VL). Failure analysis and classification: Locally operated valve from 101 CR. Valve normally in OPEN position and is not intended for any procedural manipulation during unit operation. Exposed to pressures in excess of 7 MPa during startup => E6,A2. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CLS
2 | ARE |  |  |  | 2LKA0405 | 2ARE036VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 003 GV - downstream of 033VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
2 | ARE |  |  |  | 2LKC0411 | 2ARE034VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 001 GV - downstream of 031 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
2 | ARE |  |  |  | 2LKA0407 | 2ARE035VL | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater line to 002 GV - downstream of 032 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 | CLS
2 | ARE |  |  |  | 2LKA0406 | 2ARE247VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 003 GV - downstream of 244 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
2 | ARE |  |  |  | 2LKC0408 | 2ARE245VL | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 001 GV - downstream of 242 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
2 | ARE |  |  |  | 2LKA0408 | 2ARE246VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve. Function: To isolate feedwater by-pass line to 002 GV - downstream of 243 VL Failure analysis and classification: Valve open during normal unit operation and exposed to pressure in excess of 7 MPa during startup => E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to function correctly during power operation shall be classified as => C2,C8,C9,S4,E5 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
2 | ASG |  |  |  | 2LLA0312 | 2ASG012PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG001 PO. Function: Supplies lube oil to 001PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
2 | ASG |  |  |  | 2LLB0310 | 2ASG022PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG002 PO. Function: Supplies lube oil to 002 PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
2 | ASG |  |  |  | 2LKH0202 | 2ASG032PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor driven lube oil pump for ASG003 PO. Function: Supplies lube oil to 003 PO bearings. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The pump is started daily to form a lubricating oil film on the pump bearings in case of an automatic start. Failure of the pump during a periodic test or during a routine start would make the pump inoperable and require entry into OTS. => C3 Failure of the pump could lead to damage of the pump shaft and bearings. => E5 | CLM
2 | CFI |  |  |  | 9LKX002CR | 2CFI111VC | [10 empty] | B0061 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 001 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | CFI |  |  |  | 9LKX002CR | 2CFI112VC | [10 empty] | B0062 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 002 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | CFI |  |  |  | 9LKX002CR | 2CFI113VC | [10 empty] | B0063 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 003 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | CFI |  |  |  | 9LKX002CR | 2CFI111VC | [10 empty] | B0064 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 001 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | CFI |  |  |  | 9LKX002CR | 2CFI112VC | [10 empty] | B0065 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 002 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | CFI |  |  |  | 9LKX002CR | 2CFI113VC | [10 empty] | B0066 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM | Motor operated isolation valve - SEC suction from 003 TF Valve refered to accidents/incidents procedures =>C9 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CLS
2 | DEG |  |  |  | 2LLB0308 | 2DEG013VD | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG supply line to containment - outside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
2 | DEG |  |  |  | 2LLB0307 | 2DEG045VD | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG return line from containment - outside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
2 | DEG |  |  |  | D0911 | 2DEG044VD | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: C/I valve on DEG return line from containment - inside cont. Failure analysis and classification: Valve continuously open during normal operation. Valve require to close upon CI phase A Known (verified) inoperability in "when require operating state" will necessitate entry into OTS => C3 Failure to close upon CI phase A (incident/accident condition) will affect containment integrity => C7,C9 SRSM requirement - 1 or 3RO LLRT- outage - failure will require repair time > 36 h => S7,S4,E6 SRSM requirement - 3RO verify operation from TPL - outage - failure may require repair time < 36 h => S4,E6 | CLM
2 | DMK |  |  |  | 2DMK003BX | 2DMK003PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. 2017/11/07 The failure of the DMK crane can have dire consequences for the spent-fuel pool if it drops a cask.=>C6 (Emmanuel Lamprecht - 26 October 2017) A PSA study done for the cask-licensing project for cask-drop accidents indicate that the failure of the DMK crane is a major risk at Koeberg, because – contrary to popular belief – the fuel building is not designed to handle cask drops into the cask-loading cell or cask-cleaning cell. Certain documents (e.g., KBA00A1C01027) state that the floors of these cells are designed for drops from maximum height into these cells, but then they also state that these drops are not design loads for the building because of the safety features built into the crane. However, minutes of a technical meeting held at Velizy (Koeberg Document Number 20624) between representatives from ESCOM, the AEB, FRAMATEG and SPIE-Batignolles, confirm that ESCOM accepted that the abovementioned drop incidents are not design loads for the building. Hence, we cannot rely on the building to retain the integrity of the SFP in the event of drops from the maximum height into these cells. A 0.5 m (yes, fifty centimeters) drop is included in the load-cases for the building because the crane overspeed detection & braking mechanisms are ineffective at low heights like this. | CLM
2 | DSC |  |  |  | 2DSP002AR | 2DSC001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
2 | DSD |  |  |  | 2LLO001TR | 2DSDB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSD |  |  |  | 2LLN001TR | 2DSDA01CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSG |  |  |  | 2LLN001TR | 2DSGV01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSK |  |  |  | 2LLO001TR | 2DSKA01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSK |  |  |  | 2LLO001TR | 2DSKE02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLN001TR | 2DSLB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLN001TR | 2DSLE02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLO001TR | 2DSLE03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLN001TR | 2DSLH04CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLN001TR | 2DSLH05CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSL |  |  |  | 2LLO001TR | 2DSLH06CR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSM |  |  |  | 2DSM001AR | 2DSMB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSM |  |  |  | 2DSM001AR | 2DSMC02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSP |  |  |  | 2DSP001AR | 2DSP001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
2 | DSP |  |  |  | 2DSP002AR | 2DSP002CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
2 | DSP |  |  |  | 2LLN001TR | 2DSP001AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
2 | DSP |  |  |  | 2LLO001TR | 2DSP002AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLS
2 | DSR |  |  |  | 2DSR001AR | 2DSRB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => RTM | RTM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DSR |  |  |  | 2DSR001AR | 2DSRG03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => RTM | RTM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DST |  |  |  | 2DSM001AR | 2DST001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DTL |  |  |  | 2DTL004CR | 2DSRB01CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DTL |  |  |  | 2DTL007CR | 2DSRB01CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DTL |  |  |  | 2DTL009CR | 2DSRB01CR | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DTL |  |  |  | 2DTL009CR | 2DSRB01CR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
2 | DVG |  |  |  | 2LLI0307 | 2DVG001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fresh Air Supply Fan - ASG pumps room ventilation inlet fan - Train A Function:Provide cool air o ASG pump room. Failure analsis: Component not in service. Fails to run on request/demand (or during PT) - entry into OTS => C3 SRSM requirement for auto + manual start PSA Significant Component => S6. | CLM
2 | DVG |  |  |  | 2LLJ0311 | 2DVG002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fresh Air Supply Fan - ASG pumps room ventilation inlet fan - Train A Function:Provide cool air o ASG pump room. Failure analsis: Component not in service. Fails to run on request/demand (or during PT) - entry into OTS => C3 SRSM requirement for auto + manual start PSA Significant Component => S6. | CLM
2 | DVG |  |  |  | 2LLI0306 | 2DVG003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
2 | DVG |  |  |  | 2LLJ0310 | 2DVG004ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
2 | DVG |  |  |  | 2LLI0412 | 2DVG003ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
2 | DVG |  |  |  | 2LLJ0411 | 2DVG004ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan-high and low speed supply of fresh air Function: To supply fresh air to CRDM and M/G sets Failure analysis: Component in 50% duty cycle operating regime, fails to run or maintain tempreture within limits while in service (or during PT) - entry into OTS => C3 Component fails to run at different speed => E6 | CLM
2 | DVG |  |  |  | 2DVG011CR | 2DVG001FI | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Suction filter circuitry KVD. Default (fouling): 'I0 GR1 if T ° out criteria -> C3 | CHM
2 | DVH |  |  |  | 2LLA0103 | 2DVH001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - air supply to RCV pump rooms - Train A. Function: To supply cooled air to RCV pump rooms. Failure analysis: Fan 50% in service. Fan failure will result in over-heating of RCV motors/pumps.=>E5 SRSM test requirement - 2 monthly - auto start during RPR PT => C3 | CLM
2 | DVH |  |  |  | 2LLB0105 | 2DVH002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - air supply to RCV pump rooms - Train A. Function: To supply cooled air to RCV pump rooms. Failure analysis: Fan 50% in service. Fan failure will result in over-heating of RCV motors/pumps.=>E5 SRSM test requirement - 2 monthly - auto start during RPR PT => C3 | CLM
2 | DVK |  |  |  | 2LLI0304 | 2DVK005ZV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Iodine exhaust fan - Train A Function:Evacuate air from the fuel building through a Iodine filter system. Failure analysis: Component fails to start;standby fans stars automatically= C9 SRSM requirement - 1RO starting test from manual actuation => NO C3, but => S3 SRSM requirement - 1RO starting test from Train A SI signal SRSM requirement - 1RO starting test from Hi activity KRT 013 or 014 MA => NO C2, but => E6 | CLM
2 | DVK |  |  |  | 2LLJ0308 | 2DVK006ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Iodine exhaust fan - Train B Function:Evacuate air from the fuel building through a Iodine filter system. Failure analysis: Component fails to start;standby fans stars automatically= C9 SRSM requirement - 1RO starting test from manual actuation => NO C3, but => S3 SRSM requirement - 1RO starting test from Train A SI signal SRSM requirement - 1RO starting test from Hi activity KRT 013 or 014 MA => NO C2, but => E6 | CLM
2 | DVS |  |  |  | 2LLA0406 | 2DVS001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air supply fan to EAS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
2 | DVS |  |  |  | 2LLB0409 | 2DVS002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air supply fan to EAS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
2 | DVS |  |  |  | 2LLA0407 | 2DVS003ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air supply fan to RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
2 | DVS |  |  |  | 2LLB0410 | 2DVS004ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air supply fan to RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify fans start stop from selector switch => NO C2 Component failure during accident conditions could prevent access to the motor room for valve actuator manipulation. => C9,E6 | CLM
2 | DWS |  |  |  | 2LLI0403 | 2DWS001RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater electric. Entry into OTS if inoperable => C3,E6. Cycled frequently =>I2. Exposed to sea air => A6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHS
2 | DWS |  |  |  | 2LLD0305 | 2DWS002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater electric. Entry into OTS if inoperable => C3,E6. Cycled frequently =>I2. Exposed to sea air => A6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHS
2 | DWS |  |  |  | 2LLI0404 | 2DWS001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
2 | DWS |  |  |  | 2LLJ0307 | 2DWS002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
2 | DWS |  |  |  | 2LLA0307 | 2DWS003ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
2 | DWS |  |  |  | 2LLB0304 | 2DWS004ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan - supply air. Component 50% in service. Entry into OTS if inoperable => C3,E6. Exposed to sea air => A6. PSA Significant Component => S6. | CLS
2 | EAS |  |  |  | 2LLD0304 | 2EAS002VB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate 001 PO suction from 001 BA - train A - suction from PTR 001 BA. Failure analysis and classification: - Failure to open/remain open will result in unavailabiliry of Train A and if in "when require operating state", OTS entry will require => C3,S4 - Failure to close when PTR tank level reaches 2.1m (during CS if 013 VB open) will result in loss of suction head to 001 PO making Train A unavailable => C6,C7,C9 - SRSM requirement - 2 mthly - verify valve operation (any domain) - PT failure will require entry into OTS => C3,S4 Failure to function during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | EAS |  |  |  | 2LLC0305 | 2EAS001VB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate 001 PO suction from 001 BA - train A - suction from PTR 001 BA. Failure analysis and classification: - Failure to open/remain open will result in unavailabiliry of Train A and if in "when require operating state", OTS entry will require => C3,S4 - Failure to close when PTR tank level reaches 2.1m (during CS if 013 VB open) will result in loss of suction head to 001 PO making Train A unavailable => C6,C7,C9 - SRSM requirement - 2 mthly - verify valve operation (any domain) - PT failure will require entry into OTS => C3,S4 Failure to function during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | EAS |  |  |  | 2LLD0303 | 2EAS008VB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train B EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | EAS |  |  |  | 2LLC0304 | 2EAS007VB | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train A EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | EAS |  |  |  | 2LLD0302 | 2EAS010VB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train B EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | EAS |  |  |  | 2LLC0303 | 2EAS009VB | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve. Function: Train A EAS supply line to containment - outside cont. Failure analysis and classification: Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into EPP OTS => C3 - Failure to open upon CS => C7,C9,S1,S4,E6 - SRSM requirement - 2 mthly PT - normal OPS - verify opening upon CS - failure to function correctly during PT will require entry into OTS => C3 - SRSM requirement - 1 RO PT - outage - verify opening time - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening upon CS - failure to function correctly during PT may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 - SRSM requirement - 1 RO PT - LLRT - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | EAS |  |  |  | 2LLD0301 | 2EAS014VB | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve Function: Suction line to 002 PO from cont. sump 002 PS - outside cont. Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into OTS => C3 - Failure to open upon CS (recirc signal) => C7,C9,S1,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening time & maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | EAS |  |  |  | 2LLC0302 | 2EAS013VB | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated C/I valve Function: Suction line to 001 PO from cont. sump 001 PS - outside cont. Valve continuously closed during normal operation. - Known (verified) malfunction (failure to remain leak tight closed or open when require) will render entry into OTS => C3 - Failure to open upon CS (recirc signal) => C7,C9,S1,S4,E6 - SRSM requirement - 1 RO PT - outage - verify opening time & maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | ETY |  |  |  | 2LKH0403 | 2ETY001RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | O/C - electric heater in the air duct upstream iodine filtration Component energized manually by an operator while placing iodine filtration in service. Component interlocked by 003 SD (lack of flow) and 001 ST (temp Hi). Component failure to energize (KIT 037 EC - OFF) will render iodine line inoperable => C3 Component failure to heat will reduce efficiency of the iodine filter 001 PI => E5 (no temp Lo alarm). SRSM requirement - 1RO verify energizing SRSM requirement - 1RO verify tripping SRSM requirement - 4RO tripping @ 70°C on 001 ST SRSM requirement - 4RO tripping @ Q<1000m³/h (low flow) on 003 SD SRSM requirement - 5RO verify heating capacity NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHM
2 | ETY |  |  |  | 2LLJ0305 | 2ETY002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment air circulation and exhaust fan. Function: Circulate and exhaust containment air. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Component failure when in use will require OTS entry. => C3 Component tested during monthly KWB-PT ETY-070 - failure => C3 | CLM
2 | ETY |  |  |  | 2LLI0406 | 2ETY001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment air circulation and exhaust fan. Function: Circulate and exhaust containment air. Failure analysis and classification: Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Component failure when in use will require OTS entry. => C3 Component tested during monthly KWB-PT ETY-070 - failure => C3 | CLM
2 | GCT |  |  |  | 2LKH0404 | 2GCT100VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 1 & 3 (110,111,118 & 119 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | GCT |  |  |  | 2LKH0405 | 2GCT101VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 2 & 4 (114,115,122 & 123 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | GCT |  |  |  | 2LKH0406 | 2GCT102VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 2 & 4 (112,113,120 & 121 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | GCT |  |  |  | 2LKH0407 | 2GCT103VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to condenser to groups 1 & 3 (116,117,108 & 109 VV). Failure analysis and classification: Valve require to remain open during normal operation. - Failure to OPEN during outage may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to OPEN (or close spuriously) will result in generation of "Steam Dump to Condenser Unavailable" signal to RPA which will arm RX scram upon turbine trip (C8) from power level above P16 (PR > 40%) => C6,S4. - Failure to CLOSE (in the event of steam dump control valve stuck open) will result in loss of GCT to condenser and cause automatic MSIV isolation due to excessive cool down => C6,C9,E5,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | GCT |  |  |  | 2LLA0510 | 2GCT128VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 1 Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 131 VV . Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 131 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
2 | GCT |  |  |  | 2LLC0405 | 2GCT129VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 2. Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 132 VV. Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 132 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
2 | GCT |  |  |  | 2LLI0407 | 2GCT130VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate steam dump to atmosphere - Line 2. Failure analysis and classification: Valve remain open during power operation. Sole pupose of this valve is to isolate steam flow upstream of steam flow control valve 133 VV. Component exposed to high pressure at startup => A2 - Known (verified) malfunction (failure to close or leak tight when require) will render entry into OTS => C3 - Failure to close (shall 133 VV fail to close after relief or remain tight) will result in the "steam line break event" => C4,C8,C9 - Failure to function during outage will/could require repair time > 36 hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 | CLS
2 | GEX |  |  |  | 2GEX001AR | 2GEX002AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: All enclosures and cabinets hosting components with individual trigramme (and not classified at least A6) are classifies as RTM. Component has been re-classified based on information that " it is the parent for the AVR system, which is a priority from CIP and a priority 1 from RE’s list" => C2. | CLM
2 | GEX |  |  |  | 2GEX002AP | 2GEX001AR | [10 empty] | B0601 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation generator Function: To provide the excitation current to the main generator Failure analysis and classification: Loss of the excitation generator will result in the loss of GEX001GA Therefore the loss of GEX001AP shall have the same classification as GEX001GA => C2,C4,C5,C6,C8,C9,S4,E5,E6,I1,I4 (But NO S1) NOTE: In evaluating the failure of this component it is assumed that the unit is in House Load Configuration. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX002AP | 2GEX001AR | [10 empty] | B0602 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation generator Function: To provide the excitation current to the main generator Failure analysis and classification: Loss of the excitation generator will result in the loss of GEX001GA Therefore the loss of GEX001AP shall have the same classification as GEX001GA => C2,C4,C5,C6,C8,C9,S4,E5,E6,I1,I4 (But NO S1) NOTE: In evaluating the failure of this component it is assumed that the unit is in House Load Configuration. | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX003AP | 2GEX001AR | [10 empty] | B0603 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Load angle generator Function: To supply the load angle to the excitation circuit Failure analysis and classification: Component permanently in service. -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 | CHM | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX001TR | 2GEX002TR | [10 empty] | B0604 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS
2 | GEX |  |  |  | 2GEX002TR | 2GEX003TR | [10 empty] | B0605 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS
2 | GEX |  |  |  | 2GEX001TR | 2GEX002TR | [10 empty] | B0606 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS
2 | GEX |  |  |  | 2GEX002TR | 2GEX003TR | [10 empty] | B0607 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS
2 | GEX |  |  |  | 2GEX001TR | 2GEX003TR | [10 empty] | B0608 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1 ,I4 -- Failure to function correctly may require outage repair time > 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHM | Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS
2 | GEX |  |  |  | 2GEX020CR | 2GEX001AR | [10 empty] | B0609 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX020CR | 2GEX001AR | [10 empty] | B0610 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX003TR | 2GEX001AR | [10 empty] | B0611 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Excitation Transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: Component permanently in service I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 | CHS | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GEX |  |  |  | 2GEX020CR | 2GEX001AR | [10 empty] | B0612 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | GGR |  |  |  | 2LLC0205 | 2GGR002PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lubrication oil to the main turbo-alternator when the main pump cannot Failure analysis and classification: Component on standby during turbine operation. In service during turbine shutdown and start up. - Failure to function when the turbine is in service will result in a turbine trip => C2 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 First stand by pump, receives auto start order on lo lub oil pressure. Defence in depth. => S4, E6 | CLM
2 | GGR |  |  |  | 2GGR059CR | 2GGR001MO | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM | Motor Function: To drive 001 PO Failure analysis and classification: Component continuously in service and energized => I1,I4 Failure can have the following consequences: - Failure to function during normal operation will result in no load loss. The stand-by pump 002 PO will take over. To overhaul or exchange the pump requires a turbine outage as the motor is supplied from a generator on the turbine shaft. =>C2, E6 - Outage repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities. Therefore NO C2. | CHM
2 | GGR |  |  |  | 2GGR059CR | 2GGR001MO | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM | Motor Function: To drive 001 PO Failure analysis and classification: Component continuously in service and energized => I1,I4 Failure can have the following consequences: - Failure to function during normal operation will result in no load loss. The stand-by pump 002 PO will take over. To overhaul or exchange the pump requires a turbine outage as the motor is supplied from a generator on the turbine shaft. =>C2, E6 - Outage repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities. Therefore NO C2. | CHM
2 | GSE |  |  |  | 2DNLG06CR | 2GSE002AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | This cabinet is to performed control functions for the GGR jacking oil, slow rotation, GSS, CET, CAR and other auxiliary systems to the turbine. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHM
2 | GSS |  |  |  | 2LKC0801 | 2GSS221VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve . Function: 200 & 400 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | CLM
2 | GSS |  |  |  | 2LKC0802 | 2GSS222VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve , Function:-To drain 200 & 400 ZZ tube bundle of condensate towards AHP 602RE Start-up drain path Failure analysis: Fails to close or is not leak tight => S4,E5,E6 Fails to open or is not fully open =>S4,E5,E6 Repair time < 36 Hrs => NO C2 | CLM
2 | JPP |  |  |  | 2JPP002BX | 2JPP002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply fire fighting water Failure analysis and classification: Failure will result in loss of redundancy => C9,S4,E6,A6 | CLS
2 | JPP |  |  |  | 2JPP001BX | 2JPP001PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply fire fighting water Failure analysis and classification: Failure will result in loss of redundancy => C9,S4,E6,A6 | CLS
2 | KRT |  |  |  | 2LLA0501 | 2KRT001TB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
2 | LAA |  |  |  | 2LLE0105 | 2LAA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor scram as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA001RD will result in loss of LAA001TB. Therefore the loss of LAA001RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LAA |  |  |  | 2LLI0107 | 2LAA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor shut down as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA002RD will result in loss of LAA001TB. Therefore the loss of LAA002RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LAA |  |  |  | 2LLE0105 | 2LAA001RD | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor scram as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA001RD will result in loss of LAA001TB. Therefore the loss of LAA001RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LAA |  |  |  | 2LLI0107 | 2LAA002RD | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Battery charger - 230 V DC. Function: to supply LAA with 220v DC supply. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (... an LAA battery charger is inoperable. Repair within 14 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB. If no operator action is taken, the loss of the LAA switchboard will result in the loss of the LNE switchboard. Either of these will result in entry into OTS (... the LNE switchboard is inoperable, -OR- the LAA switchboard is inoperable. Initiate fallback to SD / RRA within 1 hour.). Conservatively, this will result in the initiation (without delay) of a manual reactor shut down as/if required by Operating Incident Procedure I-LNE, and a turbine trip. => C2,C3,S4,E5. Review of the LAA feeder diagram indicates that loss of LAA002RD will result in loss of LAA001TB. Therefore the loss of LAA002RD shall have the same classification as LAA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LAA |  |  |  | 2LAA0242 | 2LNE001DL | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAA |  |  |  | 2LAA0242 | 2LNE001DL | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAA |  |  |  | 2LAA0231 | 2LNE002DL | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAA |  |  |  | 2LAA0231 | 2LNE002DL | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAA |  |  |  | 2LAA0232 | 2LNE003DL | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAA |  |  |  | 2LAA0232 | 2LNE003DL | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LAB |  |  |  | 2LAB03 | 2GGR004PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
2 | LAB |  |  |  | 2LAB03 | 2GGR004PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
2 | LAB |  |  |  | 2LAB03 | 2GGR004PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001, 002 & 003 PO are unavailable. Failure analysis and classification: Pump in service continuously and pressurised => I1,I4 To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Functional failure of the component could result in damage to the turbine bearings => E5 | CHM
2 | LAC |  |  |  | 2LAC04 | 2GGR003PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
2 | LAC |  |  |  | 2LAC04 | 2GGR003PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
2 | LAC |  |  |  | 2LAC04 | 2GGR003PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To supply lub oil to the turbine and generator bearings for safe shutdown when 001 & 002 PO are unavailable. Failure analysis and classification: To overhaul or exchange the pump requires a turbine outage. =>C2 >36 hrs delay in turbine start-up following return from outage, based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component required for redundancy and safe turbine rundown if the other oil supply pumps fail => S4,E6 Second stand by pump, receives auto start order on lo lub oil pressure (credit taken for 002PO). Functional failure of the component could result in damage to the turbine bearings => E5 | CLM
2 | LBC |  |  |  | 2LLA0509 | 2LBC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBC feeder diagram indicates that loss of LBC001RD will result in loss of LBC001TB. Therefore the loss of LBC001RD shall have the same classification as LBC001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LBD |  |  |  | 2LLB0508 | 2LBD001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBD feeder diagram indicates that loss of LBD001DL will result in loss of LBD001TB. Therefore the loss of LBD001DL shall have the same classification as LBD001TB => C1,C2,C3,C5,C6,C8,C9,S2,S4,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LBE |  |  |  | 2LLA0508 | 2LBE001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBE feeder diagram indicates that loss of LBE001RD will result in loss of LBE001TB. Therefore the loss of LBE001RD shall have the same classification as LBE001TB => C2,C3,C5,C6,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LBF |  |  |  | 2LLB0507 | 2LBF001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBF feeder diagram indicates that loss of LBF001RD will result in loss of LBF001TB. Therefore the loss of LBF001RD shall have the same classification as LBF001TB => C2,C3,C5,C6,C8,C9,S2,S4,E5,E6,I1,I4 PSA Significant Component => S6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LBJ |  |  |  | 2LLC0409 | 2LBJ001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBJ feeder diagram indicates that loss of LBJ001RD will result in loss of LBJ001TB. Therefore the loss of LBJ001RD shall have the same classification as LBJ001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LBJ |  |  |  | 2LLI0409 | 2LBJ002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBJ feeder diagram indicates that loss of LBJ001RD will result in loss of LBJ001TB. Therefore the loss of LBJ001RD shall have the same classification as LBJ001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LDA |  |  |  | 2LLA0504 | 2LDA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LDA feeder diagram indicates that loss of LDA001RD will result in loss of LDA001TB. Therefore the loss of LDA001RD shall have the same classification as LDA001TB => C1,C2,C6,C8,C9,S4,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LDA |  |  |  | 2LLC0411 | 2LDA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LDA feeder diagram indicates that loss of LDA001RD will result in loss of LDA001TB. Therefore the loss of LDA001RD shall have the same classification as LDA001TB => C1,C2,C6,C8,C9,S4,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHP |  |  |  | 2LLG0103 | 2LHP004MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Motor Function: Lube Oil Pre-lube Failure analysis and classification: -- Pump failure will result in loss of engine pre-heat. => C3, S5, I1 | CHM
2 | LHP |  |  |  | 2LLG0203 | 2LHP005PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: Oil Filling Failure analysis and classification: -- Pump failure will result in inability to fill oil storage tank and replenish consumption at 7kg/s. Estimated mission time of 30 days. => C8, C9, S1, S5. | CLM
2 | LHP |  |  |  | 2LLG0204 | 2LHP001RE | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater Function: Pre-heat Water Heating Failure analysis and classification: Loss of engine pre-heat will result in slow starts and increased engine wear. => C3, E6 | CLM
2 | LHP |  |  |  | 2LLG0205 | 2LHP002RE | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater Function: Generator anti condensation heater. Failure analysis and classification: Maintain generator stator temperature to prevent ingress of moisture. Heater failure could result in moisture ingress and subsequent degradation of stator insulation which could result in unavailability of the EDG. => C3, C8, C9, S6, E5, I1, I4 | CHM
2 | LHP |  |  |  | 2LLG0107 | 2LHP001ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
2 | LHP |  |  |  | 2LLG0105 | 2LHP002ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
2 | LHP |  |  |  | 2LHP002AR | 2LHP001GA | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHP |  |  |  | 2LHP002AR | 2LHP001GA | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHP |  |  |  | 2LHP002AR | 2LHP001GA | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHP |  |  |  | 2LLG0204 | 2LHP004RE | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Electric heater Function: Pre-heating sub-system. Failure analysis and classification: Failure of the pre-heating system does not immediately render the EDG inoperable. The EDG will however be considered inoperable in accordance with OTS if the pre-heat temperature drop down to the alarm level of 40¿C. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, | CLM
2 | LHP |  |  |  | 2LHP003AR | 2LHP002AR | [10 empty] | B0117 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: EDG relaying control cabinet. Function: Relaying for local EDG start/stop and protection control functions. Failure analysis and classification: Relaying failure could result in failure of the EDG to start or failure to run. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM
2 | LHQ |  |  |  | 2LLW0103 | 2LHQ004MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Motor Function: Lube Oil Pre-lube Failure analysis and classification: -- Pump failure will result in loss of engine pre-heat. => C3, S5, I1 | CHM
2 | LHQ |  |  |  | 2LLW0203 | 2LHQ005PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: Oil Filling Failure analysis and classification: -- Pump failure will result in inability to fill oil storage tank and replenish consumption at 7kg/s. Estimated mission time of 30 days. => C8, C9, S1, S5. | CLM
2 | LHQ |  |  |  | 2LLW0204 | 2LHQ001RE | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater Function: Pre-heat Water Heating Failure analysis and classification: Loss of engine pre-heat will result in slow starts and increased engine wear. => C3, E6 | CLM
2 | LHQ |  |  |  | 2LLW0205 | 2LHQ002RE | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Heater Function: Generator anti condensation heater. Failure analysis and classification: Maintain generator stator temperature to prevent ingress of moisture. Heater failure could result in moisture ingress and subsequent degradation of stator insulation which could result in unavailability of the EDG. => C3, C8, C9, S6, E5, I1, I4 | CHM
2 | LHQ |  |  |  | 2LLW0107 | 2LHQ001ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
2 | LHQ |  |  |  | 2LLW0105 | 2LHQ002ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
2 | LHQ |  |  |  | 2LHQ002AR | 2LHQ001GA | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHQ |  |  |  | 2LHQ002AR | 2LHQ001GA | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHQ |  |  |  | 2LHQ002AR | 2LHQ001GA | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHA Failure analysis and classification: Review of the LHA feeder diagram indicates that loss of LHP001GA may result in loss of LHA001TB. Therefore the loss of LHP001GA shall have the same classification as LHA001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LHQ |  |  |  | 2LLW0204 | 2LHQ004RE | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Electric heater Function: Pre-heating sub-system. Failure analysis and classification: Failure of the pre-heating system does not immediately render the EDG inoperable. The EDG will however be considered inoperable in accordance with OTS if the pre-heat temperature drop down to the alarm level of 40¿C. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, | CLM
2 | LHQ |  |  |  | 2LHQ003AR | 2LHQ002AR | [10 empty] | B0117 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: EDG relaying control cabinet. Function: Relaying for local EDG start/stop and protection control functions. Failure analysis and classification: Relaying failure could result in failure of the EDG to start or failure to run. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM
2 | LKL |  |  |  | 2LKD0103 | 2LKL001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKL001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C6,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LKL |  |  |  | 2LKD0103 | 2LKL001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKL001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C6,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LLG |  |  |  | 2LLI0103 | 2LLG001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLG001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LLG |  |  |  | 2LLI0103 | 2LLG001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLG001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LLW |  |  |  | 2LLJ0105 | 2LLW001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLW001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LLW |  |  |  | 2LLJ0105 | 2LLW001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLW001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL001AR | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | In the worst case when all redundancy is lost in the control logic will mean that the system will not recognise input commands from the control room and/ or SIP thus not processing commands to the RodPilot cabinets. The rods will be locked in current position. Changing the reactor state will not be possible. Any single failure within the Control Logic will activate an alarm with detailed information available but will be functional. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL002AR | [10 empty] | B0102 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL003AR | [10 empty] | B0103 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL004AR | [10 empty] | B0104 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL005AR | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | LMA |  |  |  | 2LMA100CR | 2RGL006AR | [10 empty] | B0106 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM
2 | LNE |  |  |  | 2LLI0310 | 2LNE001DL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LNE |  |  |  | 2LNE001DL | 2LNE002DL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE001DL may result in loss of LNE001TB. Therefore the loss of LNE001DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LNE |  |  |  | 2LNE002DL | 2LNE003DL | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE002DL may result in loss of LNE001TB. Therefore the loss of LNE002DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM | Inverter Function: To convert 220 V DC to 220 V AC. Failure analysis and classification: Review of the LNE feeder diagram indicates that loss of LNE003DL may result in loss of LNE001TB. Therefore the loss of LNE003DL shall have the same classification as LNE001TB => C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 NOTE: In evaluating the failure of this component it is assumed that one of the other 2 inverters is on PTW, the in-service inverter fails, and this last inverter does not function as required; resulting in loss of the switchboard. E3=>YES as per the System Engineer's review. | CHM
2 | LNE |  |  |  | 2LNE0234 | 2GPA003AR | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet hosting electrical protection equipment Function: To host protection circuits Failure analysis and classification: Component permanently in service => I1, I4 Failure to function 'when required’ could result in a turbine trip, Pn >20% Loss, outage delay => C2, S4, S7, E6 | CHM
2 | LNE |  |  |  | 2LNE0223 | 2GPA004AR | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet hosting electrical protection equipment Function: To host protection circuits Failure analysis and classification: Component permanently in service => I1, I4 Failure to function 'when required’ could result in a turbine trip, Pn >20% Loss, outage delay => C2, S4, S7, E6 | CHM
2 | LNE |  |  |  | 2LNE0351 | 2RGL010AR | [10 empty] | B0045 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | In the worst case when all redundancy is lost in the Processing Logic will mean that the system will not be able to perform rod cluster position monitoring and comparison. Functional failure of the cabinet will affect the comparison of rods and banks and the position display on RGL 001 HV. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement. If comparison only is affected then RGL 5 Group 2 applies. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNE |  |  |  | 2LNE0341 | 2RGL009AR | [10 empty] | B0049 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017-08-25: Classification updated. No longer SPV, not C2. | CHM
2 | LNE |  |  |  | 2LNE0342 | 2RGL009AR | [10 empty] | B0050 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017-08-25: Classification updated. No longer SPV, not C2. | CHM
2 | LNE |  |  |  | 2LNE0343 | 2RGL009AR | [10 empty] | B0051 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | This cabinet houses the MCP 10 and MCP 21 modules that interfaces with the RPI coil stack on the vessel head. Functional failure of the cabinet will affect the rod position indication and the comparison of rods and banks and the position display on RGL 001 HV and the LED display of the MCP 30 modules. 3 Days to repair or RGL 2 Group 1 if Bank D is affected in the event of a secondary load reduction resulting in rod movement 2017-08-25: Classification updated. No longer SPV, not C2. | CHM
2 | LNE |  |  |  | 2LNE0333 | 2RIC001AR | [10 empty] | B0055 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Entire RIC control cabinet at 19 m, including 5 channels and associated monitoring (leaking nozzles and flux thimble) used for the production of the monthly flux map . On a failure => Unable to complete the flux map => OTS group 2, decreased power below 50% (C2, C3) default 2 => Loss of monitoring on leaks at nozzles and flux thimbles => Ability to monitor the level RPE 011 PS or the results of primary leaks daily Also true for RIC 002 AR. 2017-0817- Not a SPV as per System Engineering Classification: Each one of the 5 channels is in a separate cabinet with multiple components. No sigle failure of one component can cause all 5 channels to fail. | CHM
2 | LNE |  |  |  | 2LNE0322 | 2RAM001TB | [10 empty] | B0058 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | AC Switchboard Function: AC switchboard for RAM sets. Failure analysis and classification: Switchboard continuously in service and energized => I1,I4 - Failure of the switchboard will/could make both RAM motor/alternator sets inoperable => C1,C2,C8,C9,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
2 | LNE |  |  |  | 2LNE0453 | 2ASG055CR | [10 empty] | B0071 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | TRICASTIN CLASSIFICATION USED Sensor supply (Sn ..) -> Consideration of the worst case. | CHM
2 | LNE |  |  |  | 2LNE0344 | 2GEX001AR | [10 empty] | B0076 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Cabinet. Function: To accommodate equipment. Failure analysis and classification: C2: Loss of excitation will lead to tripping the unit. S4: Failure of component could lead to change in setpoint, which can cause a power or voltage transient. E2: Loss of redundancy requires offline repair. E5: Overvoltage condition could damage primary plant insulation. E6: Generator can not operate without the AVR in operation. I1, I2: Component permanently in service I4: All channels in standby mode and energised. | CHM
2 | LNE |  |  |  | 2GSE001AR | 2GSE002AR | [10 empty] | B0081 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | This cabinet houses the Bently racks for the turbine expansion and vibration sensors. It also houses the acquisition rack for the RCP system. The vibration measurerment circuit now produces an automated 2oo20 protection trip. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM | This cabinet is to performed control functions for the GGR jacking oil, slow rotation, GSS, CET, CAR and other auxiliary systems to the turbine. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHM
2 | LNE |  |  |  | 2LNE180CR | 2GPB002AR | [10 empty] | B0183 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet - supply to auto time switch. All cabinets are classified as RTF. | RTM | Function: Sub-Synchronization Resonance Protection GPB001AR is the parent component for the SSR protection. C2 - A failure of the SSR protection (GPB) can initiate tripping of the 400kV breaker. This will house load the unit resulting in 900MW load loss. S4 - See above comment. E4 - Long lead time for spares I-1 - Always in service when unit online. I-4 - VT and CT inputs with speed signals measured from tooth wheels on turbine end and exciter end. | CHM
2 | LNE |  |  |  | 2LNE320CR | 2VVP010MP | [10 empty] | B0321 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet -1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | Line 1 steam pressure TX - Prot. channel - 2/3 logic - SIP III. Loss of PROTECTION FUNCTION => C5-To RPR - STEAMLINE BREAK PROTECTION - To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6 - To ID & EN in C/room-To EU NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHS
2 | LNE |  |  |  | 2LNE320CR | 2VVP011MP | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet -1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | Line 1 steam pressure TX - Prot. channel - 2/3 logic - SIP IV. Loss of PROTECTION FUNCTION => C5 - To RPR - STEAMLINE BREAK PROTECTION - To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6 - To - VVV 001 VV OPENING ENABLE - To ID in C/room - To EU | CHS
2 | LNE |  |  |  | 2LNE320CR | 2VVP012MP | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical | General description: Cabinet -1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | Line 3 steam pressure TX - Prot. channel - 2/3 logic - SIP III. Loss of PROTECTION FUNCTION => C5-To RPR - STEAMLINE BREAK PROTECTION-To - STEAM FLOW COMPENSATION Loss of CONTROL FUNCTION => S4,E6-To ID in C/room-To EU NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | CHS
2 | PTR |  |  |  | 2PTR001BX | 2PTR001PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | PTR recirc pump. Function: Pump used to recirculate the SFP as well as do various water transfers within the PTR system. Failure analysis: Component runs 50% during normal SFP recirculation.S4,E5,E6 Component used under varying workload conditions as 2PTR001PO is used for various transfers with varying suction heads and flowrates => E6 Component required for SFP cooling during RO when all the fuel is stored in the SFP. Both cooling trains to the SFP are required at this time. PSA Significant Component => S6. | CLM
2 | PTR |  |  |  | 2PTR002BX | 2PTR002PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | PTR recirc pump. Function: Pump used to recirculate the SFP as well as do various water transfers within the PTR system. Component used as RRA back-up during fuel unload/reload. Failure analysis: When in RRA back-up mode, the loss of 002PO results in loss of redundancy.=>S4. Component used under varying workload conditions as 2PTR002PO is used for various transfers with varying suction heads and flowrates =>C6,E5, E6 Component required for SFP cooling during RO when all the fuel is stored in the SFP. Both cooling trains to the SFP are required at this time. =>C6 PSA Significant Component => S6. Duty cycle remains low as the running regime is changing from 1 month on 2 months off, to 2 months on 2 months off. This change is to align with the testing of the emergency diesel generators. | CLM
2 | RCP |  |  |  | B0103 | 2RCP011PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 001 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 001 PO is running. Required only during start-up and shut-down. -- Failure to function during 001 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 The equipment is required to perform steps in the incident/accident procedures or severe accident management guidelines. =>C9 | CLM
2 | RCP |  |  |  | B0103 | 2RCP021PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 003 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 003 PO is running. Required only during start-up and shut-down. -- Failure to function during 003 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Equipment required to perform steps required by incident/accident procedures or severe accident management guidelines.=>C9 | CLM
2 | RCP |  |  |  | B0103 | 2RCP031PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Oil lift pump Function: To lift main pump - 003 PO, shaft. Required only during start-up and shut-down. Failure analysis and classification: Pump is out of service while 003 PO is running. Required only during start-up and shut-down. -- Failure to function during 003 PO shutdown (although undesirable) shall not cause any damage => E6 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Equipment required to perform steps required by incident/accident procedures or severe accident management guidelines.=>C9 | CLM
2 | RCP |  |  |  | J2527 | 2RCP005VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 008 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 008 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 008 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 | CHS
2 | RCP |  |  |  | E1315 | 2RCP007VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 010 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 010 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 010 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 Update, Wed 2017/11/29. Change 1/2 RCP 005/6/7/VP from C2 to C1, C2 The block valves are left open during power. However, should a PORV open and then fail to close, the relevant block valve is required to close. Therefore, the failure of the block valve on its own will have no direct plant consequences but there are OTS limitations as the plant may have to fallback to SD / RRA within 1 hour. However, if there is a failure of the block valve to close when it is required with a PORV stuck open, then it can result in an immediate reactor trip. Therefore, the ER classification of 1/2 RCP 005/006/007 VP should be changed from C2 to C1/C2. | CHS
2 | RCP |  |  |  | J2830 | 2RCP006VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate PORV 009 VP. Failure analysis and classification: Valve OPEN/CLOSED (as require) during normal operation. Not designed for frequent on-power manipulations. Under high pressure => I1,A2 - Failure to CLOSE will/could result in uncontrolled PZRZ inventory loss in the event of PORV 009 VP not CLOSE => C2,C3,C9,S4. - Failure to OPEN will/could result in unavailability of the 009 VP => C2,C3 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Component subject of PT-12-RCP 072 - 3 monthly manoeuvrability & stroke time tests - failure => C2,C3 Component subject of RCP PT - 1 RO manoeuvrability & stroke time tests - failure => C2 Update, Wed 2017/11/29. Change 1/2 RCP 005/6/7/VP from C2 to C1, C2 The block valves are left open during power. However, should a PORV open and then fail to close, the relevant block valve is required to close. Therefore, the failure of the block valve on its own will have no direct plant consequences but there are OTS limitations as the plant may have to fallback to SD / RRA within 1 hour. However, if there is a failure of the block valve to close when it is required with a PORV stuck open, then it can result in an immediate reactor trip. Therefore, the ER classification of 1/2 RCP 005/006/007 VP should be changed from C2 to C1/C2. | CHS
2 | RCP |  |  |  | E0709 | 2RCP215VP | [10 empty] | B0046 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: RCP to RRA train A interconnection valve Failure analysis and classification: Valve used when entering (or leaving RRA) conditions Valve exposed to high pressure => A2 - Failure to function or pass leak tightness test on start up could/will require outage repair time > 12h => C2,C8,C9,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RCP |  |  |  | D0103 | 2RCP212VP | [10 empty] | B0047 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: RCP to RRA train B interconnection valve Failure analysis and classification: Valve used when entering (or leaving RRA) conditions Valve exposed to high pressure => A2 - Failure to function or pass leak tightness test on start up could/will require outage repair time > 12h => C2,C8,C9,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RCP |  |  |  | E0709 | 2RCP215VP | [10 empty] | B0048 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: RCP to RRA train A interconnection valve Failure analysis and classification: Valve used when entering (or leaving RRA) conditions Valve exposed to high pressure => A2 - Failure to function or pass leak tightness test on start up could/will require outage repair time > 12h => C2,C8,C9,S4,E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RCV |  |  |  | 2LLD0412 | 2RCV005PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 002 PO Failure analysis and classification: Analysis based on RCV 002 PO is the standby Train B pump. Component seldom in service Component required when 002 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => C3 RPR test requirement - 2 monthly, any domain - 005 PO start test - failure => C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
2 | RCV |  |  |  | 2LLD0512 | 2RCV034VP | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To CLOSE/OPEN charging pumps suction from 002 BA. Failure analysis and classification: Valve normally OPEN. - Failure to CLOSE when require will result in incorrect valves configuration during SI and on 002 BA level LO3 => C3,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 RPR test requirement - 2 monthly, any domain - cLosure test - failure => C3,S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | 2LLC0508 | 2RCV004PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 001 PO Failure analysis and classification: Analysis based on 001 PO AND that 003 PO is operable Component required when 001 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => NO C3 RPR test requirement - 2 monthly, any domain - 004 PO start test - failure => NO C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
2 | RCV |  |  |  | 2LLD0511 | 2RCV048VP | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate charging line - CI - outside containment, pen 260 Valve normally OPEN and under high pressure. Require to CLOSE on SI train B => A2 - Valve failure to OPEN during outage, normal ops and during incident/accident => C3,C8,C9,S4,E5,E6 - Valve failure to CLOSE on SI will result in safety function degradation and impair ability to preform steps from incident/accident procedure => C6,C7,C8,C9,S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM test requirement - 1 or 3RO LLRT test - outage => C2 Component tested - 1 RO - SHUTDOWN IN PROGRESS, RCP AT 300 kPa, OPS PT KWB-PT-RCV-285 "AUTOMATIC LETDOWN LINE ISOLATION TEST" => C3 Component tested - 1 RO - Temp < 60°C - OPS PT KWB-PT-RIS-259 "SAFETY INJECTION SYSTEM OVERALL TEST FOR TRAIN B" => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
2 | RCV |  |  |  | 2LLC0507 | 2RCV006PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: To provide lube oil to gearbox and main pump 003 PO Failure analysis and classification: Analysis based on 003 PO AND that 001 PO is operable Component required when 003 PO is started => E5 Component tested - OPS PT weekly - verify operability of the pump => NO C3 RPR test requirement - 2 monthly, any domain - 006 PO start test - failure => NO C3 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during power operation =>C6,C8,C9,S4 ,E6 | CLM
2 | RCV |  |  |  | 2LLC0506 | 2RCV033VP | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To CLOSE/OPEN charging pumps suction from 002 BA. Failure analysis and classification: Valve normally OPEN. - Failure to CLOSE when require will result in incorrect valves configuration during SI and on 002 BA level LO3 => C3,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 RPR test requirement - 2 monthly, any domain - cLosure test - failure => C3,S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | 2LKC0309 | 2RCV076VP | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 001 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | J1921 | 2RCV050VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate charging line - downstream of 001 EX - inside containment Failure analysis and classification: Valve normally OPEN and under high pressure. Require to CLOSE on SI train A => A2 - Valve failure to OPEN during outage, normal ops and during incident/accident => C3,C8,C9,S4,E5,E6 - Valve failure to CLOSE on SI will result in safety function degradation and impair ability to preform steps from incident/accident procedure =>C6,C8,C9,S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM test requirement - 1RO - outage - stroke time check - S4,E6 Valve tested - 1 RO OPS PT in state 4 - 050 VP AND 227 VP both CLOSED = L/D isolation (007, 008, 009 VP)=> S4 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CHS
2 | RCV |  |  |  | 2LKC0508 | 2RCV077VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 002 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | J2224 | 2RCV088VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: CI - to isolate RCP pumps seal leakoff return line - outside containment Failure analysis and classification: Valve normally OPEN. Require to CLOSE upon CI A - train A - Failure to CLOSE upon CI A train B => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing on CI Ph A - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing time test - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | 2LKC0507 | 2RCV078VP | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RCP 003 PO seal injection supply line - CI - outside containment Failure analysis and classification: Valve normally OPEN. Used during outages for the maintenance activity. - Failure to CLOSE upon manual actuation from 017 TL => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 2RO verify operation on HH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 5RO verify operation on LH pump operation - outage => C2,S4,E5,E6 - SRSM requirement - 1RO verify operation - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | 2LLC0503 | 2RCV060VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate common seal injection line to RCP pumps - upstream 003/004 FI Failure analysis and classification: Valve under high pressure, normally OPEN - manually controled from 016 TL, used chiefly during outage => A2 - Valve failure to CLOSE or passing - instruction in procedure I-RRI and LAS 21 where valve is require to CLOSE => C9,S4,E5,E6 - Valve failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RCV |  |  |  | 2LLD0505 | 2RCV089VP | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: CI - to isolate RCP pumps seal leakoff return line - inside containment Failure analysis and classification: Valve normally OPEN. Require to CLOSE upon CI A - train B - Failure to CLOSE upon CI A train B => C6,C7,C9,S4, - SRSM requirement - 1 or 3RO LLRT test - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing on CI Ph A - outage => C2,S4,E5,E6 - SRSM requirement - 3RO cLosing time test - outage => C2,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RCV |  |  |  | 2LLD0504 | 2RCV222VP | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HH pumps miniflow valve Failure analysis and classification: Valve normally OPEN. Under high pressure. - Failure to CLOSE upon SI signal => C6,C8,C9 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 RPR test requirement - 2 monthly, any domain - closure test - failure => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RCV |  |  |  | 2LLC0602 | 2RCV223VP | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HH pumps miniflow valve Failure analysis and classification: Valve normally OPEN. Under high pressure. - Failure to CLOSE upon SI signal => C6,C8,C9 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 RPR test requirement - 2 monthly, any domain - closure test - failure => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | REA |  |  |  | 2LLD0502 | 2REA210VB | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate direct boration line to RCV Component used to inject rapidly significant amount of the borated water to RCP charging pumps suction as required for. Failure analysis and classification: Valve used to inject rapidly significant amount of the borated water to RCP charging pumps suction Valve normally CLOSED. Require to OPEN upon opening order from TPL. - Failure to open (jammed closed) when require will impair ability to perform steps required by incident/accident procedures => C6,C9,S4,E5,E6 SRSM test requirements - 1 RO - manoeuvrability test from TPL during outage - failure => S4 Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
2 | REA |  |  |  | 2REA001BX | 2REA003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: Boric acid pump Failure analysis and classification: - Pump failure to supply boric acid will require entry into OTS => C3 Failure to function correctly may require outage repair time < 36hrs based on Maintenances repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
2 | REA |  |  |  | 2REA002BX | 2REA004PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: Boric acid pump Failure analysis and classification: - Pump failure to supply boric acid will require entry into OTS => C3 Failure to function correctly may require outage repair time < 36hrs based on Maintenances repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 | CLM
2 | RIC |  |  |  | B0406 | 2RIC002AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | RIC control panel in the chain of flux at 3.5 m in the BR including the 5 channel paths and associated monitoring. Used to make the monthly flux map. On a failure => Unable to make the flux map => OTS group 2, decrease of power below 50% (C2, C3). Following update of class criteria on 19 Dec 2011, changed S4 to 0 because OTS implication is accounted for by C3. This is applicable to RIC 001 AR as well. | CHM
2 | RIS |  |  |  | C0103 | 2RIS001VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 001 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | G0103 | 2RIS003VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 003 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | C0406 | 2RIS002VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: 002 BA towards RCP Failure analysis and classification: Valve normally open (with opening confirmation on SI) Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 -- Failure to AUTO OPEN (re-open if selected to auto mode) above P11 => E5,E6 Fails to open => C3,C9. SRSM requirement - 10 years - operation from TPL => C2 (outage) Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLE0408 | 2RIS075VB | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump suction line from PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Valve receives confirmation OPENING order upon Train A SI signal. Valve require to CLOSE for second phase of SI (on the recirculation signal from RPR train A and 051 VP fully open). - Failure to OPEN will result in incorrect valve configuration for normal operation and it will require entry into OTS, with any fallback constraint and during first phase of SI making suction from PTR 001 BA via Train A unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C3,C6,C9,S4,E5,E6 - Failure to CLOSE will result in incorrect valves configuration during SI phase 2. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLD0603 | 2RIS085VB | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump suction line from PTR 001 BA - Train B Failure analysis and classification: Valve normally CLOSED. Valve receives confirmation OPENING order upon Train B SI signal. Valve require to CLOSE for second phase of SI (on the recirculation signal from RPR train B and 052 VP fully open). - Failure to OPEN will result in incorrect valve configuration for normal operation and it will require entry into OTS, with any fallback constraint and during first phase of SI making suction from PTR 001 BA via Train B unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C3,C6,C9,S4,E5,E6 - Failure to CLOSE will result in incorrect valves configuration during SI phase 2. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLE0512 | 2RIS012VP | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HHSI pumps suction from PTR 001 BA - Train A Failure analysis and classification: Valve normally CLOSED. Require to AUTO OPEN upon SI, RCV 011 MN level Lo3 and ANTIDILUTION from REA. Require to AUTO CLOSE on RPR boosting signal and 077 VP fully OPEN. - Failure to OPEN will result in incorrect valves configuration during SI making suction from PTR 001 BA via Train A unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to CLOSE will result in incorrect valves configuration during SI in boosting mode. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 | CLM
2 | RIS |  |  |  | 2LLD0606 | 2RIS013VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate HHSI pumps suction from PTR 001 BA - Train B Failure analysis and classification: Valve normally CLOSED. Require to AUTO OPEN upon SI, RCV 012 MN level Lo3 and ANTIDILUTION from REA. Require to AUTO CLOSE on RPR boosting signal and 078 VP fully OPEN. - Failure to OPEN will result in incorrect valves configuration during SI making suction from PTR 001 BA via Train B unavailable. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to CLOSE will result in incorrect valves configuration during SI in boosting mode. Degradation of critical safety function or parameter control and impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C9,S4,E5,E6. - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLE0511 | 2RIS020VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - HHSI (BIT by-pass) line towards cold legs - penetration 262 - outside containment Valve closed during normal operation. There are no RIS auto actions associated with this valve. High operating pre Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RIS |  |  |  | 2LLD0712 | 2RIS144VP | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train B Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo3 (2.1m) for "Recirculation Configuration". - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon recirculating signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLC0604 | 2RIS021VP | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - HHSI (BIT by-pass) line towards hot legs - penetration 263 - outside containment Valve closed during normal operation. There are no RIS auto actions associated with this valve. High operating pres Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RIS |  |  |  | 2LLD0711 | 2RIS145VP | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 002 PO miniflow line to PTR 001 BA - Train B Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration" (if 078 VP fully OPEN). - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon boosting signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLE0510 | 2RIS032VP | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | HHSI discharge line towards cold legs via 004 BA inlet motorized valve - normally closed Function: To isolate 004BA and open on SI signal. Failure analysis: Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Valve fails to operate as required(open on SI signal).=>C6,C8,C9,E5,E6. Component is tested during the outage; test failure => C2 Component is tested during at power operation for passing; test failure => entry into OTS => C3 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe - (outage) => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLD0607 | 2RIS033VP | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | HHSI discharge line towards cold legs via 004 BA inlet motorized valve - normally closed Function: To isolate 004BA and open on SI signal. Failure analysis: Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Valve fails to operate as required(open on SI signal).=>C6,C8,C9,E5,E6. Component is tested during the outage; test failure => C2 Component is tested during at power operation for passing; test failure => entry into OTS => C3 SRSM requirement - 2 monthly - verify functioning during RPR test (any domain) => C3 SRSM requirement - 1RO - verify SI sequence test (any domain) => C2 SRSM requirement - 1RO - verify valve stroke time & fail safe - (outage) => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLE0509 | 2RIS034VP | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 004 BA outlet - penetration 266 - outside containment Valve permanently closed during normal operation. Valve require to open on SI signal. High operating pressure => A2 Valve failure to open Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RIS |  |  |  | 2LLD0608 | 2RIS035VP | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 004 BA outlet - penetration 266 - outside containment Valve permanently closed during normal operation. Valve require to open on SI signal. High operating pressure => A2 Valve failure to open Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RIS |  |  |  | 2LLE0508 | 2RIS051VP | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO suction from 005 BA - penetration 105 - outside containment Valve permanently closed during normal operation. On SI initiation valve remain closed. It is required to open during later stages for SI recircirculation line-up. Function: To provide SI flow (re-circulation)to RCP in event of Safety Injection. Failure analysis: Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLD0609 | 2RIS052VP | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated cont isol valve. To open/close valve on demand. Failure analysis: Valve fails to open:=>C3,C7,C9,E5,E6. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,S4,E5,E6.. Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLE0507 | 2RIS061VP | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO discharge towards RCP cold legs - penetration 104 - outside containment Valve permanently closed during normal operation. Valve is manipulated open/closed while in accident/SAMG proced Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLD0610 | 2RIS062VP | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 002 PO discharge towards RCP cold legs - penetration 207 - outside containment Valve permanently closed during normal operation. Valve is manipulated open/closed while in accident/SAMG proced Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLE0506 | 2RIS063VP | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 001 PO discharge towards RCP hot legs - penetration 102 - outside containment. Valve closed during normal operation. It receives opening order on SI signal. Function: To provide SI flow to RCP in event of Safety Injection. Failure analysis: Subject to Hi Press.=>A2. Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLD0611 | 2RIS064VP | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RIS 002 PO discharge towards RCP hot legs - penetration 101 - outside containment Valve permanently closed during normal operation. Valve receives opening order during SI. Function: To provide SI flow to RCP in event of Safety Injection. Failure analysis: Subject to Hi Press.=>A2. Valve fails to open:=>C3,C6,C7,C9,E5,E6. Valve fails to close as required:=>C3,C7,E5,E6. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLS
2 | RIS |  |  |  | 2LLE0505 | 2RIS077VP | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump 001 PO discharge line from HHSI pumps suction. Failure analysis and classification: Valve normally CLOSED. Require to OPEN upon Train A SI signal. Valve receives confirmation OPENING order from RPR upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration". - Failure to OPEN will result in degradation of critical safety function or parameter control and it will impair ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C8,C9,S4,S6 - Failure to CLOSE upon manual order from TPL will result in incorrect line-up of the critcal safety function component => C3,S4 - Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM testing requirement - 2 monthly & 1RO - valve correct operation on SI signal with PTR 001 BA Lo2 - Boost phase - (any domain) => C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLD0612 | 2RIS078VP | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate LHSI pump 002 PO discharge line from HHSI pumps suction. Failure analysis and classification: Valve normally CLOSED. Require to OPEN upon Train B SI signal. Valve receives confirmation OPENING order from RPR upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration". - Failure to OPEN will result in degradation of critical safety function or parameter control and it will impair ability to perform steps required by incident/accident procedures or severe accident management guidelines => C6,C8,C9,S4,S6 - Failure to CLOSE upon manual order from TPL will result in incorrect line-up of the critcal safety function component => C3,S4 - Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM testing requirement - 2 monthly & 1RO - valve correct operation on SI signal with PTR 001 BA Lo2 - Boost phase - (any domain) => C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RIS |  |  |  | 2LLE0504 | 2RIS132VP | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo2 (5,9m) for "Boosting Configuration" (if 077 VP fully OPEN). - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon boosting signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RIS |  |  |  | 2LLE0503 | 2RIS133VP | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate RIS 001 PO miniflow line to PTR 001 BA - Train A Failure analysis and classification: Valve normally OPEN. Receives confirmation OPENING order upon SI signal. Require to AUTO CLOSE upon PTR 001 BA level Lo3 (2.1m) for "Recirculation Configuration". - Valve failure to OPEN when require will result in declaration of an unplanned OTS event,or during the outage it will require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities or => C2,C3 - Valve failure to CLOSE upon recirculating signal during SI will result in degradation of critical safety function or parameter control => C6,C9,S4,E5,E6 SRSM testing requirement - 2 monthly & 1RO - operating correctly on SI signal - (any domain) => C2,C3 SRSM testing requirement - 1RO verify operation from TPL - (outage) => C2 SRSM testing requirement - 1RO verify stroke time - (outage) => C2 RPR PT - 2 monthly - verify operation => C3 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RPE |  |  |  | E0709 | 2RPE014PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Pump Function: Discharge from 003 BA Failure analysis and classification: -- Pump failure to function correctly during outage (draining or venting) could be repaired > 36 h => therefore NO C2 -- Pump failure to function correctly during normal operation will make defeat purpose of 003 BA (to collect, quantify and evacuate the effluence) => C9 (003 BA intended for leaks calculations - referenced in accident/incident procedures) When is service the bushes wear and if not maintained lead to shaft shear and impellor damage => E6 | CLM
2 | RRA |  |  |  | D0406 | 2RRA001VP | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate inlet line from RCP - Train A Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 SRSM test requirement - 1 RO - verify closed interlock @ P>2,8MPa - outage => S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RRA |  |  |  | E0103 | 2RRA015VP | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate discharge line towards RCP loop 3 cold leg - Train B Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 Valve used duriung outages - evident failure Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RRA |  |  |  | D1416 | 2RRA014VP | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate discharge line towards RCP loop 1 cold leg - Train A Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 Valve used duriung outages - evident failure Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RRA |  |  |  | E1012 | 2RRA021VP | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate inlet line from RCP - Train B Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 SRSM test requirement - 1 RO - verify closed interlock @ P>2,8MPa - outage => S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RRA |  |  |  | E1012 | 2RRA021VP | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate inlet line from RCP - Train B Failure analysis and classification: Valve closed when RRA not require. - Failure to function OPEN/CLOSE during outage will result in delay < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6,A5 - Failure to function OPEN/CLOSE when require will result in degradation of the capability to shut down and maintain RX at cold shut down => C6,C8,S4,E5,E6 - Failure to OPEN/CLOSE will result in impaired ability to perform steps required by incident/accident procedures or severe accident management guidelines => C9 SRSM test requirement - 1 RO - verify closed interlock @ P>2,8MPa - outage => S4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLS
2 | RRI |  |  |  | 2LLJ0303 | 2RRI040VN | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train B RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLJ0302 | 2RRI059VN | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train B RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLJ0301 | 2RRI170VN | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RRM coolers - outside containment Component permanently open during normal operation. SRSM requirement - Closing on CIB + stroke time - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLJ0401 | 2RRI177VN | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line to RRM coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | B0103 | 2RRI019VN | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate outlet line from RRA 001 RF - CI - inside containment, pen 215 Failure analysis and classification: Valve normally CLOSED. - Valve failure to OPEN when RRA require during incident/accident condition will result in degradation of critical safety function or parameter control => C6,C8,C9,S4,E5,E6 - Valve failure to OPEN when RRA require for cooldown will result in an unplanned OTS event, with any fallback constraint => C3 - Valve failure to remain CLOSED (leak tight) will result in degradation of containment (penetration) integrity => C7 - Valve malfunction during the outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly closing test (RPR)KWB-PT-12-RPR-125 - normal operation - PT failure => C3 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | E0406 | 2RRI020VN | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve Function: To isolate outlet line from RRA 002 RF - CI - inside containment, pen 216 Failure analysis and classification: Valve normally CLOSED. - Valve failure to OPEN when RRA require during incident/accident condition will result in degradation of critical safety function or parameter control => C6,C8,C9,S4,E5,E6 - Valve failure to OPEN when RRA require for cooldown will result in an unplanned OTS event, with any fallback constraint => C3 - Valve failure to remain CLOSED (leak tight) will result in degradation of containment (penetration) integrity => C7 - Valve malfunction during the outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 SRSM requirement - 2 monthly closing test (RPR)KWB-PT-12-RPR-125 - normal operation - PT failure => C3 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | J0103 | 2RRI189VN | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RRM return line - penetration 211 - inside containment Function: Normally open. Used for RRM operations, CI valve. Failure analysis: Valve fails to open:=>C8,C9,E5,E6 Valve fails to close/pass PT's/remain leak tight as required:=>C3,C7,E5,E6 Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | 2LLJ0402 | 2RRI210VN | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 001 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | J0406 | 2RRI280VN | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Electric motor actuator for motor operated isolation valve 280 VN - CI - RCP 001 PO return line - penetration 202a - inside containment Function: Motor operated cont isol valve. To open/close valve on demand. Failure analysis: Valve fails to open:=>C3,C7,E5,E6,I1,I4. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,E5,E6,I1,I4. Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | 2LLJ0403 | 2RRI211VN | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 002 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | J0709 | 2RRI281VN | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 002 POreturn line - penetration 202b - inside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLJ0404 | 2RRI212VN | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 003 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | J1012 | 2RRI282VN | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 003 PO return line - penetration 209 - inside containment Function: Cont isol valve. To supply RRI to RCP motor cooling Failure analysis: Valve fails to open:=>C3,C6,C7,E5,E6,I4. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,E5,E6,I4. Failure to function correctly should need an outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | 2LLJ0405 | 2RRI283VN | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 001 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB + stroke time - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLJ0406 | 2RRI284VN | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 002 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLJ0407 | 2RRI285VN | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 003 PO coolers - outside containment Component permanently open during normal operation. SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - Closing on CIB - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLE0501 | 2RRI041VN | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train A RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLJ0408 | 2RRI300VN | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI supply line to RCP 002 BA & 021 RF - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure repair time > 12 Hours => S7 SRSM requirement - LLRT - outage - PT failure => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLE0601 | 2RRI058VN | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motorised isolation valve Train A RRI inter-train changeover valve. Function: To operate inter train changeover valve. Failure analysis: -- Failure to function during outage could/will cause outage delay > 36Hrs => C2 -- Failure to OPEN the valve will result in degradation of the capability to shut down and maintain RX at cold shut down => C8,S4. -- Failure to OPEN the valve will result in inability to perform steps from incident/accident procedures => C9 -- Failure to isolate the valve = change over of trains inhibited - => C2, C3 Failure of mechanical operation/limit switches = valves in-operable=>E5,E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLJ0409 | 2RRI304VN | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 002 BA - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | 2LLE0602 | 2RRI146VN | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate RRI flow to DEG. Failure analysis and classification: Valve permanently OPEN. Used for leak finding and maintenence activity. - Valve failure to OPEN valve will result in loss of RRI cooling to DEG and suseqent EVC and EVR temperatures increase => S4,E5,E6. - Valve failure to function OPERN/CLOSED will impaire ability to perform steps required by incident/accident procedures => C9 - Valve failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | 2LLJ0410 | 2RRI313VN | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Containment isolation, motor operated valve on RRI return line from RCP 021 RF - outside containment Component permanently open during normal operation. SRSM requirement - 2 monthly closing test (RPR) - normal operation - PT failure => C3 SRSM requirement - Closing on CIA - outage - PT failure => S7 SRSM requirement - LLRT - outage - PT failure repair time > 12 Hours => S7 Component failure could degrade containment integrity OTS. => C3,C7 | CLM
2 | RRI |  |  |  | J1315 | 2RRI318VN | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCP 002 BA return line - penetration 208b - inside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRI |  |  |  | 2LLD0706 | 2RRI551VN | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve. Function: To isolate RRI flow to DEG. Failure analysis and classification: Valve permanently OPEN. Used for leak finding and maintenence activity. - Valve failure to OPEN valve will result in loss of RRI cooling to DEG and suseqent EVC and EVR temperatures increase => S4,E5,E6. - Valve failure to function OPERN/CLOSED will impaire ability to perform steps required by incident/accident procedures => C9 - Valve failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 ERCR 36720 Production Challenge, Outage Matrix update of Odd Number Tasks to Even Number tasks to align with the Koeberg Outage Regime. GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2, and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CLM
2 | RRI |  |  |  | J1618 | 2RRI319VN | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - RCV 021 RF return line - penetration 208c - outside containment Normal operation - valve OPEN. Function: Cont isol valve. To supply RRI to RCP/RCV cooling Failure analysis: Valve fails to open:=>C3,C6,C7,E5,E6,I4. Valve fails to close/pass PT's/LLRT as required:=>C3,C7,E5,E6,I4. Failure to function correctly should need an outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | CHM
2 | RRI |  |  |  | 2LLE0609 | 2RRI465VN | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve RRI465VN Function: To isolate RRI common inlet line to the REN/RCV coolers Failure analysis and classification: Failure of valve to operate = unable to isolate sections of supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair operations required by accident/incident procedures (I-RRI) => C9,E6 | CLM
2 | RRI |  |  |  | 2LLE0610 | 2RRI466VN | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve RRI466VN Function: To isolate RRI common inlet line to the REN/RCV coolers Failure analysis and classification: Failure of valve to operate = unable to isolate sections of supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair operations required by accident/incident procedures (I-RRI) => C9,E6 | CLM
2 | RRM |  |  |  | DKH | 2RRM001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRM |  |  |  | DFH | 2RRM002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRM |  |  |  | DHF | 2RRM003ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | RRM |  |  |  | ADG | 2RRM004ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | CDRM ventilation fan. Function: Circulates air through the CRDM. Failure analysis and classification: 50 % duty cycle. -- Failure of the fan to function correctly will/could require outage repair time > 12 hrs => C2 -- Failure of the running fan will require the standby fan to be started (or it will AUTO start) => S4 -- Failure of the stand-by fan to function when require will result in loss of 50% cooling capability. RX will be shutdown immediately to state SD/RRA => C2 (expected exhaust air temperature rise to 80 degC) Used in I-procedure => C9 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | SAP |  |  |  | 2LLI0201 | 2SAP101CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air compressor - train A, emergency, piston. Unavailability will result in loss of redundancy and defence in depth => S4. Component failure could impair steps in the incident and accident procedures. => C9 | CLM
2 | SAP |  |  |  | 2LLJ0201 | 2SAP102CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Air compressor - train B, emergency, piston. Unavailability will result in loss of redundancy and defence in depth => S4. Component failure could impair steps in the incident and accident procedures. => C9 | CLM
2 | SAR |  |  |  | 2LLB0503 | 2SAR432VA | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Motor operated isolation valve - CI - supply line - penetration 203a - outside containment Normal operation - valve OPEN. Outage - valve available for manipulation. Failure to OPEN/CLOSE will/could cause outage delay (repair time) > Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CLM
2 | SEC |  |  |  | 2LLE0612 | 2SEC001MO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
2 | SEC |  |  |  | 2LLB0501 | 2SEC002MO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
2 | SEC |  |  |  | 2LLE0712 | 2SEC003MO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
2 | SEC |  |  |  | 2LLB0601 | 2SEC004MO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO | 2020/224 |  | 2 RO | 223 | V&T |  |  |  | Critical |  |  | Essential circulating water pump motor. Function: Supplies essential circulating water to RRI. Failure analysis and classification: Component in service and energised when selected to run. => I1,I4 Installed in corrosive environment => A6 -- Functional failure making pump inoperable will result in loss of redundancy and reduction of defence in depth => S4 -- Failure to function during outage will/could require outage repair time > 12 hrs => C2,C6 Component required during incident and accident procedures. => C9 | CHS
9 | JDT |  |  |  | 2LNE500CR | 9JDT200AR | [10 empty] | B0903 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description: Cabinet - supply to JDT. All cabinets are classified as RTF. | RTM | Fire detection panel Function: Unit 2 containment Failure analysis and classification: Component permanently in service. -- Functional failure rending fire detection in Unit 2 containment inoperable (in more than one RCP pump room) will require entry into OTS => C3 | CHM
9 | JDT |  |  |  | 1LNE500CR | 9JDT100AR | [10 empty] | B0931 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description: Cabinet - supply to JDT. All cabinets are classified as RTF. | RTM | Fire detection panel Function: Unit 1 containment Failure analysis and classification: Component permanently in service. -- Functional failure rending fire detection in Unit 1 containment inoperable (in more than one RCP pump room) will require entry into OTS => C3 | CHM
9 | JDT |  |  |  | 9JDT201AR | 9JDT100AR | [10 empty] | B0965 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | Cabinet : Local panelfor housing of JDT equipment. Any panel faults are displayed in the common control room and will be acted upon accordingly. => RTF | RTM | Fire detection panel Function: Unit 1 containment Failure analysis and classification: Component permanently in service. -- Functional failure rending fire detection in Unit 1 containment inoperable (in more than one RCP pump room) will require entry into OTS => C3 | CHM
9 | LKZ |  |  |  | 9LKZ001TB | 9LXZ001RD | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description: 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKZ001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => S1,E6,I1,I4 | SHM | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LXZ feeder diagram indicates that loss of LXZ001RD will result in loss of LXZ001TB. Therefore the loss of LXZ001RD shall have the same classification as LXZ001TB => C1,C2,C3,C4,C5,C6,C7,C8,C9,S1,S2,S3,S4,S5,S6,E5,E6 LXZ 001 RD is permanently in service => I1 and I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | KRT |  |  |  | 9KRT501AR | 1KRT001TB | [10 empty] | B0798 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
9 | KRT |  |  |  | 9KRT501AR | 2KRT001TB | [10 empty] | B0799 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM
9 | DNN |  |  |  | 9DNNB30CR | 1KRG161AR | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Cabinet Function: SIP V - To provide the correct environmental and support preserve for electronic equipment Failure analysis and classification Component permanently in service => I1,I4 -- Failure to function during outage will/could result in delay requiring outage repair time > 12 h => C2,E6 -- Failure to provide the correct environmental and support preserve for electronic equipment will/may result in TX trip => C1,C6,C9,S4 | CHM
9 | DSD |  |  |  | 9LLM001TR | 9DSDC01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
9 | DSL |  |  |  | 9LLM001TR | 9DSLB01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
9 | DSL |  |  |  | 9LLM001TR | 9DSLC02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
9 | DSL |  |  |  | 9LLM001TR | 9DSLA03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM | Emergency Lighting: Emergency lighting is required to ensure the safe execution of actions that are included in the LAS’s, accident procedures or even SAMG’s. The emergency lighting is also crucial for the safety of personnel in hazardous environments. => C9, S1. | CLM
9 | LBG |  |  |  | 9LKK0506 | 9LBG001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBG feeder diagram indicates that loss of LBG001RD will result in loss of LBG001TB. Therefore the loss of LBG001RD shall have the same classification as LBG001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LBG |  |  |  | 9LKI0307 | 9LBG002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBG feeder diagram indicates that loss of LBG002RD will result in loss of LBG001TB. Therefore the loss of LBG002RD shall have the same classification as LBG001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LBK |  |  |  | 9LLV0202 | 9LBK001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBK feeder diagram indicates that loss of LBK001RD will result in loss of LBK001TB. Therefore the loss of LBK001RD shall have the same classification as LBK001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LCD |  |  |  | 9LKK0505 | 9LCD001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LCD feeder diagram indicates that loss of LCD001RD will result in loss of LCD001TB. Therefore the loss of LCD001RD shall have the same classification as LCD001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LCD |  |  |  | 9LKI0306 | 9LCD002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LCD feeder diagram indicates that loss of LCD002RD will result in loss of LCD001TB. Therefore the loss of LCD002RD shall have the same classification as LCD001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LCG |  |  |  | 9LLV0203 | 9LCG001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LCG feeder diagram indicates that loss of LCG001RD will result in loss of LCG001TB. Therefore the loss of LCG001RD shall have the same classification as LCG001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LHS |  |  |  | 9LLV0206 | 9LHS004MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Pump Motor Function: Lube Oil Pre-lube Failure analysis and classification: -- Pump failure will result in loss of engine pre-heat. => C3, S5, I1 | CHM
9 | LHS |  |  |  | 9LLV0211 | 9LHS005PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Pump Function: Oil Filling Failure analysis and classification: -- Pump failure will result in inability to fill oil storage tank and replenish consumption at 7kg/s. Estimated mission time of 30 days. => C8, C9, S1, S5. | CLM
9 | LHS |  |  |  | 9LLV0212 | 9LHS001RE | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Heater Function: Pre-heat Water Heating Failure analysis and classification: Loss of engine pre-heat will result in slow starts and increased engine wear. => C3, E6 | CLM
9 | LHS |  |  |  | 9LLV0312 | 9LHS002RE | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Heater Function: Generator anti condensation heater. Failure analysis and classification: Maintain generator stator temperature to prevent ingress of moisture. Heater failure could result in moisture ingress and subsequent degradation of stator insulation which could result in unavailability of the EDG. => C3, C8, C9, S6, E5, I1, I4 | CHM
9 | LHS |  |  |  | 9LLV0107 | 9LHS001ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
9 | LHS |  |  |  | 9LLV0105 | 9LHS002ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Fan Function: Engine room exhaust Failure analysis and classification: -- Failure to remove exhaust fumes and heat from engine room will result failure of electrical boards. This is the DSE basis for 001/2 ZV. => C3, C8, C9, S1, S5, E2, E6 | CLM
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHC Failure analysis and classification: Review of the LHC feeder diagram indicates that loss of LHS001GA may result in loss of LHC001TB. 9LHS is not dedicated to the essential switchboards. Any 9 LHS failure will result in entry into LCO LH4 which makes provision for a 30-day long repair if required (without any fallback). C9,S4,S5,E5,E6 | CLM
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHC Failure analysis and classification: Review of the LHC feeder diagram indicates that loss of LHS001GA may result in loss of LHC001TB. 9LHS is not dedicated to the essential switchboards. Any 9 LHS failure will result in entry into LCO LH4 which makes provision for a 30-day long repair if required (without any fallback). C9,S4,S5,E5,E6 | CLM
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHC Failure analysis and classification: Review of the LHC feeder diagram indicates that loss of LHS001GA may result in loss of LHC001TB. 9LHS is not dedicated to the essential switchboards. Any 9 LHS failure will result in entry into LCO LH4 which makes provision for a 30-day long repair if required (without any fallback). C9,S4,S5,E5,E6 | CLM
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description:Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | 6,6 kV Diesel generator Function: Provide 6,6 kV emergency supply to LHC Failure analysis and classification: Review of the LHC feeder diagram indicates that loss of LHS001GA may result in loss of LHC001TB. 9LHS is not dedicated to the essential switchboards. Any 9 LHS failure will result in entry into LCO LH4 which makes provision for a 30-day long repair if required (without any fallback). C9,S4,S5,E5,E6 | CLM
9 | LHS |  |  |  | 9LLV0212 | 9LHS004RE | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Electric heater Function: Pre-heating sub-system. Failure analysis and classification: Failure of the pre-heating system does not immediately render the EDG inoperable. The EDG will however be considered inoperable in accordance with OTS if the pre-heat temperature drop down to the alarm level of 40¿C. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, | CLM
9 | LHS |  |  |  | 9LHS003AR | 9LHS002AR | [10 empty] | B0117 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical | General description: EDG relaying control cabinet. Function: Relaying for local EDG start/stop and protection control functions. Failure analysis and classification: Relaying failure could result in failure of the EDG to start or failure to run. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM | Automatic voltage regulator (AVR) cabinet. Function: Control and regulate emergency diesel generator output voltage and power. Failure analysis and classification: Failure of the AVR result in failure of the EDG to deliver power. Fallback to SD / RRA within 3 days if one EDG is unavailable, 8 hour fallback if both EDG's are unavailable => C3, Loss of emergency power to safety train result in degradation of the capability to shut down the reactor => C8, Loss of EDG impact incident/accident procedures or severe accident management guidelines => C9 EDG failures impact on Core Damage Frequency (CDF) => S6, Component always in service and energized => I1,I4 | CHM
9 | LKX |  |  |  | 9LKX0212 | 9LKX002CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Panel with breaker (9LKX212JA) for motor actuator operated isolation valve (1SEC201VE) - CFI/SEC interconnection line Valve require to open while commissioning CFI/SEC interconnection line => C9. Classification based on supplied equipment classification. | CLM
9 | LLV |  |  |  | 9LLZ0103 | 9LLV001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLV001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LLV |  |  |  | 9LLZ0103 | 9LLV001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLV001TB and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LLZ |  |  |  | 9LKK0103 | 9LLZ001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLZ001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LLZ |  |  |  | 9LKK0103 | 9LLZ001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLZ001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C9,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | LNF |  |  |  | 9LKI0305 | 9LNF001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Transformer. Function: Power transformer Failure analysis and classification: Review of theLNF feeder diagram indicates that loss of LNF001TR will result in loss of LNF001TB. Therefore the loss of LNF001TR shall have the same classification as LNF001TB => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM
9 | RIS |  |  |  | 9LKI0105 | 9RIS001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | C9, E5 and I1 = yes. The control panel continuously houses the controls of the 9 RIS 011 PO hydraulic control circuit. Therefore it is required in order to operate 9 RIS 011 PO under accident conditions as required in SAMGs. | CHM
9 | RRI |  |  |  | 9LKI0403 | 9RRI044VN | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Motor isolation valve for unit 9 RRI supplies from unit 1. Function: To RRI044 VN - RRI supply to the waste treatment coolers Failure analysis and classification: valve fails to operate = unable to swop over unit 9 RI supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair to perform steps required by accident/incident procedures (I-RRI) => C9,E6 | CLM
9 | RRI |  |  |  | 9LKI0404 | 9RRI045VN | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Motor isolation valve for unit 9 RRI supplies from unit 2. Function: To RRI045 VN - RRI supply to the waste treatment coolers Failure analysis and classification: valve fails to operate = unable to swop over unit 9RRI supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair to perform steps required by accident/incident procedures (I-RRI) => C9,E6 | CLM
9 | RRI |  |  |  | 9LKI0405 | 9RRI322VN | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Motor isolation valve for unit 9 RRI supplies from unit 1. Function: To RRI322 VN - RRI supply to the waste treatment coolers Failure analysis and classification: valve fails to operate = unable to swop over unit 9RRI supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair to perform steps required by accident/incident procedures (I-RRI) => C9,E6 | CLM
9 | RRI |  |  |  | 9LKI0406 | 9RRI323VN | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 Yearly | 2019 |  | 2 Yearly | 2018 | V&T |  |  |  | Critical |  |  | Motor isolation valve for unit 9 RRI supplies from unit 1. Function: To RRI322 VN - RRI supply to the waste treatment coolers Failure analysis and classification: valve fails to operate = unable to swop over unit 9RRI supplies => S4,E5,E6. -- Failure to function when required for maintenance => E6 -- Failure to function will impair to perform steps required by accident/incident procedures (I-RRI) => C9,E6 | CLM
0 | KRT |  |  |  | 0KRT903CR | 0KRT901PO | [10 empty] | B0602 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump for KRT901MA. Function: recirculates water for sampling. Failure analysis and classification: Component placed in service only when sampling is required. Component failure makes KRT901MA inoperable. OTS allows for grab samples during KER discharge if 901MA is inpoperable. => S4,E6,I1,I4 | SHM
0 | KRT |  |  |  | 0KRT907CR | 0KRT902PO | [10 empty] | B0604 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump for 0KRT902MA. Function: Circulates sampling water. Failure analysis and classification: Component remains in service and is pressurised. => I1,I4 Component failure is a loss of redundancy with only 0KRT903MA available. => S4,A6 | SHS
0 | DVA |  |  |  | 0DVAA20AR | 0DVA030ZV | [10 empty] | B0157 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac switchboard Function: Supply 380 Vac to SHY Plant Failure analysis and classification: Switchboard located in SHY Plant. Switchboard permanently in service => I1,I4 -- Failure to supply 48 Vdc will result in loss of SHY Plant => S4,E6 | SHM
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac switchboard Function: Supply 380 Vac to SHY Plant Failure analysis and classification: Switchboard located in SHY Plant. Switchboard permanently in service => I1,I4 -- Failure to supply 48 Vdc will result in loss of SHY Plant => S4,E6 | SHM
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac switchboard Function: Supply 380 Vac to SHY Plant Failure analysis and classification: Switchboard located in SHY Plant. Switchboard permanently in service => I1,I4 -- Failure to supply 48 Vdc will result in loss of SHY Plant => S4,E6 | SHM
1 | PTR |  |  |  | 1LLI001TB | 1PTR137VB | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLI001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM | Manually operated isolation valve Function: 001 BA outlet towards 001 PO/002 PO suction. Failure analysis and classification: Component normally CLOSED - used for 001 BA water transfer and recirculation. Component located in corrosive and dusty environment => A6,A7 - Failure to function OPEN/CLOSE may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 - Failure to CLOSE (isolate) will prevent maintenance activity downstream of 001 BA => S4,S7,E5. - Failure to OPEN/CLOSE for 001 BA recirculation => E6 Component located in corrosive and dusty environment. => A6,A7 | SLS
1 | KRT |  |  |  | 1KRT021CR | 1KRT001PO | [10 empty] | B0600 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply samples to radiation detector Failure analysis and classification: Component always in service => I1,I4 Failure will result in loss of redundancy => S4,E6 | SHM
1 | KRT |  |  |  | 1KRT025CR | 1KRT002PO | [10 empty] | B0603 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Diaphragm Pump Function: To supply ETY samples to radiation detectors Failure analysis and classification: S4, E5, E6, I1, I4. Failure will result in loss of Defence in Depth => S4 Failure will result in degradation other detectors => E5 Failure will result in entry into OTS (no fallback, but prevents fuel handling) => E6 Component always in service => I1 ,I4 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM001AP | [10 empty] | B0300 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM401BN | 1RAM001AP | [10 empty] | B0301 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM001AP | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM001AP | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM001AP | [10 empty] | B0313 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM002AP | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM002AP | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM002TB | 1RAM002AP | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002AP | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RAM |  |  |  | 1RAM601BN | 1RAM002AP | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | RRB |  |  |  | 1RRB109AR | 1RRB001TB | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1RRB109AR | 1RRB001TB | [10 empty] | B0406 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1RRB209AR | 1RRB002TB | [10 empty] | B0493 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1RRB209AR | 1RRB002TB | [10 empty] | B0511 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
1 | SXS |  |  |  | 1SXS501AR | 1SXS501PO | [10 empty] | B0601 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
1 | SXS |  |  |  | 1SXS501AR | 1SXS503PO | [10 empty] | B0602 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
1 | SXS |  |  |  | 1SXS502AR | 1SXS502PO | [10 empty] | B0701 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
1 | SXS |  |  |  | 1SXS502AR | 1SXS504PO | [10 empty] | B0702 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
1 | ABP |  |  |  | 1LKC0308 | 1ABP035VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolates common drain path from bled steam lines to 301 and 302 RE above 20% secondary power. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure in the open position would reduce plant efficiency and power output at power levels above 20% => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0307 | 1ABP036VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolates common drain path from bled steam lines to 201 and 202 RE above 20% secondary load. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure in the open position would reduce plant efficiency and power output at power levels above 20% => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0303 | 1ABP001VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 002 VV - bled steam from LP1 turbine to 201 RE Failure analysis and classification: Failure to CLOSE will require manual intervention locally =>S4,E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
1 | ABP |  |  |  | 1LKA0309 | 1ABP003VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 004 VV - bled steam from LP1 turbine to 202 RE Failure analysis and classification: Failure to CLOSE will require manual intervention locally =>S4,E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
1 | ABP |  |  |  | 1LKC0302 | 1ABP005VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 006 VV - bled steam from LP2 turbine to 201 RE. Failure analysis and classification: Failure to CLOSE will require manual intervention locally => S4, E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
1 | ABP |  |  |  | 1LKA0308 | 1ABP007VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 008 VV - bled steam from LP2 turbine to 202 RE. Failure analysis and classification: Failure to CLOSE will require manual intervention locally => S4,E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
1 | ABP |  |  |  | 1LKC0301 | 1ABP009VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 010 VV - bled steam from LP3 turbine to 201 RE. Failure analysis and classification: Failure to CLOSE will require manual intervention locally =>S4, E6,E5,I1,I4. High pressure system => I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
1 | ABP |  |  |  | 1LKA0307 | 1ABP011VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 012 VV - bled steam from LP3 turbine to 202 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally =>S4, E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0306 | 1ABP013VV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 014 VV - bled steam from LP1 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKA0312 | 1ABP015VV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 016 VV - bled steam from LP1 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4, E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0305 | 1ABP017VV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 014 VV - bled steam from LP2 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKA0311 | 1ABP019VV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 020 VV - bled steam from LP2 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0304 | 1ABP021VV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 022 VV - bled steam from LP3 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKA0310 | 1ABP023VV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 020 VV - bled steam from LP3 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKC0401 | 1ABP025VV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Bled steam line isolation from HP turbine to 401 RE. Failure analysis and classification: Valve receives auto closing order from Turbine trip, Hi level and Hi Hi level Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE could/will require manual intervention and/or possible damage to major equipment => S4,E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ABP |  |  |  | 1LKA0306 | 1ABP027VV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Bled steam line isolation from HP turbine to 402 RE. Failure analysis and classification: Valve receives auto closing order from Turbine trip, Hi level and Hi Hi level Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE could/will require manual intervention and/or possible damage to major equipment => S4,E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | ACO |  |  |  | 1ACO005CR | 1ACO003VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 002 PO suction Failure Analysis and Classification: Valve operated manually from local cabinet 005 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then AC O needs to be shutdown.=> possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ACO |  |  |  | 1ACO004CR | 1ACO001VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 001 PO suction Failure Analysis and Classification: Valve operated manually from local cabinet 004 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown => possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ACO |  |  |  | 1ACO006CR | 1ACO006VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 001 PO discharge valve Failure Analysis and Classification: Valve operated manually from local cabinet 006CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown => possible C2.)This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ACO |  |  |  | 1ACO007CR | 1ACO011VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the pump -> E2 | EHM | Motor operated isolation valve Function: 002 PO discharge valve Failure Analysis and Classification: Valve operated manually from local cabinet 007 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown.=> possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AGM |  |  |  | 1LKF0505 | 1AGM001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - motor driven lube oil pump (start-up and cost down operation) Pump required to run during APA 003 PO pump start-up and coast down - Failure to provide lube oil pressure at start-up makes APA 003 PO unavailable. Malfunction will result in inoperability of the APA 003 PO (no speed control) Lost of redundancy=>S4,E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 Failure to provide lube oil pressure at coast down (and bearings cooling function for 1 0 min after APA 003 PO stop) => E5 | SLM
1 | AGR |  |  |  | 1LKD0406 | 1AGR003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 001 PO - lube and control oil pump Non essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
1 | AGR |  |  |  | 1LLC0101 | 1AGR004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 002 PO - lube and control oil pump Essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
1 | AGR |  |  |  | 1LLE0202 | 1AGR005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 001 PO - lube and control oil pump Essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
1 | AGR |  |  |  | 1LKD0407 | 1AGR006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 002 PO - lube and control oil pump Non essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
1 | AHP |  |  |  | 1LKA0303 | 1AHP001VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation to 501 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating) after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKA0302 | 1AHP005VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation - 601 RE outlet Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating) after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKC0402 | 1AHP006VL | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation to 502 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 2 heaters back in service (or de-isolating) after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKC0403 | 1AHP010VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation downstream of 602 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating)after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKA0301 | 1AHP011VL | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: HP heaters by-pass line isolation Failure analysis and classification: Valve normally closed. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to operate when required makes maintenance on either line impossible =>S4,E2,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKC0805 | 1AHP018VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: 501/502 RE - drain to 003 BA on bledsteam supply line Failure analysis and classification: Valve drains accumulated condensate in the GPV bled steam supply line to No.5 HP heaters during startup and at power transients of between 0% and 20%. Failure to open/close by logic control generates alarm after 40 seconds. Exposed to water/condensate impingement during low power transients => A7 - Failure to close either by motor or manually will result in loss of efficiency => S4,E5,E6Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to open during power transient may require manual intervention locally => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKC0806 | 1AHP027VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: 601/602 RE - drain to 003 BA on bledsteam supply line Failure analysis and classification: Valve drains accumulated condensate in the GPV bled steam supply line to No.6 HP heaters during startup and at power transients of between 0% and 50%. Failure to open/close by logic control generates alarm after 40 seconds. Exposed to water/condensate impingement during low power transients => A7 - Failure to close either by motor or manually will result in loss of efficiency => S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to open during power transient may require manual intervention locally => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | AHP |  |  |  | 1LKA0401 | 1AHP001VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 501 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 501 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKA0402 | 1AHP002VV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 501 RE - main bledsteam line - by-pass to 001 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 001 VV prevents 001 VV from opening if 002 VV not fully open. - CLOSING function is Hi Hi level in 501 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKC0404 | 1AHP004VV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 502 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 502 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKC0405 | 1AHP005VV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 502 RE - main bledsteam line - by-pass to 004 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock prevents 004 VV from opening if 005 VV not fully open. - CLOSING function is Hi Hi level in 502 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKA0403 | 1AHP007VV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 601 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 601 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKA0404 | 1AHP008VV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 601 RE - main bledsteam line - by-pass to 007 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 007 VV prevents 007 VV from opening if 008 VV not fully open. - CLOSING function is Hi Hi level in 601 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKC0406 | 1AHP010VV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 602 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 602 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | AHP |  |  |  | 1LKC0407 | 1AHP011VV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 602RE - main bledsteam line - by-pass to 010 VV Failure analysis and classification: Valve normally OPEN. Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 010 VV prevents 010 VV from opening if 011VV not fully open. - CLOSING function is Hi Hi level in 602 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | APA |  |  |  | 1APA002CR | 1APA001VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 001VL control. Cabinets classified as RTF. | RTM | Motor operated isolation valve Function: To isolate 003 PO suction (upstream 001 FI) Failure analysis and classification: Valve intended for the maintenence purposes, normally open if pump in standby mode - operated manually from local cabinet 002 CR. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | APA |  |  |  | 1APA003CR | 1APA003VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 003 VL control. Cabinets classified as RTF. | RTM | Motor operated isolation valve Function: To isolate 003 PO suction (downstream 001 FI) Failure analysis and classification: Valve intended for the maintenence purposes, normally open from 003 CR if pump in operation or in standby mode. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | APA |  |  |  | 1APA004CR | 1APA005VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 005VL control. Cabinets classified as RTF. | RTM | Motor operated isolation valve Function: To isolate 003 PO discharge Failure analysis and classification: Valve intended for the maintenence purposes, normally open if pump in standby mode - operated manually from local cabinet 007 CR. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities =>S7 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 | SLS
1 | APA |  |  |  | 1LKS0202 | 1APA001RS | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater Function: To keep the out-of-service motor free from moisture Failure analysis and classification: Deterioration of the insulation due to misture is applicable only if pump is in standby => S4,I4 | SHM
1 | ATE |  |  |  | 1ATE009CR | 1ATE915VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 903 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ATE |  |  |  | 1ATE008CR | 1ATE909VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 902 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ATE |  |  |  | 1ATE007CR | 1ATE903VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 901 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | ATE |  |  |  | 1ATE006CR | 1ATE913VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 903 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
1 | ATE |  |  |  | 1ATE005CR | 1ATE907VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 902 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
1 | ATE |  |  |  | 1ATE004CR | 1ATE901VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 901 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
1 | ATE |  |  |  | 9LKN0512 | 1ATE001PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Acid reclaiming pump. Function: Transfer acid as required for resin regeneration. Failure analysis and classification: Component in service only on regeneration=<50%. Component failure would delay resin regeneration. => E6 Component body or flange failure would constitute a safety hazard to personnel if the acid leaves the bund area. => S1 | SLM
1 | ATE |  |  |  | 1ATE010CR | 1ATE011PO | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Caustic soda pump. Function: Transfer caustic soda for resin regeneration. Failure analysis and classification: Component in service from time to time.=<50%. Component failure would delay resin regeneration. => E6 Component body or flange failure would constitute a safety hazard to personnel if the caustic soda leaves the bund area. => S1 | SLM
1 | CAP |  |  |  | 1LKC0512 | 1CAP008VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: To remotely drain excess water from the condenser on a high level alarm threshold towards SXS system from CEX pumps discharge header at a max. rate 0f 200 t/h. Failure analysis and classification: Failure to open : Failure to remotely discharge excess water from a condenser high condensate level condition on demand. Manual actuation of valve via handwheel still possible => S4,E5,E6. Manual handwheel Failure to open => high condenser level uncontrollable, (tube leak, all make up flow isolated), unit load to be reduced, with eventual unit shutdown =>C2,S4,E5 Failure to close : Pre-outage drainage, no impact, outage time to repair => E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | CET |  |  |  | 1LKC0409 | 1CET001VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate turbine gland steam header - VVP steam supply line Valve normally closed above 50% turbine load if steam header pressure is higher then 110 kPa abs Valve receive opening order if VVP live steam pressure is higher than 2 Map and steam header pressure is less than 110 kPa abs. Failure analysis and classification: Failure to operate as required (open/close on demand) => S4,E5,E6 - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | CET |  |  |  | 1LKC0410 | 1CET010VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate turbine gland steam header - SVA steam supply line Failure analysis and classification: Valve normally closed above 50% turbine load if steam header pressure is higher then 110 kPa abs Valve receive opening order if VVP live steam pressure is higher than 2 MPa - Failure to operate as required (open/close on demand) => S4,E5,E6 - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | CEX |  |  |  | 1CEX006CR | 1CEX013VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 003 PO suction. Failure analysis and classification: Component remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
1 | CEX |  |  |  | 1CEX005CR | 1CEX007VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 002 PO suction. Failure analysis and classification: Component remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
1 | CEX |  |  |  | 1CEX004CR | 1CEX001VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Local control box of the isolation valve to the pump discharge power on TEM CEX On failure -> Unable to operate the valve electrically -> risk of having a pump CEX unavailable -> E6 | EHM | Motor operated isolation valve Function: Isolates 001 PO suction. Failure analysis and classification: Component remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
1 | CEX |  |  |  | 1LKA0409 | 1CEX003VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 001 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SHM
1 | CEX |  |  |  | 1LKA0410 | 1CEX009VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 002 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SHM
1 | CEX |  |  |  | 1LKA0610 | 1CEX015VL | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 003 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
1 | CRF |  |  |  | 1LKG0210 | 1CRF004PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | CRF pump stuffing box supply pump. Function: Supply stuffing box water. Failure analysis and classification: Redundancy with 005 PO Component 50% in service. Component failure would require the standby pump to run to maintain the CRF pump stuffing boxes wet with potable water, to prevent a forced shutdown of the in service CRF pumps. => S4,E6 Component in extremely corrosive environment. => A6 | SLS
1 | CRF |  |  |  | 1LKG0211 | 1CRF005PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | CRF pump stuffing box supply pump. Function: Supply stuffing box water. Failure analysis and classification: Redundancy with 004 PO Component 50% in service. Component failure would require the standby pump to run to maintain the CRF pump stuffing boxes wet with potable water, to prevent a forced shutdown of the in service CRF pumps. => S4,E6 Component in extremely corrosive environment. => A6 | SLS
1 | CRF |  |  |  | 1LKG0301 | 1CRF001RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 001 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 | SHM
1 | CRF |  |  |  | 1LKG0412 | 1CRF002RS | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 002 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 | SHM
1 | CRF |  |  |  | 1LKG0401 | 1CRF003RS | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 003 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 | SHM
1 | CVI |  |  |  | 1LKC0202 | 1CVI019VA | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
1 | CVI |  |  |  | 1LKC0201 | 1CVI020VA | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
1 | CVI |  |  |  | 1LKC0310 | 1CVI021VA | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
1 | CVI |  |  |  | 1LKC0812 | 1CVI003VV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolating valve. Function : To provide steam injection isolation to 003 EJ booster air ejector from steam barrel (SVA-1.2 MPa). Booster air ejector to boost vacuum pump inlet pressure when CRF temperatures lower than normal (higher vacuum pressure causes inefficient vacuum pump operation). Failure Analysis and Classification: • Fails to CLOSE/jammed OPEN; - Loss of energy/steam to atmosphere, can not be repaired on line due to lack of isolation capabilities => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, vacuum pumps performance/efficiency will tend to degrade, temperature increase in vacuum pump circuit, tripping of vacuum pump, inability to maintain efficient condenser cycle => S4. | SLM
1 | DEL |  |  |  | 1LLA0309 | 1DEL001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - chilled water circulating - train A. Loss of cooling water flow could result in loss of DVL cooling. (No credit for train B) Component 50% in service. | SLM
1 | DEL |  |  |  | 1LLB0302 | 1DEL002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - chilled water circulating - train B. Loss of cooling water flow could result in loss of DVL cooling. (No credit for train A) Component 50% in service. | SLM
1 | DEL |  |  |  | 1LLA0105 | 1DEL001GF | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train A. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train B) | SHM
1 | DEL |  |  |  | 1LLB0107 | 1DEL002GF | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train B. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train A) | SHM
1 | DEL |  |  |  | 1LLA0105 | 1DEL001GF | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train A. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train B) | SHM
1 | DEL |  |  |  | 1LLB0107 | 1DEL002GF | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train B. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train A) | SHM
1 | DMG |  |  |  | 1LKG0406 | 1DMG001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMG |  |  |  | 1LKG0407 | 1DMG002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMG |  |  |  | 1LKG0408 | 1DMG003PR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMG |  |  |  | 1LKG0409 | 1DMG004PR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMK |  |  |  | 1LKL0202 | 1DMK001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMK |  |  |  | 1LKL0201 | 1DMK002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMM |  |  |  | 9DMM001CR | 1DMM001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMR |  |  |  | B0406 | 1DMR002PA | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMR |  |  |  | DFH | 1DMR001PR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. A functional failure of the component will result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMR |  |  |  | BGJ | 1DMR001PR | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. A functional failure of the component will result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMR |  |  |  | G0103 | 1DMR003PR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMR |  |  |  | 1LKF0401 | 1DMR004PA | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMW |  |  |  | 1LKD0410 | 1DMW003PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMW |  |  |  | 1LKD0412 | 1DMW004PR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMX |  |  |  | 1LKH0201 | 1DMX001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMX |  |  |  | 1LKH0312 | 1DMX002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMX |  |  |  | 1LKF0309 | 1DMX004PR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMX |  |  |  | 1LLG0104 | 1DMX005PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DMX |  |  |  | 1LLW0104 | 1DMX006PR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
1 | DVC |  |  |  | 1DVC004CR | 1DVC008RS | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater in booster iodine supply fans DVC 002 ZV and DVC 003 ZV inlet duct - Train B Purpose - to condition iodine filters while DVC 002 ZV in operation. Component periodically tested for functionality (SRSM - 1 RO @ any domain) => NO C2 - repair does not affect outage duration Because affects iodine filter operability => NO C3,S4 and E5 | SHM
1 | DVC |  |  |  | 1DVC011CR | 1DVC009RS | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Box connection to JDT 004 and CR 005. Contains only terminals. Failure: No light installed hardware with this kit ---> RTF | RTM | Electric heater in booster iodine supply fans DVC 002 ZV and DVC 003 ZV inlet duct - Train A Purpose - to condition iodine filters while DVC 001 ZV in operation. Component periodically tested for functionality (SRSM - 1 RO @ any domain) => NO C2 - repair does not affect outage duration Because affects iodine filter operability => NO C3,S4 and E5 | SHM
1 | DVC |  |  |  | 1LLB0303 | 1DVC002ZV | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | The booster iodine supply fan DVC 002 ZV - Train A (normally on standby) Component periodically tested for functionality (SRSM - 1 RO @ in any state => component fails PT => NO C3 but S4 and E6. | SLM
1 | DVC |  |  |  | 1LLA0308 | 1DVC001ZV | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | The booster iodine supply fan DVC 001 ZV - Train A (normally on standby) Component periodically tested for functionality (SRSM - 1 RO @ in any state => component fails PT => NO C3 but S4 and E6. | SLM
1 | DVC |  |  |  | 1LLB0101 | 1DVC004ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Normal ventilation fan DVC 004 ZV - Train B (50% duty cycle) Component periodically tested for functionality (start - stop) - (SRSM - 5 RO @ RCD) => if component fails PT => NO C2 - repair has no affect on outage duration. Associated motor periodically tested for vibration (6 monthly - KLM 008) => if component fails the test => NO C3 but S4 Component failure while in service => NO C3 but S4 Component failure while in the back-up auto start configuration =>NO C3 but S4,E6 | SLM
1 | DVC |  |  |  | 1LLA0207 | 1DVC003ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Normal ventilation fan DVC 003 ZV - Train A (50% duty cycle) Component periodically tested for functionality (start - stop) - (SRSM - 5 RO @ RCD) => if component fails PT => NO C2 - repair has no affect on outage duration. Associated motor periodically tested for vibration (6 monthly - KLM 008) => if component fails the test => NO C3 but S4 Component failure while in service => NO C3 but S4 Component failure while in the back-up auto start configuration =>NO C3 but S4,E6 | SLM
1 | DVE |  |  |  | 1LKC0807 | 1DVE001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | TRICASTIN CLASSIFICATION USED Cabinet incorporating information provided by the DVE 006, 010, 011 & 014ST (fire protection Anfi-RS) ---> Same rank as T -> S1, S4, E6 | SHM
1 | DVE |  |  |  | 1LLB0301 | 1DVE003ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train B Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLA0306 | 1DVE001ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train A Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLB0401 | 1DVE004ZV | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train B Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLA0305 | 1DVE002ZV | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train A Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLB0402 | 1DVE006ZV | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B battery room exhaust fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
1 | DVE |  |  |  | 1LLA0304 | 1DVE005ZV | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A battery room exhaust fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
1 | DVE |  |  |  | 1LLB0402 | 1DVE008ZV | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B battery room supply fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
1 | DVE |  |  |  | 1LLA0303 | 1DVE007ZV | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - Unit 9 battery room and 7m electrical boards exhaust fan. . Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
1 | DVE |  |  |  | 1LLB0301 | 1DVE010ZV | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLA0306 | 1DVE009ZV | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLB0401 | 1DVE012ZV | [10 empty] | B0036 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLA0305 | 1DVE011ZV | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
1 | DVE |  |  |  | 1LLA0304 | 1DVE013ZV | [10 empty] | B0039 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A battery room supply fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
1 | DVE |  |  |  | 1LLI0308 | 1DVE014ZV | [10 empty] | B0041 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Unit 0 battery room on 24m Lvl Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
1 | DVF |  |  |  | 1LLA0302 | 1DVF001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - smoke exhaust. Entry into OTS if inoperable (without fall-back)=> NO C3,S4. | SLM
1 | DVF |  |  |  | 1LLB0403 | 1DVF002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - smoke exhaust. Entry into OTS if inoperable (without fall-back)=> NO C3,S4. | SLM
1 | DVK |  |  |  | 1LLI0305 | 1DVK003RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater - iodine line common inlet duct SRSM requirement - 1RO heater auto ON/OFF test from starting/stopping 003 ZV => NO C3, S4 SRSM requirement - 5 yearly verification of the heating capacity | SLM
1 | DVK |  |  |  | 1LLJ0309 | 1DVK002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater - iodine line common inlet duct SRSM requirement - 1RO heater auto ON/OFF test from starting/stopping 002 ZV => NO C3, S4 SRSM requirement - 5 yearly verification of the heating capacity | SLM
1 | DVL |  |  |  | 1LLA0401 | 1DVL101ZV | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - stairs U1 supply. Failure can be mitigated with creating draft by opening doors 0 & 24 m Lvl => E6 Partial inoperability of DVL is an OTS Group 2 event => S4 Fan continuously in service => I1 | SHM
1 | DVL |  |  |  | 1LLB0406 | 1DVL104ZV | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - SAP compressors room train B cooling. Function: Cools the emergency compressor room while the compressor is in service. Failure could render emergency compressor train inoperable. => S4,E6 | SLM
1 | DVL |  |  |  | 1LLA0402 | 1DVL102ZV | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - stairs U1 exhaust. Failure can be mitigated with creating draft by opening doors 0 & 24 m Lvl => E6 Failure of 1DVL 102 ZV will mean that there will be no ventilation exhaust from rooms L701, L601, L501, L403, L304, L202, L608, L508, L407 and L307. Proper cooling of these areas cannot be guaranteed if the exhaust fan fails. Partial inoperability of DVL is an OTS Group 2 event => S4 Fan continuously in service => I1 | SHM
1 | DVL |  |  |  | 1LLB0408 | 1DVL203ZV | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train B supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
1 | DVL |  |  |  | 1LLA0403 | 1DVL103ZV | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - SAP compressors room train A cooling. Function: Cools the emergency compressor room while the compressor is in service. Failure could render emergency compressor train inoperable. => S4,E6 | SLM
1 | DVL |  |  |  | 1LLB0407 | 1DVL204ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train B supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
1 | DVL |  |  |  | 1LLA0404 | 1DVL201ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train A supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
1 | DVL |  |  |  | 1LLA0405 | 1DVL202ZV | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train A supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
1 | DVN |  |  |  | 1LKJ0103 | 1DVN007ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB Iodine air extraction fan. Function: Iodine extraction fan. Failure analysis: fan fails to start.=>S1,E5,E6 Component used to exhaust air from the NAB possible Iodine contaminated rooms. => S1 Component normally in service and pressurised as per OPS Regime on bypass. => I1,I4 PSA Significant Component => S6. | SHM
1 | DVN |  |  |  | 1DVN001BX | 1DVN001ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB supply air fan. Component used to supply air to the NAB common rooms. PSA Significant Component => S6. | SLM
1 | DVN |  |  |  | 1DVN004BX | 1DVN004ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB exhaust air fan. Component used to exhaust air from the NAB common rooms. PSA Significant Component => S6. | SLM
1 | DVW |  |  |  | 1LLA0410 | 1DVW001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Filter common suction duct - Train A electric heater SRSM requirement - 1RO verify correct operation => NO C3, S4 SRSM requirement - 5 years verify heating capacity => NO C3, S4 | SLM
1 | DVW |  |  |  | 1LLB0512 | 1DVW002RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Filter common suction duct - Train B electric heather SRSM requirement - 1RO verify correct operation => NO C3, S4 SRSM requirement - 5 years verify heating capacity => NO C3, S4 | SLM
1 | DVW |  |  |  | 1LLC0307 | 1DVW001ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extraction fan Function: Train A - Iodine extraction fan - peripheral rooms ventilation Failure analysis and classification: - Failure to function in "when require operating state" may reresult in inefficiency of the iodine filtration, DVN KRT may be activated => S1 - Failure to function will require OTS entry, but with no fallback constraints => S4,E6 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) => S4 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) on SI signal - outage => S4 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
1 | DVW |  |  |  | 1LKH0402 | 1DVW003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Train A - normal extraction fan Function: To keep the periferal room under negative pressure and to keep iodine filters conditioned. Failure analysis: Component always in service and pressurised. => I1,I4 003ZV fails to start .=>S1,E5,E6. SRSM requirement - 1RO verify correct operation of the fan (and associated logic)=> E6 | SHM
1 | DVW |  |  |  | 1LLD0307 | 1DVW002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extraction fan Function: Train B - Iodine extraction fan - peripheral rooms ventilation Failure analysis and classification: - Failure to function in "when require operating state" may reresult in inefficiency of the iodine filtration, DVN KRT may be activated => S1 - Failure to function will require OTS entry, but with no fallback constraints => S4,E6 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) => S4 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) on SI signal - outage => S4 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
1 | EAS |  |  |  | 1LLD0401 | 1EAS132VB | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 002 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 134 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
1 | EAS |  |  |  | 1LLC0301 | 1EAS131VB | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 001 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 133 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
1 | EAS |  |  |  | 1LLD0402 | 1EAS134VB | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 002 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 132 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
1 | EAS |  |  |  | 1LLC0401 | 1EAS133VB | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 001 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 131 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
1 | EVC |  |  |  | E0103 | 1EVC001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
1 | EVC |  |  |  | B0406 | 1EVC002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
1 | EVC |  |  |  | E0406 | 1EVC003ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
1 | EVC |  |  |  | B0709 | 1EVC004ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
1 | EVF |  |  |  | CGJ | 1EVF001RS | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater electric. Failure (does not heat, thus reducing the efficacy of the PI) may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure (does not heat, thus reducing the efficacy of the PI) will reduce necessary redundancy => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
1 | EVF |  |  |  | DHK | 1EVF002RS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater electric R243. Failure (does not heat, thus reducing the efficacy of the PI) may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure (does not heat, thus reducing the efficacy of the PI) will reduce necessary redundancy => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
1 | EVF |  |  |  | A0103 | 1EVF001ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R310. Failure to circulate air may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure to circulate air will reduce necessary redundancy => S4. | SLM
1 | EVF |  |  |  | A0406 | 1EVF002ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R310. Failure to circulate air may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure to circulate air will reduce necessary redundancy => S4. | SLM
1 | EVR |  |  |  | CFJ | 1EVR001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 1 Failure analysis and classification: The component is continuously in service and energised => I1,I4 - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
1 | EVR |  |  |  | CFJ | 1EVR002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 2 Failure analysis and classification: The component is 50% in service. - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
1 | EVR |  |  |  | E0709 | 1EVR005ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Containment dome recirculation fan Failure analysis and classification: Component 50% in service. -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function "when required" will result in reduction in necessary redundancy => S4 . | SLM
1 | EVR |  |  |  | BEH | 1EVR003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 2 Failure analysis and classification: The component is 50% in service. - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
1 | EVR |  |  |  | E1618 | 1EVR004ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Containment dome recirculation fan Failure analysis and classification: Component 50% in service. -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function "when required" will result in reduction in necessary redundancy => S4 . | SLM
1 | GEV |  |  |  | 1GEV002CR | 1GEV011AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 001 TP inside 011 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 126 EC OLTC 1 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | GEV |  |  |  | 1GEV002CR | 1GEV012AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 002 TP inside 012 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 127 EC OLTC 2 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | GEV |  |  |  | 1GEV002CR | 1GEV013AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 003 TP inside 013 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 128 EC OLTC 3 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | GEX |  |  |  | 1LKC0610 | 1GEX004TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Emergency excitation transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: When in service: (due to the unavailability of GEX001/2/3TR), it is permanently in service =>I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 When not in service: -- Functional failure of the transformer will result in a reduction of “defence in depth” Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | GFR |  |  |  | 1LKA0504 | 1GFR001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - boosting pump for HP pumps 003 /004 PO. Component always in service and pressurised. => I1 ,I4 Functional Failure will require standby pump 002 PO to be placed in service => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SHM
1 | GFR |  |  |  | 1LKC0712 | 1GFR002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - boosting pump for HP pumps 003 /004 PO. Component always in service and pressurised. => I1 ,I4 Functional Failure will require standby pump 001PO to be placed in service => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SHM
1 | GFR |  |  |  | 1LKA0209 | 1GFR003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - HP. Component always in service and pressurised. => I1 ,I4 ,A2 Functional Failure will require standby pump 004 PO to be placed in service. => S4 , E6. Component failure during startup testing could delay the outage by more than 12 hours. => C2 | SHS
1 | GFR |  |  |  | 1LKC0209 | 1GFR004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - HP. Component always in service and pressurised. => I1 ,I4 ,A2 Functional Failure will require standby pump 004 PO to be placed in service. => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SHS
1 | GGR |  |  |  | 1LKF0511 | 1GGR204VN | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated preset valve (servomotor) Function: To regulate (adjust) SRI flow rate through the coolers (001 and 002 RF). Failure analysis and classification: Valve continuously in srevice to control SRI flow rate accordingly to lube oil temperature setpoint => I3. DAN! - Failure to function could lead to unacceptable lube oil temperature => S4,E5. force manual - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E6 | SHM
1 | GGR |  |  |  | 1LKA0503 | 1GGR009ZV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - 009 BA gas extraction Component always required to be in service and pressurised. => I1,i4 Fan required in service according to the safety regulations to extract explosive gases (hydrogen) from oil => S1, S5, E5 | SHM
1 | GGR |  |  |  | 1GGR010BX | 1GGR010PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Jacking oil pump Failure analysis and classification: Only one jacking oil pump required for turbine barring and run-up. Pump required to be in service up to 500 rpm during turbine run-up. (011 PO equivalent) => S4,E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | GGR |  |  |  | 1GGR011BX | 1GGR011PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Jacking oil pump Failure analysis and classification: Only one jacking oil pump required for turbine barring and run-up. Pump required to be in service up to 500 rpm during turbine run-up. (010 PO equivalent) => S4,E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
1 | GGR |  |  |  | 1GGR001AR | 1GGR020MO | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. | RTM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
1 | GGR |  |  |  | 1GGR001AR | 1GGR020MO | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. | RTM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
1 | GGR |  |  |  | 1GGR001AR | 1GGR020MO | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. | RTM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
1 | GGR |  |  |  | 1GGR001GA | 1GGR059CR | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Alternator Function: To supply 001MO/001PO Failure analysis and classification: Component continuously in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an immediate production loss > 20% => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | CHM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
1 | GGR |  |  |  | 1GGR001GA | 1GGR059CR | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Alternator Function: To supply 001MO/001PO Failure analysis and classification: Component continuously in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an immediate production loss > 20% => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | CHM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
1 | GGR |  |  |  | 1GGR001AR | 1GGR059CR | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. | RTM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
1 | GHE |  |  |  | 1LLI0408 | 1GHE003PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380V AC standby emergency seal oil pump. -Provides a small amount of detrained oil back to the seal oil supply to the generator seal oil circuit, while the bulk is returned to 004 DZ air detraining tank. - Receives inlet supply from GGR lube oil circuit. - Fails to pump, reduction in defence of depth, requires emergency DC seal oil pump 004 PO to operate => S4, E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
1 | GHE |  |  |  | 1LKE0302 | 1GHE006ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Spark resistant centrifugal fan for 004 DZ air detraining tank. -Generates input to KIT when on 012 EC. -Removes air and possible "spill over" hydrogen vapour from the gaseous portion of 004 DZ detraining tank to atmosphere. - Failure to degas 004 DZ will not render the seal oil system inoperable. The degassing function will be ensured by the GGR vapour exhauster (KWB-S.GHE). -The hydrogen purity within the alternator should be checked and increased if the purity level drops to below 96%. -Reduction of defence in depth => S4, I1, I4. | SHM
1 | GPV |  |  |  | 1LKC0711 | 1GPV051VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - Drain line from 001 BA to AHP 003 BA via 031 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from CET001BA Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
1 | GPV |  |  |  | 1LKC0710 | 1GPV052VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from GV's to AHP 003 BA via 038 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
1 | GPV |  |  |  | 1LKC0709 | 1GPV053VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from GV's to AHP 003 BA via 039 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
1 | GPV |  |  |  | 1LKC0708 | 1GPV054VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from RSV's to AHP 003 BA via 033 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
1 | GPV |  |  |  | 1LKC0707 | 1GPV055VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from HP turbine exhaust to AHP 003 BA Off power drain valve Function: To isolate drain path from HP turbine Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
1 | GSE |  |  |  | 1LKA0501 | 1GSE003AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1GSE003AR | 1GRE002AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
1 | GSE |  |  |  | 1GSE003AR | 1GRE002AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
1 | GSE |  |  |  | 1GSE005AR | 1GRE002AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
1 | GSE |  |  |  | 1GSE005AR | 1GSE003AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1GSE005AR | 1GSE003AR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1GSE005AR | 1GSE003AR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1GSE005AR | 1GSE003AR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1LKA0501 | 1GSE003AR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSE |  |  |  | 1GSE005AR | 1GSE003AR | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
1 | GSS |  |  |  | 1LKC0706 | 1GSS001VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: To isolate heating steam line towards 100 & 300 ZZ - main valve. Failure analysis and classification: Valve receives opening order @ T>238 degC (+/- 30%PE) and remain open during higher power operation. Valve receives closing order on turbine trip signal - (no consequences since GPV valves will close first) - Failure to open will result in delay during start-up (power escalation) => C2. - Failure to close on turbine trip signal - (no serious consequences since GPV valves will close first) => S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | GSS |  |  |  | 1LKC0705 | 1GSS002VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: To isolate heating steam line towards 200 & 400 ZZ - main valve. Failure analysis and classification: Valve receives opening order @ T>238 degC (+/- 30%PE) and remain open during higher power operation. Valve receives closing order on turbine trip signal - (no consequences since GPV valves will close first) - Failure to open will result in delay during start-up (power escalation) => C2. - Failure to close on turbine trip signal - (no consequences since GPV valves will close first) => E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | GSS |  |  |  | 1LKC0704 | 1GSS005VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To drain condensation from the steam line downstream of 001/003 VV to the AHP 001 BA Failure analysis and classification: Valve open during startup. Require to auto close when 001 VV not closed. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | GSS |  |  |  | 1LKC0703 | 1GSS006VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To drain condensation from the steam line downstream of 002/004 VV to the AHP 001 BA Failure analysis and classification: Valve open during startup. Require to auto close when 002 VV not closed. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
1 | GSS |  |  |  | 1LKC0702 | 1GSS121VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve . Function: 100 & 300 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | SLM
1 | GSS |  |  |  | 1LKC0701 | 1GSS122VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve . Function: 100 & 300 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | SLM
1 | GSS |  |  |  | 1LKC0802 | 1GSS222VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve , Function:-To drain 200 & 400 ZZ tube bundle of condensate towards AHP 602RE Start-up drain path Failure analysis: Fails to close or is not leak tight => S4,E5,E6 Fails to open or is not fully open =>S4,E5,E6 Repair time < 36 Hrs => NO C2 | SLM
1 | GST |  |  |  | 1LKE0209 | 1GST001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Stator cooling pump Failure analysis and classification: Pump continuously in service => I1 - Failure to function will render pump inoperable and if: in service (credit taken for second stand-by pump with auto start) => S4 when on stand-by as a back-up pump => C2,S4 Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | GST |  |  |  | 1LKS0209 | 1GST002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Stator cooling pump Failure analysis and classification: Pump continuously in service => I1 - Failure to function will render pump inoperable and if: in service (credit taken for second stand-by pump with auto start) => S4 when on stand-by as a back-up pump => C2,S4 Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | GSY |  |  |  | 1LKB0203 | 1GSY001MO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Electric motor Function: To drive cooling fan for 24 KV busbars. Failure analysis and classification: The motor drives 001 ZV which in turn drives 003 ZV Component in service 50% due to a train A and Train B. - Fan/motor condition is monitored during OPS rounds. Upon malfunction, the stand-by train can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
1 | GSY |  |  |  | 1LKC0103 | 1GSY002MO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Electric motor Function: To drive cooling fan for 24 KV busbars. Failure analysis and classification: The motor drives 002 ZV which in turn drives 004 ZV Component in service 50% due to fan set 001/3 ZV and fan set 002/4 ZV running 2 months on 2 months off. - Fan/motor condition is monitored during OPS rounds. Upon malfunction, the stand-by train can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
1 | GSY |  |  |  | 1LKB0309 | 1GSY006ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Alternator terminal box cooling fan Failure analysis and classification: Component in service 50% due to fan 006 ZV and fan 007 ZV running 2 months on 2 months off. - Fan condition is monitored during OPS rounds. Upon malfunction, the fan on stand-by can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
1 | GSY |  |  |  | 1LKB0310 | 1GSY007ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Alternator terminal box cooling fan Failure analysis and classification: Component in service 50% due to fan 006 ZV and fan 007 ZV running 2 months on 2 months off. - Fan condition is monitored during OPS rounds. Upon malfunction, the fan on stand-by can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
1 | JPD |  |  |  | 1LLD0509 | 9JPD610VE | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve on JPD system. Function: To isolate section of JPD Component pressurised. => I4 Failure analysis: Fails to operate (open/close) the valve.=> S1,S4,E5,E6. Mechanical operation/open/close limits not functioning=> E6. | SHM
1 | JPP |  |  |  | 1LLE0701 | 1JPP002VE | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated valve . 1JPP001BA filling valve Function: To fill and maintain 001BA level at programed level. Failure analysis: Fails to operate (open/close) the valve => S1,E6. Mechanical operation/open/close limits not functioning=>E6. | SLM
1 | LAB |  |  |  | 1LLI0105 | 1LAB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 2 3 0 V DC to LAB 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 004 PO - "first" emergency lube oil pump - running continuously 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4 , E6 -- Functional failure of the component could result in loss of GGR004 PO leading to damage to the turbine bearings => E5 | SHS
1 | LAC |  |  |  | 1LKH0105 | 1LAC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 2 3 0 V DC to LAC 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 003 PO ("second" emergency lube oil pump - starting on low pressure), and GHE 004 PO (emergency seal oil pump - starting on low pressure). 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4 , E6 | SHS
1 | LAC |  |  |  | 1LKH0105 | 1LAC001RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 2 3 0 V DC to LAC 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 003 PO ("second" emergency lube oil pump - starting on low pressure), and GHE 004 PO (emergency seal oil pump - starting on low pressure). 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4 , E6 | SHS
1 | LAC |  |  |  | 1LAC03 | 1GHE004PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Standby emergency seal oil pump 004 PO. Failure analysis and classification: Pump may only run for approx. 2 - 4 hrs from LAC batteries. Pump receives auto start order upon low discharge pressure of pumps 001 and 003 PO - (003 PO is diessel backed). - Failure to supply detrained seal oil to the generator seal circuit, while the other pumps are not available, will require turbine load reduction (seals supply from GGR) and loss of H2=> S1, S4 - Failure to function correctly should need an outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
1 | LAC |  |  |  | 1LAC03 | 1GHE004PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Standby emergency seal oil pump 004 PO. Failure analysis and classification: Pump may only run for approx. 2 - 4 hrs from LAC batteries. Pump receives auto start order upon low discharge pressure of pumps 001 and 003 PO - (003 PO is diessel backed). - Failure to supply detrained seal oil to the generator seal circuit, while the other pumps are not available, will require turbine load reduction (seals supply from GGR) and loss of H2=> S1, S4 - Failure to function correctly should need an outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
1 | LBA |  |  |  | 1LLE0401 | 1LBA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBA feeder diagram indicates that loss of LBA001RD will result in loss of LBA001TB. Therefore the loss of LBA001RD shall have the same classification as LBA001TB => C1,C2,C3,C4,C6,C7,C8,C9,S1,S3,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LBA |  |  |  | 1LLC0407 | 1LBA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBA feeder diagram indicates that loss of LBA002RD will result in loss of LBA001TB. Therefore the loss of LBA002RD shall have the same classification as LBA001TB => C1,C2,C3,C4,C6,C7,C8,C9,S1,S3,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LBB |  |  |  | 1LLB0509 | 1LBB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 125 V DC. Function: To provide trn A with 125v DC and charge 001BT Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. The battery life will allow for operator action to supply the board from a charger. =>C2,S4,E5. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LBB |  |  |  | 1LLD0405 | 1LBB002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 125 V DC. Function: To provide trn A with 125v DC and charge 001BT Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. The battery life will allow for operator action to supply the board from a charger. =>C2,S4,E5. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LCA |  |  |  | 1LLA0506 | 1LCA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCA 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCA switchboard results in the loss of all digital control and indication for Train A and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LCA |  |  |  | 1LLE0403 | 1LCA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by LCA 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCA switchboard results in the loss of all digital control and indication for Train A and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LCB |  |  |  | 1LLB0505 | 1LCB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCB 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCB switchboard results in the loss of all digital control and indication for Train B and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LCB |  |  |  | 1LLD0406 | 1LCB002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCB 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCB switchboard results in the loss of all digital control and indication for Train B and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
1 | LCC |  |  |  | 1LLA0505 | 1LCC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function:To provide 48v DC supply to 001TB and to charge 001BT Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, which results in the loss of all digital control for circuits used to link Train A on Train B, and for circuits that cannot be designated as either Train A or Train B. This will result in an automatic reactor scram, a turbine trip, and the unavailability of unit changeover from unit transformer supply to station transformer supply. => C2,S4,E5. PSA Significant Component => S6. Classification update: ERCR 36137 - No longer an SPV as evaluated by System Engineering. | SHM
1 | LCC |  |  |  | 1LLC0410 | 1LCC002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function:To provide 48v DC supply to 001TB and to charge 001BT Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, which results in the loss of all digital control for circuits used to link Train A on Train B, and for circuits that cannot be designated as either Train A or Train B. This will result in an automatic reactor scram, a turbine trip, and the unavailability of unit changeover from unit transformer supply to station transformer supply. => C2,S4,E5. PSA Significant Component => S6. Classification update: ERCR 36137 - No longer an SPV as evaluated by System Engineering. | SHM
1 | LHP |  |  |  | 1LLG0101 | 1LHP001PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 001 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 001 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 002 PO would be required to fulfil this function. = > S4. | SLM
1 | LHP |  |  |  | 1LLG0201 | 1LHP002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 002 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 002 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 001 PO would be required to fulfil this function. = > S4. | SLM
1 | LHP |  |  |  | 1LLG0202 | 1LHP003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: to supply fuel from 005 BA to engine fuel rack during engine operation. Failure analysis and classification: -- 003 PO fuel pump operates continuously to supply fuel from 005 BA to engine fuel rack during standby and engine operation. = > I1 -- 003 PO failure would result in failure to transfer fuel from 005 BA to engine fuel rack during standby conditions. This would result in a reduction of redundancy and 007 PO would be required to fulfill this function on its own. = > S4. Requirement in the SAR of both 003 and 007 PO to be operable is not critical. | SHM
1 | LHQ |  |  |  | 1LLW0101 | 1LHQ001PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 001 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 001 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 002 PO would be required to fulfil this function. = > S4. | SLM
1 | LHQ |  |  |  | 1LLW0201 | 1LHQ002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 002 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 002 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 001 PO would be required to fulfil this function. = > S4. | SLM
1 | LHQ |  |  |  | 1LLW0202 | 1LHQ003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: to supply fuel from 005 BA to engine fuel rack during engine operation. Failure analysis and classification: -- 003 PO fuel pump operates continuously to supply fuel from 005 BA to engine fuel rack during standby and engine operation. = > I1 -- 003 PO failure would result in failure to transfer fuel from 005 BA to engine fuel rack during standby conditions. This would result in a reduction of redundancy and 007 PO would be required to fulfill this function on its own. = > S4. Requirement in the SAR of both 003 and 007 PO to be operable is not critical. | SHM
1 | LMA |  |  |  | 1LMA180CR | 1GEV011AR | [10 empty] | B0184 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 001 TP inside 011 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 126 EC OLTC 1 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | LMA |  |  |  | 1LMA180CR | 1GEV012AR | [10 empty] | B0185 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 002 TP inside 012 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 127 EC OLTC 2 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | LMA |  |  |  | 1LMA180CR | 1GEV013AR | [10 empty] | B0186 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 003 TP inside 013 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 128 EC OLTC 3 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 | SHS
1 | LNE |  |  |  | 1LNE0463 | 1GSE001AR | [10 empty] | B0067 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | This cabinet houses the Bently racks for the turbine expansion and vibration sensors. It also houses the acquisition rack for the RCP system. The vibration measurerment circuit now produces an automated 2oo20 protection trip. =>S4,E5 This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
1 | PTR |  |  |  | 1LKL0203 | 1PTR005PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump. Function: RX cavity recirculation pump . Failure analysis and classification: Pump used exclusivly during outage for RX Cavity recirculation, transfer water from Internal Storage compartment and to supply RCP pump seal injection. - Failure to function correctly for RX Cavity recirculation, transfer water from Internal Storage compartment and to supply RCP pump seal injection => S4,E6 - Failure to function may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E6 | SLM
1 | RAM |  |  |  | 1LKC0205 | 1RAM001MO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
1 | RAM |  |  |  | 1LKC0205 | 1RAM001MO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
1 | RAM |  |  |  | 1LKA0201 | 1RAM002MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
1 | RAM |  |  |  | 1LKA0201 | 1RAM002MO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
1 | RCP |  |  |  | 1LKC0101 | 1RCP001RS | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 1 heaters Function: Supply to three ON-OFF heaters on 001 BA - (3 phases supplied by LKC 101 JA ) Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 -- Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKC0101 | 1RCP001RS | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 1 heaters Function: Supply to three ON-OFF heaters on 001 BA - (3 phases supplied by LKC 101 JA ) Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 -- Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKB0205 | 1RCP002RS | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 2 heaters Function: Supply to three ON-OFF heaters on 001 BA - 3 phases supplied by LKB 205 JA Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKB0205 | 1RCP002RS | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 2 heaters Function: Supply to three ON-OFF heaters on 001 BA - 3 phases supplied by LKB 205 JA Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKA0103 | 1RCP003RS | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKA0103 | 1RCP003RS | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKB0207 | 1RCP004RS | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCP |  |  |  | 1LKB0207 | 1RCP004RS | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
1 | RCV |  |  |  | 1LLD0510 | 1RCV054VP | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the suction line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | RCV |  |  |  | 1LLC0504 | 1RCV053VP | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the suction line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. - Valve failure to function as require for maintenence activity => S4,E5,E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | RCV |  |  |  | 1LLD0507 | 1RCV084VP | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | RCV |  |  |  | 1LLD0506 | 1RCV086VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | RCV |  |  |  | 1LLC0502 | 1RCV083VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | RCV |  |  |  | 1LLC0501 | 1RCV085VP | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
1 | REA |  |  |  | 1LLI0101 | 1REA001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralized water pump Component 50% in service. Failure of the motor/pump will reduce necessary redundancy (not periodically tested) in primary system make-up => S4 | SLM
1 | REA |  |  |  | 1LLJ0103 | 1REA002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralized water pump Component 50% in service. Failure of the motor/pump will reduce necessary redundancy (not periodically tested) in primary system make-up => S4 | SLM
1 | RIS |  |  |  | 1LLE0405 | 1RIS021PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Single stage centrifugal pump Function: To recirc the BIT for sampling purposes. Failure analysis and classification: Component used during power operation => NO C3 but S4, E6 | SLM
1 | RPE |  |  |  | B0103 | 1RPE003PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Discharge pump for RPE011PS. Component used mostly during RO when draining or filling operations are in progress. => E6 RPE 003/4 PO are the floor drains pumps in the reactor building. During the RO’s they are used to remove water drained from the reactor vessel cavity. During plant operation they are used to remove water as a result of external leakage from liquid systems in the RX. Classification has been changed. => S4, E5. | SLM
1 | RPE |  |  |  | E0406 | 1RPE004PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Discharge pump for RPE011PS. Component used mostly during RO when draining or filling operations are in progress. => E6 RPE 003/4 PO are the floor drains pumps in the reactor building. During the RO’s they are used to remove water drained from the reactor vessel cavity. During plant operation they are used to remove water as a result of external leakage from liquid systems in the RX. Classification has been changed. => S4, E5. | SLM
1 | RRB |  |  |  | 1LLC0607 | 1RRB001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1LLD0707 | 1RRB002TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1LLC0610 | 1RRB003TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Switchboard Function: 380Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1LLD0703 | 1RRB004TB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
1 | RRB |  |  |  | 1LLC0610 | 1RRB003TB | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Switchboard Function: 380Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
1 | SAP |  |  |  | 1LKF0508 | 1SAP201VA | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - SAR from SAT isolation. Valve normally open. Closed manually from C/room upon low pressure condition to protect essential air supply => S4. | SLM
1 | SEC |  |  |  | 1LLE0302 | 1SEC009FI | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train A - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
1 | SEC |  |  |  | 1LLB0404 | 1SEC010FI | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train B - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
1 | SEC |  |  |  | 1LLE0301 | 1SEC011FI | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train A - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
1 | SEC |  |  |  | 1LLB0405 | 1SEC012FI | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train B - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
1 | STR |  |  |  | 1LKA0101 | 1STR001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply water to the steam transformer Failure analysis and classification: Failure will result in loss of feedwater o the steam transformer => S4,E6 | SLM
1 | STR |  |  |  | 1LKB0209 | 1STR002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply water to the steam transformer Failure analysis and classification: Failure will result in loss of feedwater o the steam transformer => S4,E6 | SLM
1 | SXS |  |  |  | 1LKE0205 | 1SXS004PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extended Spindle Pump. SXS 004 PO is the last line of defence in removing water from the MX should the other 2 pumps fail or be insufficient in volume. =>S4 If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | SLM
1 | TEG |  |  |  | 1LKJ0406 | 1TEG001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Compressor for hydrogenated gas from 9TEG001BA. Function: Compress hydrogenated gas and discharge to TEG storage tanks. Failure analysis and classification: Component cycled frequently. => I2 Component failure to compress will require the standby compressor to operate. => S4 Component leak could cause a hydrogen explosion or a Nitrogen leak. => S1 | SHM
1 | TEG |  |  |  | 1LKJ0405 | 1TEG001RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater associated with the operation of iodine traps on failure -> partial or total unavailability of an iodine, chapter 9 test but no associated event -> S1 | SLM
1 | TEG |  |  |  | 1LKJ0407 | 1TEG001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Continuous aerated vents fan. Function: Extract hazardous gasses from RPE vent pots and sampling boxes. Component 50% in service Failure analysis and classification: Component failure will require the other fan to be placed in service. => S4 Component failure could allow the escape of hazardous and radioactive gases from sampling boxes. => S1 | SLM
2 | KRT |  |  |  | 2KRT129CR | 2KRT905MA | [10 empty] | B0908 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | PSA Significant Component => S6. Component always in service and under electric tension. => I1,I4 | SHM
2 | KRT |  |  |  | 2KRT129CR | 2KRT906MA | [10 empty] | B0909 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | PSA Significant Component => S6. Component always in service and under electric tension. => I1,I4 | SHM
2 | KRT |  |  |  | 2KRT129CR | 2KRT907MA | [10 empty] | B0910 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | PSA Significant Component => S6. Component always in service and under electric tension. => I1,I4 | SHM
2 | PTR |  |  |  | 2LLI001TB | 2PTR137VB | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLI001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM | Manually operated isolation valve Function: 001 BA outlet towards 001 PO/002 PO suction. Failure analysis and classification: Component normally CLOSED - used for 001 BA water transfer and recirculation. Component located in corrosive and dusty environment => A6,A7 - Failure to function OPEN/CLOSE may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 - Failure to CLOSE (isolate) will prevent maintenance activity downstream of 001 BA => S4,S7,E5. - Failure to OPEN/CLOSE for 001 BA recirculation => E6 Component located in corrosive and dusty environment. => A6,A7 | SLS
2 | KRT |  |  |  | 2KRT021CR | 2KRT001PO | [10 empty] | B0600 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply samples to radiation detector Failure analysis and classification: Component always in service => I1,I4 Failure will result in loss of redundancy => S4,E6 | SHM
2 | KRT |  |  |  | 2KRT025CR | 2KRT002PO | [10 empty] | B0603 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Diaphragm Pump Function: To supply ETY samples to radiation detectors Failure analysis and classification: S4, E5, E6, I1, I4. Failure will result in loss of Defence in Depth => S4 Failure will result in degradation other detectors => E5 Failure will result in entry into OTS (no fallback, but prevents fuel handling) => E6 Component always in service => I1 ,I4 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM001AP | [10 empty] | B0300 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM401BN | 2RAM001AP | [10 empty] | B0301 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM001AP | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM001AP | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM001AP | [10 empty] | B0313 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM002AP | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM002AP | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM002TB | 2RAM002AP | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Switch board cabinet Function: Contain RAM system related equipment necessary for control, indications and protection of the MG sets. Failure analysis and classification: Switchboard continuously in service I1,I4 -- Malfunction of the switchboard will/could result in the reactor scram => C1 -- For the partial malfunction, making one RAM MG set unavailable causes a reduction of defence in depth => S4 | CHM | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002AP | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | RAM |  |  |  | 2RAM601BN | 2RAM002AP | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 260 Vac Generator Function: RGL supply Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | SXS |  |  |  | 1SXS501AR | 2SXS501PO | [10 empty] | B0601 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
2 | SXS |  |  |  | 1SXS501AR | 2SXS503PO | [10 empty] | B0602 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
2 | SXS |  |  |  | 1SXS502AR | 2SXS502PO | [10 empty] | B0701 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
2 | SXS |  |  |  | 1SXS502AR | 2SXS504PO | [10 empty] | B0702 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet. Cabinets are classified as RTF. | RTM | Submersible Pump. Failure of the pump would increase the risk of flooding the SEC pump areas. => S4, E5. | SLM
2 | ABP |  |  |  | 2LKC0308 | 2ABP035VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolates common drain path from bled steam lines to 301 and 302 RE above 20% secondary power. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure in the open position would reduce plant efficiency and power output at power levels above 20% => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0307 | 2ABP036VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolates common drain path from bled steam lines to 201 and 202 RE above 20% secondary load. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure in the open position would reduce plant efficiency and power output at power levels above 20% => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0303 | 2ABP001VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 002 VV - bled steam from LP1 turbine to 201 RE Failure analysis and classification: Failure to CLOSE will require manual intervention locally =>S4,E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
2 | ABP |  |  |  | 2LKA0309 | 2ABP003VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 004 VV - bled steam from LP1 turbine to 202 RE Failure analysis and classification: Failure to CLOSE will require manual intervention locally =>S4,E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
2 | ABP |  |  |  | 2LKC0302 | 2ABP005VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 006 VV - bled steam from LP2 turbine to 201 RE. Failure analysis and classification: Failure to CLOSE will require manual intervention locally => S4, E6,E5,I1,I4. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. | SHM
2 | ABP |  |  |  | 2LKA0308 | 2ABP007VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 008 VV - bled steam from LP2 turbine to 202 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 Failure to CLOSE will require manual intervention locally => S4,E6,E5,I1,I4. | SHM
2 | ABP |  |  |  | 2LKC0301 | 2ABP009VV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 010 VV - bled steam from LP3 turbine to 201 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7. Failure to CLOSE will require manual intervention locally =>S4, E6,E5,I1,I4. High pressure system => I1,I4. | SHM
2 | ABP |  |  |  | 2LKA0307 | 2ABP011VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 012 VV - bled steam from LP3 turbine to 202 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally =>S4, E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0306 | 2ABP013VV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 014 VV - bled steam from LP1 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKA0312 | 2ABP015VV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 016 VV - bled steam from LP1 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4, E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0305 | 2ABP017VV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 014 VV - bled steam from LP2 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKA0311 | 2ABP019VV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 020 VV - bled steam from LP2 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0304 | 2ABP021VV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 022 VV - bled steam from LP3 turbine to 301 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKA0310 | 2ABP023VV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Isolation valve, upstream of air assisted NRV 020 VV - bled steam from LP3 turbine to 302 RE. Failure analysis and classification: Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE will require manual intervention locally => S4,E5,E6,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKC0401 | 2ABP025VV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Bled steam line isolation from HP turbine to 401 RE. Failure analysis and classification: Valve receives auto closing order from Turbine trip, Hi level and Hi Hi level Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE could/will require manual intervention and/or possible damage to major equipment => S4,E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ABP |  |  |  | 2LKA0306 | 2ABP027VV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: Bled steam line isolation from HP turbine to 402 RE. Failure analysis and classification: Valve receives auto closing order from Turbine trip, Hi level and Hi Hi level Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to CLOSE could/will require manual intervention and/or possible damage to major equipment => S4,E6,E5,I1,I4. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | ACO |  |  |  | 2ACO005CR | 2ACO003VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 002 PO suction Failure Analysis and Classification: Valve operated manually from local cabinet 005 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then AC O needs to be shutdown.=> possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ACO |  |  |  | 2ACO004CR | 2ACO001VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 001 PO suction Failure Analysis and Classification: Valve operated manually from local cabinet 004 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown => possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ACO |  |  |  | 2ACO006CR | 2ACO006VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | Motor operated isolation valve Function: 001 PO discharge valve Failure Analysis and Classification: Valve operated manually from local cabinet 006CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown => possible C2.)This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ACO |  |  |  | 2ACO007CR | 2ACO011VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the pump -> E2 | EHM | Motor operated isolation valve Function: 002 PO discharge valve Failure Analysis and Classification: Valve operated manually from local cabinet 007 CR. Valve remain OPEN if pump is in stand-by mode. - Failure to OPEN when require => S4 (loss or redundancy). - Failure to CLOSE - impact on maintenance activity => E5,E6. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 (Depending on when fault is found during the cycle, if valve needs repairs then ACO needs to be shutdown.=> possible C2.) This will have repercussions on the maintenance of CEX and ACO. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AGM |  |  |  | 2LKF0505 | 2AGM001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - motor driven lube oil pump (start-up and cost down operation) Pump required to run during APA 003 PO pump start-up and coast down - Failure to provide lube oil pressure at start-up makes APA 003 PO unavailable. Malfunction will result in inoperability of the APA 003 PO (no speed control) Lost of redundancy=>S4,E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 Failure to provide lube oil pressure at coast down (and bearings cooling function for 1 0 min after APA 003 PO stop) => E5 | SLM
2 | AGR |  |  |  | 2LKD0406 | 2AGR003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 001 PO - lube and control oil pump Non essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
2 | AGR |  |  |  | 2LLC0101 | 2AGR004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 002 PO - lube and control oil pump Essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
2 | AGR |  |  |  | 2LLE0202 | 2AGR005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 001 PO - lube and control oil pump Essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
2 | AGR |  |  |  | 2LKD0407 | 2AGR006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - APP 002 PO - lube and control oil pump Non essentially supplied. Two redundant 100% pumps permanently in service. Loss of one pump =>S4 Supply lube oil to the LP circuit for lubricating and cooling turbine driven feedwater pump journal and thrust bearings. Supply lube oil to the HP circuit for speed regulation and protection of the turbine driven feedwater pump | SHM
2 | AHP |  |  |  | 2LKA0303 | 2AHP001VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation to 501 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating) after maintenance => S4,E6,I1,I4,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKA0302 | 2AHP005VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation - 601 RE outlet Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating) after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKC0402 | 2AHP006VL | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation to 502 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 2 heaters back in service (or de-isolating) after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKC0403 | 2AHP010VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Feedwater isolation downstream of 602 RE Failure analysis and classification: Valve normally open. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Malfunction during power generation may prevent placing HP line 1 heaters back in service (or de-isolating)after maintenance => S4,E6,A2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKA0301 | 2AHP011VL | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: HP heaters by-pass line isolation Failure analysis and classification: Valve normally closed. Maintenance purpose only. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to operate when required makes maintenance on either line impossible =>S4,E2,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKC0805 | 2AHP018VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: 501/502 RE - drain to 003 BA on bledsteam supply line Failure analysis and classification: Valve drains accumulated condensate in the GPV bled steam supply line to No.5 HP heaters during startup and at power transients of between 0% and 20%. Failure to open/close by logic control generates alarm after 40 seconds. Exposed to water/condensate impingement during low power transients => A7 - Failure to close either by motor or manually will result in loss of efficiency => S4,E5,E6Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to open during power transient may require manual intervention locally => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKC0806 | 2AHP027VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: 601/602 RE - drain to 003 BA on bledsteam supply line Failure analysis and classification: Valve drains accumulated condensate in the GPV bled steam supply line to No.6 HP heaters during startup and at power transients of between 0% and 50%. Failure to open/close by logic control generates alarm after 40 seconds. Exposed to water/condensate impingement during low power transients => A7 - Failure to close either by motor or manually will result in loss of efficiency => S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure to open during power transient may require manual intervention locally => E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | AHP |  |  |  | 2LKA0401 | 2AHP001VV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 501 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 501 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKA0402 | 2AHP002VV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 501 RE - main bledsteam line - by-pass to 001 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 001 VV prevents 001 VV from opening if 002 VV not fully open. - CLOSING function is Hi Hi level in 501 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKC0404 | 2AHP004VV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 502 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 502 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKC0405 | 2AHP005VV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 502 RE - main bledsteam line - by-pass to 004 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock prevents 004 VV from opening if 005 VV not fully open. - CLOSING function is Hi Hi level in 502 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKA0403 | 2AHP007VV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 601 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 601 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKA0404 | 2AHP008VV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 601 RE - main bledsteam line - by-pass to 007 VV Failure analysis and classification: Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 007 VV prevents 007 VV from opening if 008 VV not fully open. - CLOSING function is Hi Hi level in 601 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKC0406 | 2AHP010VV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 602 RE - main bledsteam line Failure analysis and classification: Valve normally OPEN. - CLOSING function is for hi hi level in 602 RE and for maintenance purpose => E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | AHP |  |  |  | 2LKC0407 | 2AHP011VV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric motor operated isolation valve. Function: 602RE - main bledsteam line - by-pass to 010 VV Failure analysis and classification: Valve normally OPEN. Failure to open may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Interlock with 010 VV prevents 010 VV from opening if 011VV not fully open. - CLOSING function is Hi Hi level in 602 RE and for maintenance purposes => E6,E5 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | APA |  |  |  | 2APA002CR | 2APA001VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 001VL control. Cabinets classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | Motor operated isolation valve Function: To isolate 003 PO suction (upstream 001 FI) Failure analysis and classification: Valve intended for the maintenence purposes, normally open if pump in standby mode - operated manually from local cabinet 002 CR. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | APA |  |  |  | 2APA003CR | 2APA003VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 003 VL control. Cabinets classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | Motor operated isolation valve Function: To isolate 003 PO suction (downstream 001 FI) Failure analysis and classification: Valve intended for the maintenence purposes, normally open from 003 CR if pump in operation or in standby mode. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | APA |  |  |  | 2APA004CR | 2APA005VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Local cabinet for 005VL control. Cabinets classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | Motor operated isolation valve Function: To isolate 003 PO discharge Failure analysis and classification: Valve intended for the maintenence purposes, normally open if pump in standby mode - operated manually from local cabinet 007 CR. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 Failure to open during planned start-up (line-up) => S4,E5,E6 Component exposed to high pressure => A2 | SLS
2 | APA |  |  |  | 2LKS0202 | 2APA001RS | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater Function: To keep the out-of-service motor free from moisture Failure analysis and classification: Deterioration of the insulation due to misture is applicable only if pump is in standby => S4,I4 | SHM
2 | ATE |  |  |  | 2ATE009CR | 2ATE915VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 903 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ATE |  |  |  | 2ATE008CR | 2ATE909VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 902 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ATE |  |  |  | 2ATE007CR | 2ATE903VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate discharge from 901 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | ATE |  |  |  | 2ATE006CR | 2ATE913VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 903 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
2 | ATE |  |  |  | 2ATE005CR | 2ATE907VL | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 902 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
2 | ATE |  |  |  | 2ATE004CR | 2ATE901VL | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Valve, motorised isolation Function: To isolate suction to 901 PO Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6. Failure to open or is not fully open => S4,E5,E6. - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E5,E6 | SLM
2 | ATE |  |  |  | 9LKN0511 | 2ATE001PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Acid reclaiming pump. Function: Transfer acid as required for resin regeneration. Failure analysis and classification: Component in service only on regeneration=<50%. Component failure would delay resin regeneration. => E6 Component body or flange failure would constitute a safety hazard to personnel if the acid leaves the bund area. => S1 | SLM
2 | ATE |  |  |  | 2ATE010CR | 2ATE011PO | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Caustic soda pump. Function: Transfer caustic soda for resin regeneration. Failure analysis and classification: Component in service from time to time.=<50%. Component failure would delay resin regeneration. => E6 Component body or flange failure would constitute a safety hazard to personnel if the caustic soda leaves the bund area. => S1 | SLM
2 | CAP |  |  |  | 2LKC0512 | 2CAP008VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolation valve. Function: To remotely drain excess water from the condenser on a high level alarm threshold towards SXS system from CEX pumps discharge header at a max. rate 0f 200 t/h. Failure analysis and classification: Failure to open : Failure to remotely discharge excess water from a condenser high condensate level condition on demand. Manual actuation of valve via handwheel still possible => S4,E5,E6. Manual handwheel Failure to open => high condenser level uncontrollable, (tube leak, all make up flow isolated), unit load to be reduced, with eventual unit shutdown =>C2,S4,E5 Failure to close : Pre-outage drainage, no impact, outage time to repair => E6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | CET |  |  |  | 2LKC0409 | 2CET001VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate turbine gland steam header - VVP steam supply line Valve normally closed above 50% turbine load if steam header pressure is higher then 110 kPa abs Valve receive opening order if VVP live steam pressure is higher than 2 Map and steam header pressure is less than 110 kPa abs. Failure analysis and classification: Failure to operate as required (open/close on demand) => S4,E5,E6 - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | CET |  |  |  | 2LKC0410 | 2CET010VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate turbine gland steam header - SVA steam supply line Failure analysis and classification: Valve normally closed above 50% turbine load if steam header pressure is higher then 110 kPa abs Valve receive opening order if VVP live steam pressure is higher than 2 MPa - Failure to operate as required (open/close on demand) => S4,E5,E6 - Failure to function correctly during an outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E5,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | CEX |  |  |  | 2CEX006CR | 2CEX013VL | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 003 PO suction. Failure analysis and classification: Valve remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
2 | CEX |  |  |  | 2CEX005CR | 2CEX007VL | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 002 PO suction. Failure analysis and classification: Valve remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
2 | CEX |  |  |  | 2CEX004CR | 2CEX001VL | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Local control box of the isolation valve to the pump discharge power on TEM CEX On failure -> Unable to operate the valve electrically -> risk of having a pump CEX unavailable -> E6 | EHM | Motor operated isolation valve Function: Isolates 001 PO suction. Failure analysis and classification: Valve remains open during unit operation and only has a maintenance isolation function => I1 Component continuously under negative pressure when the condenser is under vacuum (connected to the condenser) => E5,E6,I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
2 | CEX |  |  |  | 2LKA0409 | 2CEX003VL | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 001 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SHM
2 | CEX |  |  |  | 2LKA0410 | 2CEX009VL | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 002 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SHM
2 | CEX |  |  |  | 2LKA0610 | 2CEX015VL | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: Isolates 003 PO discharge. Failure analysis and classification: Failure to close or is not leak tight => S4,E5,E6 Failure to open or is not fully open => S4,E5,E6 Component continuously under pressure => I4 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
2 | CRF |  |  |  | 2LKG0210 | 2CRF004PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | CRF pump stuffing box supply pump. Function: Supply stuffing box water. Failure analysis and classification: Redundancy with 005 PO Component 50% in service. Component failure would require the standby pump to run to maintain the CRF pump stuffing boxes wet with potable water, to prevent a forced shutdown of the in service CRF pumps. => S4,E6 Component in extremely corrosive environment. => A6 | SLS
2 | CRF |  |  |  | 2LKG0211 | 2CRF005PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | CRF pump stuffing box supply pump. Function: Supply stuffing box water. Failure analysis and classification: Redundancy with 004PO Component 50% in service. Component failure would require the standby pump to run to maintain the CRF pump stuffing boxes wet with potable water, to prevent a forced shutdown of the in service CRF pumps. => S4,E6 Component in extremely corrosive environment. => A6 | SLS
2 | CRF |  |  |  | 2LKG0301 | 2CRF001RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 001 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | CRF |  |  |  | 2LKG0412 | 2CRF002RS | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 002 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | CRF |  |  |  | 2LKG0401 | 2CRF003RS | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater - 003 MO. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | CVI |  |  |  | 2LKC0202 | 2CVI019VA | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
2 | CVI |  |  |  | 2LKC0201 | 2CVI020VA | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
2 | CVI |  |  |  | 2LKC0310 | 2CVI021VA | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operating isolation valve. Function: Provides a means of breaking vacuum in the main condenser. Failure analysis and classification: • Following a turbine trip if the main turbine needs to be slowed down as rapidly as possible. • Valve can only be operated (interlocked) with turbine trip signal and turbine speed < 1000 rpm signal. • Valve receives opening signal from the control room (007 TL). • Failure to CLOSE/jammed OPEN; - Handwheel still available locally => S4. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4 • Failure to OPEN/jammed CLOSED; - Loss of function, inability to break vacuum. Credit for vacuum breaker valve redundancy => E6,E5. | SLM
2 | CVI |  |  |  | 2LKC0812 | 2CVI003VV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motorised isolating valve. Function : To provide steam injection isolation to 003 EJ booster air ejector from steam barrel (SVA-1.2 MPa). Booster air ejector to boost vacuum pump inlet pressure when CRF temperatures lower than normal (higher vacuum pressure causes inefficient vacuum pump operation). Failure Analysis and Classification: • Fails to CLOSE/jammed OPEN; - Loss of energy/steam to atmosphere, can not be repaired on line due to lack of isolation capabilities => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, vacuum pumps performance/efficiency will tend to degrade, temperature increase in vacuum pump circuit, tripping of vacuum pump, inability to maintain efficient condenser cycle => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | DEL |  |  |  | 2LLA0309 | 2DEL001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - chilled water circulating - train A. Loss of cooling water flow could result in loss of DVL cooling. (No credit for train B) Component 50% in service. | SLM
2 | DEL |  |  |  | 2LLB0302 | 2DEL002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - chilled water circulating - train B. Loss of cooling water flow could result in loss of DVL cooling. (No credit for train A) Component 50% in service. | SLM
2 | DEL |  |  |  | 2LLA0105 | 2DEL001GF | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train A. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train B) | SHM
2 | DEL |  |  |  | 2LLB0107 | 2DEL002GF | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train B. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train A) | SHM
2 | DEL |  |  |  | 2LLA0105 | 2DEL001GF | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train A. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train B) | SHM
2 | DEL |  |  |  | 2LLB0107 | 2DEL002GF | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Chiller assembly - train B. Loss of the entire chiller could result in loss of DVL cooling. (No credit for train A) | SHM
2 | DMG |  |  |  | 2LKG0406 | 2DMG001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMG |  |  |  | 2LKG0407 | 2DMG002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMG |  |  |  | 2LKG0408 | 2DMG003PR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMG |  |  |  | 2LKG0409 | 2DMG004PR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMK |  |  |  | 2LKL0202 | 2DMK001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMK |  |  |  | 2LKL0201 | 2DMK002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMR |  |  |  | B0406 | 2DMR002PA | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMR |  |  |  | DFH | 2DMR001PR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. A functional failure of the component will result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMR |  |  |  | BGJ | 2DMR001PR | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. A functional failure of the component will result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage =>S7 E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMR |  |  |  | G0103 | 2DMR003PR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMR |  |  |  | 2LKF0401 | 2DMR004PA | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMW |  |  |  | 2LKD0410 | 2DMW003PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMW |  |  |  | 2LKD0412 | 2DMW004PR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMW |  |  |  | 2LKD0201 | 2DMW006PR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMX |  |  |  | 2LKH0201 | 2DMX001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMX |  |  |  | 2LKH0312 | 2DMX002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMX |  |  |  | 2LKF0309 | 2DMX004PR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMX |  |  |  | 2LLG0104 | 2DMX005PR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DMX |  |  |  | 2LLW0104 | 2DMX006PR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
2 | DVC |  |  |  | 2DVC004CR | 2DVC008RS | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater in booster iodine supply fans DVC 002 ZV and DVC 003 ZV inlet duct - Train B Purpose - to condition iodine filters while DVC 002 ZV in operation. Component periodically tested for functionality (SRSM - 1 RO @ any domain) => NO C2 - repair does not affect outage duration Because affects iodine filter operability => NO C3,S4 and E5 | SHM
2 | DVC |  |  |  | 2DVC011CR | 2DVC009RS | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Box connection to JDT 004 and CR 005. Contains only terminals. Failure: No light installed hardware with this kit ---> RTF | RTM | Electric heater in booster iodine supply fans DVC 002 ZV and DVC 003 ZV inlet duct - Train A Purpose - to condition iodine filters while DVC 001 ZV in operation. Component periodically tested for functionality (SRSM - 1 RO @ any domain) => NO C2 - repair does not affect outage duration Because affects iodine filter operability => NO C3,S4 and E5 | SHM
2 | DVC |  |  |  | 2LLB0303 | 2DVC002ZV | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | The booster iodine supply fan DVC 002 ZV - Train A (normally on standby) Component periodically tested for functionality (SRSM - 1 RO @ in any state => component fails PT => NO C3 but S4 and E6. | SLM
2 | DVC |  |  |  | 2LLA0308 | 2DVC001ZV | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | The booster iodine supply fan DVC 001 ZV - Train A (normally on standby) Component periodically tested for functionality (SRSM - 1 RO @ in any state => component fails PT => NO C3 but S4 and E6. | SLM
2 | DVC |  |  |  | 2LLB0305 | 2DVC004ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Normal ventilation fan DVC 004 ZV - Train B (50% duty cycle) Component periodically tested for functionality (start - stop) - (SRSM - 5 RO @ RCD) => if component fails PT => NO C2 - repair has no affect on outage duration. Associated motor periodically tested for vibration (6 monthly - KLM 008) => if component fails the test => NO C3 but S4 Component failure while in service => NO C3 but S4 Component failure while in the back-up auto start configuration =>NO C3 but S4,E6 | SLM
2 | DVC |  |  |  | 2LLA0303 | 2DVC003ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Normal ventilation fan DVC 003 ZV - Train A (50% duty cycle) Component periodically tested for functionality (start - stop) - (SRSM - 5 RO @ RCD) => if component fails PT => NO C2 - repair has no affect on outage duration. Associated motor periodically tested for vibration (6 monthly - KLM 008) => if component fails the test => NO C3 but S4 Component failure while in service => NO C3 but S4 Component failure while in the back-up auto start configuration =>NO C3 but S4,E6 | SLM
2 | DVE |  |  |  | 2LKC0807 | 2DVE001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | TRICASTIN CLASSIFICATION USED Cabinet incorporating information provided by the DVE 006, 010, 011 & 014ST (fire protection Anfi-RS) ---> Same rank as T -> S1, S4, E6 | SHM
2 | DVE |  |  |  | 2LLB0301 | 2DVE003ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train B Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLA0306 | 2DVE001ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train A Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLB0401 | 2DVE004ZV | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train B Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLA0305 | 2DVE002ZV | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - cabling floor exhaust fan train A Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLB0402 | 2DVE006ZV | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B battery room exhaust fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
2 | DVE |  |  |  | 2LLA0304 | 2DVE005ZV | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A battery room exhaust fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
2 | DVE |  |  |  | 2LLB0402 | 2DVE008ZV | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B battery room supply fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
2 | DVE |  |  |  | 2LLB0301 | 2DVE010ZV | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLA0306 | 2DVE009ZV | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A cabling floor supply fan. Component 100% in service. => I1 Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
2 | DVE |  |  |  | 2LLB0401 | 2DVE012ZV | [10 empty] | B0036 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train B cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLA0305 | 2DVE011ZV | [10 empty] | B0037 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A cabling floor supply fan. Component 50% in service. Component required for cooling the cable trays. => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SLM
2 | DVE |  |  |  | 2LLA0304 | 2DVE013ZV | [10 empty] | B0039 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - train A battery room supply fan. Component continuously in service => E6 The current classification of the component is ECONOMIC, and this classification is to be corrected to SIGNIFICANT. The change is requested based on the failure of the fan, resulting in a GROUP 2 LCO which requires operator monitoring, because half of the function of the DVE system would be lost during the failure. Based on the entry into the Group 2 LCO, it is understood that question S2 and S4 for the component should be ticked as YES, thereby changing the classification => S2, S4. | SHM
2 | DVF |  |  |  | 2LLA0302 | 2DVF001ZV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - smoke exhaust. Entry into OTS if inoperable (without fall-back)=> NO C3,S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | DVF |  |  |  | 2LLB0403 | 2DVF002ZV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - smoke exhaust. Entry into OTS if inoperable (without fall-back)=> NO C3,S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | DVK |  |  |  | 2LLI0305 | 2DVK003RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater - iodine line common inlet duct SRSM requirement - 1RO heater auto ON/OFF test from starting/stopping 003 ZV => NO C3, S4 SRSM requirement - 5 yearly verification of the heating capacity | SLM
2 | DVK |  |  |  | 2LLJ0309 | 2DVK002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Electric heater - iodine line common inlet duct SRSM requirement - 1RO heater auto ON/OFF test from starting/stopping 002 ZV => NO C3, S4 SRSM requirement - 5 yearly verification of the heating capacity | SLM
2 | DVL |  |  |  | 2LLB0406 | 2DVL104ZV | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - SAP compressors room train B cooling. Function: Cools the emergency compressor room while the compressor is in service. Failure could render emergency compressor train inoperable. => S4,E6 | SLM
2 | DVL |  |  |  | 2LLB0408 | 2DVL203ZV | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train B supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
2 | DVL |  |  |  | 2LLA0403 | 2DVL103ZV | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - SAP compressors room train A cooling. Function: Cools the emergency compressor room while the compressor is in service. Failure could render emergency compressor train inoperable. => S4,E6 | SLM
2 | DVL |  |  |  | 2LLB0407 | 2DVL204ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train B supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
2 | DVL |  |  |  | 2LLA0404 | 2DVL201ZV | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train A supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
2 | DVL |  |  |  | 2LLA0405 | 2DVL202ZV | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - DVL train A supply. Component continiously in service and pressurised when selected. => I1,I4 Failure will render train partially inoperable. => S4,E6 | SHM
2 | DVN |  |  |  | 2LKJ0103 | 2DVN008ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB Iodine air extraction fan. Function: Iodine extraction fan. Failure analysis: fan fails to start.=>S1,E5,E6 Component used to exhaust air from the NAB possible Iodine contaminated rooms. => S1 Component normally in service and pressurised as per OPS Regime on bypass. => I1,I4 PSA Significant Component => S6. | SHM
2 | DVN |  |  |  | 2DVN003BX | 2DVN003ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB supply air fan. Component used to supply air to the NAB common rooms. PSA Significant Component => S6. | SLM
2 | DVN |  |  |  | 2DVN006BX | 2DVN006ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB exhaust air fan. Component used to exhaust air from the NAB common rooms. PSA Significant Component => S6. | SLM
2 | DVW |  |  |  | 2LLA0410 | 2DVW001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Filter common suction duct - Train A electric heater SRSM requirement - 1RO verify correct operation => NO C3, S4 SRSM requirement - 5 years verify heating capacity => NO C3, S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | DVW |  |  |  | 2LLB0512 | 2DVW002RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Filter common suction duct - Train B electric heather SRSM requirement - 1RO verify correct operation => NO C3, S4 SRSM requirement - 5 years verify heating capacity => NO C3, S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | DVW |  |  |  | 2LLC0307 | 2DVW001ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extraction fan Function: Train A - Iodine extraction fan - peripheral rooms ventilation Failure analysis and classification: - Failure to function in "when require operating state" may reresult in inefficiency of the iodine filtration, DVN KRT may be activated => S1 - Failure to function will require OTS entry, but with no fallback constraints => S4,E6 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) => S4 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) on SI signal - outage => S4 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
2 | DVW |  |  |  | 2LKH0402 | 2DVW003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Train A - normal extraction fan Function: To keep the periferal room under negative pressure and to keep iodine filters conditioned. Failure analysis: Component always in service and pressurised. => I1,I4 003ZV fails to start .=>S1,E5,E6. SRSM requirement - 1RO verify correct operation of the fan (and associated logic)=> E6 | SHM
2 | DVW |  |  |  | 2LLD0307 | 2DVW002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extraction fan Function: Train B - Iodine extraction fan - peripheral rooms ventilation Failure analysis and classification: - Failure to function in "when require operating state" may reresult in inefficiency of the iodine filtration, DVN KRT may be activated => S1 - Failure to function will require OTS entry, but with no fallback constraints => S4,E6 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) => S4 - SRSM requirement - 1RO verify correct operation of the fan (+ associated logic) on SI signal - outage => S4 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
2 | EAS |  |  |  | 2LLD0401 | 2EAS132VB | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 002 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 134 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
2 | EAS |  |  |  | 2LLC0301 | 2EAS131VB | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 001 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 133 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
2 | EAS |  |  |  | 2LLD0402 | 2EAS134VB | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 002 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 132 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
2 | EAS |  |  |  | 2LLC0401 | 2EAS133VB | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: 001 PO mini-flow isolation. Failure analysis and classification: Valve closed during normal operation. Intended for test Train A pump and system. Credit taken for 131 VB - SRSM requirement - 1 RO PT - outage - verify maneuverability by TPL - failure to function correctly during PT may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLM
2 | EVC |  |  |  | E0103 | 2EVC001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
2 | EVC |  |  |  | B0406 | 2EVC002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
2 | EVC |  |  |  | E0406 | 2EVC003ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
2 | EVC |  |  |  | B0709 | 2EVC004ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R147. Component 50% in service. Component used to cool the concrete around the reactor vessel. => E6 Component failure would cause a loss of redundancy that could cause an entry to OTS. => S4. | SLM
2 | EVF |  |  |  | CGJ | 2EVF001RS | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater electric. Failure (does not heat, thus reducing the efficacy of the PI) may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure (does not heat, thus reducing the efficacy of the PI) will reduce necessary redundancy => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | EVF |  |  |  | DHK | 2EVF002RS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater electric R243. Failure (does not heat, thus reducing the efficacy of the PI) may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure (does not heat, thus reducing the efficacy of the PI) will reduce necessary redundancy => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | EVF |  |  |  | A0103 | 2EVF001ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R310. Failure to circulate air may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure to circulate air will reduce necessary redundancy => S4. | SLM
2 | EVF |  |  |  | A0406 | 2EVF002ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - supply air R310. Failure to circulate air may cause an unacceptable increase in personnel or radiological (level of activity = orange zone) safety => S1. Failure to circulate air will reduce necessary redundancy => S4. | SLM
2 | EVR |  |  |  | CFJ | 2EVR001ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 1 Failure analysis and classification: The component is continuously in service and energised => I1,I4 - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SHM
2 | EVR |  |  |  | CFJ | 2EVR002ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 2 Failure analysis and classification: The component is 50% in service. - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
2 | EVR |  |  |  | E0709 | 2EVR005ZV | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Containment dome recirculation fan Failure analysis and classification: Component 50% in service. -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function "when required" will result in reduction in necessary redundancy => S4 . | SLM
2 | EVR |  |  |  | BEH | 2EVR003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: containment cooling- Loop 2 Failure analysis and classification: The component is 50% in service. - Failure to function will require starting the standby fan, this will result in reduction in redundancy => S4,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7 | SLM
2 | EVR |  |  |  | E1618 | 2EVR004ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Containment dome recirculation fan Failure analysis and classification: Component 50% in service. -- Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function "when required" will result in reduction in necessary redundancy => S4 . | SLM
2 | GEV |  |  |  | 2GEV002CR | 2GEV011AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 001 TP inside 011 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 126 EC OLTC 1 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | GEV |  |  |  | 2GEV002CR | 2GEV012AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 002 TP inside 012 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 127 EC OLTC 2 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | GEV |  |  |  | 2GEV002CR | 2GEV013AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM | Tap changer control mechanism - 003 TP inside 013 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 128 EC OLTC 3 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | GEX |  |  |  | 2LKC0610 | 2GEX004TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Emergency excitation transformer Function: To supply voltage to the excitation circuit Failure analysis and classification: When in service: (due to the unavailability of GEX001/2/3TR), it is permanently in service =>I1,I4 -- Failure to function during outage (start - up) will/could require outage repair time > 12 hrs => C2 -- Failure to function during normal operation will result in immediate production loss => C2 -- Functional failure of the transformer may result in an unacceptable risk to personnel, and the environment. => S1 -- Functional failure of the transformer may result in an unplanned power transient (sustained generation loss) => S4 -- Repair cost is considered high => E6 When not in service: -- Functional failure of the transformer will result in a reduction of “defence in depth” Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | GFR |  |  |  | 2LKA0504 | 2GFR001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - boosting pump for HP pumps 003 /004 PO. Component 50% in service. Functional Failure will require standby pump 002 PO to be placed in service => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SLM
2 | GFR |  |  |  | 2LKC0712 | 2GFR002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - boosting pump for HP pumps 003 /004 PO. Component 50% in service. Functional Failure will require standby pump 001PO to be placed in service => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SLM
2 | GFR |  |  |  | 2LKA0209 | 2GFR003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - HP. Component 50% in service and pressurised greater than 7000kPa. => A2 Functional Failure will require standby pump 004 PO to be placed in service. => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SLS
2 | GFR |  |  |  | 2LKC0209 | 2GFR004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump - HP. Component 50% in service and pressurised greater than 7000kPa. => A2 Functional Failure will require standby pump 004 PO to be placed in service. => S4 , E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintanencs repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | SLS
2 | GGR |  |  |  | 2LKF0511 | 2GGR204VN | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Manual pre-set valve Function: To regulate (adjust) SRI flow rate through the coolers (001 and 002 RF). Failure analysis and classification: Valve manipulated when require to control lube oil temperature by varying SRI flow rate accordingly => I3. - Failure to function could lead to unacceptable lube oil temperature => S4,E5. - Failure to function correctly during outage may require repair time < 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7,S4,E6 | SHM
2 | GGR |  |  |  | 2LKA0503 | 2GGR009ZV | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan - 009 BA gas extraction Component always required to be in service and pressurised. => I1,i4 Fan required in service according to the safety regulations to extract explosive gases (hydrogen) from oil => S1, S5, E5 | SHM
2 | GGR |  |  |  | 2GGR010BX | 2GGR010PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Jacking oil pump Failure analysis and classification: Only one jacking oil pump required for turbine barring and run-up. Pump required to be in service up to 500 rpm during turbine run-up. (011 PO equivalent) => S4,E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | GGR |  |  |  | 2GGR011BX | 2GGR011PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Jacking oil pump Failure analysis and classification: Only one jacking oil pump required for turbine barring and run-up. Pump required to be in service up to 500 rpm during turbine run-up. (010 PO equivalent) => S4,E6,A2 Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLS
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001TR | 2GGR001AR | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | GGR |  |  |  | 2GGR001AR | 2GGR020MO | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
2 | GGR |  |  |  | 2GGR001AR | 2GGR020MO | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
2 | GGR |  |  |  | 2GGR001AR | 2GGR020MO | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM | Electric motor Function: To drive turning gear. Failure analysis and classification: Require during units start-up and shut down to prevent turbine shaft deformation and damage of the bearings. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S7, E6 | SLM
2 | GGR |  |  |  | 2GGR001GA | 2GGR059CR | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Alternator Function: To supply 001MO/001PO Failure analysis and classification: Component continuously in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an immediate production loss > 20% => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | CHM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
2 | GGR |  |  |  | 2GGR001GA | 2GGR059CR | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Alternator Function: To supply 001MO/001PO Failure analysis and classification: Component continuously in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an immediate production loss > 20% => C2 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | CHM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
2 | GGR |  |  |  | 2GGR001AR | 2GGR059CR | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM | Box (Small panel) Function: To house unspecified GGR equipment (without trigrammes). Failure analysis and classification: Component permanently in service => I1,I4 Failure can have the following consequences: - Failure to function during outage (start - up) will/could require outage repair time > 36 hrs => S7 - Failure to function during normal operation will result in a "Programmed Shutdown" resulting in an unplanned sustained generation loss, and a reduction in defence in depth => S4,E6 | SHM
2 | GHE |  |  |  | 2LLI0408 | 2GHE003PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380V AC standby emergency seal oil pump. -Provides a small amount of detrained oil back to the seal oil supply to the generator seal oil circuit, while the bulk is returned to 004 DZ air detraining tank. - Receives inlet supply from GGR lube oil circuit. - Fails to pump, reduction in defence of depth, requires emergency DC seal oil pump 004 PO to operate => S4, E6. Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
2 | GHE |  |  |  | 2LKE0302 | 2GHE006ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Spark resistant centrifugal fan for 004 DZ air detraining tank. -Generates input to KIT when on 012 EC. -Removes air and possible "spill over" hydrogen vapour from the gaseous portion of 004 DZ detraining tank to atmosphere. - Failure to degas 004 DZ will not render the seal oil system inoperable. The degassing function will be ensured by the GGR vapour exhauster (KWB-S.GHE). -The hydrogen purity within the alternator should be checked and increased if the purity level drops to below 96%. -Reduction of defence in depth => S4, I1, I4. | SHM
2 | GPV |  |  |  | 2LKC0711 | 2GPV051VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - Drain line from 001 BA to AHP 003 BA via 031 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from CET001BA Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
2 | GPV |  |  |  | 2LKC0710 | 2GPV052VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from GV's to AHP 003 BA via 038 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
2 | GPV |  |  |  | 2LKC0709 | 2GPV053VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from GV's to AHP 003 BA via 039 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
2 | GPV |  |  |  | 2LKC0708 | 2GPV054VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from RSV's to AHP 003 BA via 033 DI Start-up drain path open up to 90% HP opening ref. Function: To isolate drain path from upstream HP governor valves Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
2 | GPV |  |  |  | 2LKC0707 | 2GPV055VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - drain line from HP turbine exhaust to AHP 003 BA Off power drain valve Function: To isolate drain path from HP turbine Failure analysis: Fails to close or is not leak tight(maintenance) =>E5,E6 Fails to open or is not fully open => S4,E5,E6 Fails to perform it's function. | SLM
2 | GSE |  |  |  | 2GSE003AR | 2GRE002AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
2 | GSE |  |  |  | 2GSE003AR | 2GRE002AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
2 | GSE |  |  |  | 2GSE005AR | 2GRE002AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Increased burden to the operator due to additional alarms being generated. The failure of fans within could result in increased component failure. This cabinet houses various equipment required for the Turbine Protection and Control system (GRE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
2 | GSE |  |  |  | 2GSE005AR | 2GSE003AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
2 | GSE |  |  |  | 2GSE005AR | 2GSE003AR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
2 | GSE |  |  |  | 2LKA0501 | 2GSE003AR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
2 | GSE |  |  |  | 2GSE005AR | 2GSE003AR | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Mainly housing the power circuitry for the cabinets, controllers and the safety solenoids. Transformers for the DC voltage and current detection for the RPR protection. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM | Located on the 7M level in the switchgear room. Loss of one linked supply either LKA or PMG could be tolerated but not both. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SHM
2 | GSS |  |  |  | 2LKC0706 | 2GSS001VV | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: To isolate heating steam line towards 100 & 300 ZZ - main valve. Failure analysis and classification: Valve receives opening order @ T>238 degC (+/- 30%PE) and remain open during higher power operation. Valve receives closing order on turbine trip signal - (no consequences since GPV valves will close first - Failure to open will result in delay during start-up (power escalation) => C2. - Failure to close on turbine trip signal - (no serious consequences since GPV valves will close first) => S4,E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | GSS |  |  |  | 2LKC0705 | 2GSS002VV | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve. Function: To isolate heating steam line towards 200 & 400 ZZ - main valve. Failure analysis and classification: Valve receives opening order @ T>238 degC (+/- 30%PE) and remain open during higher power operation. Valve receives closing order on turbine trip signal - (no consequences since GPV valves will close first) - Failure to open will result in delay during start-up (power escalation) => C2. - Failure to close on turbine trip signal - (no consequences since GPV valves will close first) => E5,E6 Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | GSS |  |  |  | 2LKC0704 | 2GSS005VV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To drain condensation from the steam line downstream of 001/003 VV to the AHP 001 BA Failure analysis and classification: Valve open during startup. Require to auto close when 001 VV not closed. Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | GSS |  |  |  | 2LKC0703 | 2GSS006VV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To drain condensation from the steam downstream of 002/004 VV Failure analysis and classification: Valve open during startup. Require to auto close when 002 VV not closed. Failure to function correctly may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | GSS |  |  |  | 2LKC0702 | 2GSS121VV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve . Function: 100 & 300 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | SLM
2 | GSS |  |  |  | 2LKC0701 | 2GSS122VV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve . Function: 100 & 300 ZZ drain of the tube bundle condensate towards AHP 003 BA Start-up drain path. Failure analysis: Fails to close or is not leak tight(discharges to flash tank) => S4,E5,E6 Fails to open or is not fully open => S4,E5,E6 Repair time < 36 Hrs => NO C2 | SLM
2 | GST |  |  |  | 2LKE0209 | 2GST001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Stator cooling pump Failure analysis and classification: Pump continuously in service => I1 - Failure to function will render pump inoperable and if: in service (credit taken for second stand-by pump with auto start) => S4 when on stand-by as a back-up pump => C2,S4 Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | GST |  |  |  | 2LKS0209 | 2GST002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Stator cooling pump Failure analysis and classification: Pump continuously in service => I1 - Failure to function will render pump inoperable and if: in service (credit taken for second stand-by pump with auto start) => S4 when on stand-by as a back-up pump => C2,S4 Failure to function correctly during outage may require repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | GSY |  |  |  | 2LKB0203 | 2GSY001MO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Electric motor Function: To drive cooling fan for 24 KV busbars. Failure analysis and classification: The motor drives 001 ZV which in turn drives 003 ZV Component in service 50% due to a train A and Train B. - Fan/motor condition is monitored during OPS rounds. Upon malfunction, the stand-by train can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
2 | GSY |  |  |  | 2LKC0103 | 2GSY002MO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: 24 kV busbars cooling fan. Failure analysis and classification: 50% fan operating in tandem with a second 50% fan. (the motor drives 002 ZV which in turn drives 004 ZV) Component in service 50% due to a train A and Train B. - Fan condition is monitored during OPS rounds. Upon malfunction, the stand-by train can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
2 | GSY |  |  |  | 2LKB0309 | 2GSY006ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Alternator terminal box cooling fan Failure analysis and classification: Component in service 50% due to fan 006 ZV and fan 007 ZV running 2 months on 2 months off. - Fan condition is monitored during OPS rounds. Upon malfunction, the fan on stand-by can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
2 | GSY |  |  |  | 2LKB0310 | 2GSY007ZV | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Alternator terminal box cooling fan Failure analysis and classification: Component in service 50% due to fan 006 ZV and fan 007 ZV running 2 months on 2 months off. - Fan condition is monitored during OPS rounds. Upon malfunction, the fan on stand-by can be started =>S4, E6 - PT-1 2 -GSY-063 2 monthly test, test failure => E6 | SLM
2 | JPD |  |  |  | 2LLD0509 | 9JPD601VE | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 9JPD601VE sectional isolating valve Function: To isolate section of JPD Failure analysis: Fails to operate (open/close) the valve.=>S4,E5,E6. Mechanical operation/open/close limits not functioning=>E6. | SHM
2 | JPP |  |  |  | 2LLE0701 | 2JPP002VE | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated valve .2 JPP001BA filling valve Function: To fill and maintain 001BA level at programed level. Failure analysis: Fails to operate (open/close) the valve => S1,E6. Mechanical operation/open/close limits not functioning=>E6. | SLM
2 | LAB |  |  |  | 2LLI0105 | 2LAB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 2 3 0 V DC to LAB 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 004 PO - "first" emergency lube oil pump - running continuously 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4 , E6 -- Functional failure of the component could result in loss of GGR004 PO leading to damage to the turbine bearings => E5 | SHS
2 | LAC |  |  |  | 2LKH0105 | 2LAC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 230 V DC to LAC 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 003 PO ("second" emergency lube oil pump - starting on low pressure), and GHE 004 PO (emergency seal oil pump - starting on low pressure). 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4, E6 | SHS
2 | LAC |  |  |  | 2LKH0105 | 2LAC001RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Charger Function: To supply 230 V DC to LAC 001 TB Failure analysis and classification: 001 TB is the source of supply to the GGR 003 PO ("second" emergency lube oil pump - starting on low pressure), and GHE 004 PO (emergency seal oil pump - starting on low pressure). 001 RD is permanently in service maintaining 001 BT charged => I1,I4 -- Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 -- Failure to function during normal operation will result loss of necessary redundancy and defence in depth => S4, E6 | SHS
2 | LAC |  |  |  | 2LAC03 | 2GHE004PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Standby emergency seal oil pump 004 PO. Failure analysis and classification: Pump may only run for approx. 2 - 4 hrs from LAC batteries. Pump receives auto start order upon low discharge pressure of pumps 001 and 003 PO - (003 PO is diessel backed). - Failure to supply detrained seal oil to the generator seal circuit, while the other pumps are not available, will require turbine load reduction (seals supply from GGR) and loss of H2=> S1, S4 - Failure to function correctly should need an outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
2 | LAC |  |  |  | 2LAC03 | 2GHE004PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: Standby emergency seal oil pump 004 PO. Failure analysis and classification: Pump may only run for approx. 2 - 4 hrs from LAC batteries. Pump receives auto start order upon low discharge pressure of pumps 001 and 003 PO - (003 PO is diessel backed). - Failure to supply detrained seal oil to the generator seal circuit, while the other pumps are not available, will require turbine load reduction (seals supply from GGR) and loss of H2=> S1, S4 - Failure to function correctly should need an outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | SLM
2 | LBA |  |  |  | 2LLE0401 | 2LBA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBA feeder diagram indicates that loss of LBA001RD will result in loss of LBA001TB. Therefore the loss of LBA001RD shall have the same classification as LBA001TB => C1,C2,C3,C4,C6,C7,C8,C9,S1,S3,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LBA |  |  |  | 2LLC0407 | 2LBA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBA feeder diagram indicates that loss of LBA002RD will result in loss of LBA001TB. Therefore the loss of LBA002RD shall have the same classification as LBA001TB => C1,C2,C3,C4,C6,C7,C8,C9,S1,S3,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LBB |  |  |  | 2LLB0509 | 2LBB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 125 V DC. Function: To provide trn A with 125v DC and charge 001BT Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. The battery life will allow for operator action to supply the board from a charger. =>C2,S4,E5. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LBB |  |  |  | 2LLD0405 | 2LBB002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 125 V DC. Function: To provide trn A with 125v DC and charge 001BT Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by 001 BT. The battery life will allow for operator action to supply the board from a charger. =>C2,S4,E5. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LCA |  |  |  | 2LLA0506 | 2LCA001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCA 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCA switchboard results in the loss of all digital control and indication for Train A and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LCA |  |  |  | 2LLE0403 | 2LCA002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 001 RD will result in 001 TB being supplied by LCA 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCA switchboard results in the loss of all digital control and indication for Train A and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LCB |  |  |  | 2LLB0505 | 2LCB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCB 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCB switchboard results in the loss of all digital control and indication for Train B and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LCB |  |  |  | 2LLD0406 | 2LCB002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function: To provide 48vDC to 001TB and to charge 001BT. Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by LCB 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, The resultant loss of the power to the scram breaker under voltage coils causes a reactor scram =>E5. A steam line isolation occurs due to the de-energisation of solenoids in the MSIV air circuits => C2. The loss of LCB switchboard results in the loss of all digital control and indication for Train B and non-essential systems on the unit => S4. The loss of the power supply to GPA results in the opening of the 400kV breaker. This in turn results in a changeover to 132kV supplies (Fed by LCC) => S4. PSA Significant Component => S6. Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
2 | LCC |  |  |  | 2LLA0505 | 2LCC001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function:To provide 48v DC supply to 001TB and to charge 001BT Failure analysis: While in operation, loss of 001 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 001 RD will result in operator action - 001 TB to be supplied from 002 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, which results in the loss of all digital control for circuits used to link Train A on Train B, and for circuits that cannot be designated as either Train A or Train B. This will result in an automatic reactor scram, a turbine trip, and the unavailability of unit changeover from unit transformer supply to station transformer supply. => C2,S4,E5. PSA Significant Component => S6. Classification update: ERCR 36137 - No longer an SPV as evaluated by System Engineering. | SHM
2 | LCC |  |  |  | 2LLC0410 | 2LCC002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Battery charger - 48 V DC. Function:To provide 48v DC supply to 001TB and to charge 001BT Failure analysis: While in operation, loss of 002 RD will result in entry into OTS (A battery charger of a switchboard is inoperable. Repair within 7 days.) => NO C3. While in operation, loss of 002 RD will result in operator action - 001 TB to be supplied from 001 RD => S4,I-1,I4. While in standby, and fails to perform it's backup function, failure of 002 RD will result in 001 TB being supplied by 001 BT. As the voltage on 001 BT drops the under-voltage protection eventually causes the loss of 001 TB, which results in the loss of all digital control for circuits used to link Train A on Train B, and for circuits that cannot be designated as either Train A or Train B. This will result in an automatic reactor scram, a turbine trip, and the unavailability of unit changeover from unit transformer supply to station transformer supply. => C2,S4,E5. PSA Significant Component => S6. Classification update: ERCR 36137 - No longer an SPV as evaluated by System Engineering. | SHM
2 | LHP |  |  |  | 2LLG0101 | 2LHP001PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 001 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 001 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 002 PO would be required to fulfil this function. = > S4. | SLM
2 | LHP |  |  |  | 2LLG0201 | 2LHP002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 002 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 002 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 001 PO would be required to fulfil this function. = > S4. | SLM
2 | LHP |  |  |  | 2LLG0202 | 2LHP003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: to supply fuel from 005 BA to engine fuel rack during engine operation. Failure analysis and classification: -- 003 PO fuel pump operates continuously to supply fuel from 005 BA to engine fuel rack during standby and engine operation. = > I1 -- 003 PO failure would result in failure to transfer fuel from 005 BA to engine fuel rack during standby conditions. This would result in a reduction of redundancy and 007 PO would be required to fulfill this function on its own. = > S4. Requirement in the SAR of both 003 and 007 PO to be operable is not critical. | SHM
2 | LHQ |  |  |  | 2LLW0101 | 2LHQ001PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 001 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 001 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 002 PO would be required to fulfil this function. = > S4. | SLM
2 | LHQ |  |  |  | 2LLW0201 | 2LHQ002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 002 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 002 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 001 PO would be required to fulfil this function. = > S4. | SLM
2 | LHQ |  |  |  | 2LLW0202 | 2LHQ003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: to supply fuel from 005 BA to engine fuel rack during engine operation. Failure analysis and classification: -- 003 PO fuel pump operates continuously to supply fuel from 005 BA to engine fuel rack during standby and engine operation. = > I1 -- 003 PO failure would result in failure to transfer fuel from 005 BA to engine fuel rack during standby conditions. This would result in a reduction of redundancy and 007 PO would be required to fulfill this function on its own. = > S4. Requirement in the SAR of both 003 and 007 PO to be operable is not critical. | SHM
2 | LMA |  |  |  | 2LMA0141 | 2GGR001AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Cabinet All cabinets are classified as RTF. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHM
2 | LMA |  |  |  | 2LMA180CR | 2GEV011AR | [10 empty] | B0184 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 001 TP inside 011 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 126 EC OLTC 1 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | LMA |  |  |  | 2LMA180CR | 2GEV012AR | [10 empty] | B0185 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 002 TP inside 012 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 127 EC OLTC 2 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | LMA |  |  |  | 2LMA180CR | 2GEV013AR | [10 empty] | B0186 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | General description: Distribution box. All cabinets are classified as RTF. | RTM | Tap changer control mechanism - 003 TP inside 013 AR Failure to change the tap within 7 seconds will result in: Generate alarm 008 AA, O.L.T.C. EXCESS RUN TIME Genarate KIT 128 EC OLTC 3 EXCESS RUN TIME – PRESENCE Blocking of the tap changing and: Generate alarm 006 AA O.L.T.C. BLOCKED Generate KIT 124 EC OLTC BLOCKED - PRESENCE Provide input to logic to generate tap changers discrepancy: Generate alarm 007 AA O.L.T.C. POSITION DISCREPANCY Generate KIT 125 EC OLTC DISCREPANCY POS – PRESENCE Provide input to Mimic diagram Loss of the remote tap change ability will neccesitate to manual operation => S4 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SHS
2 | LNE |  |  |  | 2LNE0463 | 2GSE001AR | [10 empty] | B0067 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | This cabinet houses the Bently racks for the turbine expansion and vibration sensors. It also houses the acquisition rack for the RCP system. The vibration measurerment circuit now produces an automated 2oo20 protection trip. This cabinet houses various equipment required for the Turbine Protection and Control system (GSE/GSE) to operate. A single failure of the cabinet to perform its function would require additional failures of the equipment to make the criteria for C2 classification. The only aspect that could lead to the complete cabinet failure is loss of power supply; however, the power supply is redundant to all the cabinets, therefore the cabinet is not a SPV. | SLM
2 | PMC |  |  |  | 2LKL0107 | 2PMC002TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in Fuel bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment will/could require outage repair time > 12 h => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | PMC |  |  |  | 2LKL0107 | 2PMC002TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in Fuel bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment will/could require outage repair time > 12 h => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | PMC |  |  |  | CGE | 2PMC001TB | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to PMC equipment in RX bldg. Failure analysis and classification: Switchboard in service during outage -- Failure to supply 380 Vac to PMC equipment will/could require outage repair time > 12 h => C2,S4,E6 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SLM
2 | PTR |  |  |  | 2LKL0203 | 2PTR005PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump. Function: RX cavity recirculation pump . Failure analysis and classification: Pump used exclusivly during outage for RX Cavity recirculation, transfer water from Internal Storage compartment and to supply RCP pump seal injection. - Failure to function correctly for RX Cavity recirculation, transfer water from Internal Storage compartment and to supply RCP pump seal injection => S4,E6 - Failure to function may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E6 | SLM
2 | RAM |  |  |  | 2LKC0205 | 2RAM001MO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
2 | RAM |  |  |  | 2LKC0205 | 2RAM001MO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
2 | RAM |  |  |  | 2LKA0201 | 2RAM002MO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
2 | RAM |  |  |  | 2LKA0201 | 2RAM002MO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Electric motor Function: To provide drive to the 3 phase 260 V generator 001 AP Failure analysis and classification: Two 100% motor-generator sets, normally synchronized and in parallel supplying RGL => I1,I4 On return from outage both set are required to be in service Failure to function correctly may require outage repair time > 36hrs based on Maintenance repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 - Failure of one set if operating in tandem will result in loss of redundancy => S4 -- PM maintenance require => E6 | SHM
2 | RCP |  |  |  | 2LKC0101 | 2RCP001RS | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 1 heaters Function: Supply to the three ON-OFF heaters on 001 BA - 3 phases supplied by LKC 101 JA Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKC0101 | 2RCP001RS | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 1 heaters Function: Supply to the three ON-OFF heaters on 001 BA - 3 phases supplied by LKC 101 JA Failure analysis and classification: Component in service during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKB0205 | 2RCP002RS | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 2 heaters Function: Supply to the three ON-OFF heaters on 001 BA - 3 phases supplied by LKB 205 JA Failure analysis and classification: Component inservice during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKB0205 | 2RCP002RS | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 2 heaters Function: Supply to the three ON-OFF heaters on 001 BA - 3 phases supplied by LKB 205 JA Failure analysis and classification: Component inservice during start-up, shutdown and significant change in RCP boron concentration -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKA0103 | 2RCP003RS | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKA0103 | 2RCP003RS | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKB0207 | 2RCP004RS | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCP |  |  |  | 2LKB0207 | 2RCP004RS | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM
2 | RCV |  |  |  | 2LLD0510 | 2RCV054VP | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the suction line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | RCV |  |  |  | 2LLC0504 | 2RCV053VP | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the suction line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. - Valve failure to function as require for maintenence activity => S4,E5,E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | RCV |  |  |  | 2LLD0507 | 2RCV084VP | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | RCV |  |  |  | 2LLD0506 | 2RCV086VP | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | RCV |  |  |  | 2LLC0502 | 2RCV083VP | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 001 and 002 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | RCV |  |  |  | 2LLC0501 | 2RCV085VP | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve Function: To isolate the discharge line between 002 and 003 PO Failure analysis and classification: Valve normally OPEN. Used for maintenence activity. Valve under high pressure => A2 - Valve failure to function as require for maintenence activity => S4,E5.E6 - SRSM requirement - 1 RO - verify correct operation - outage => S4,E5,E6 - Failure to function correctly may require outage repair time > 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 GC 83539-007 GA Following the System Engineering screening & evaluation of SPVs, these components are no longer considered SPVs, classification to be updated on IQReview => Not C2 and A functional failure of the component may result in a greater than 36 hour delay in an intended change of the Reactor Operating State, or a greater than 36 hour delay in the return from outage => S7. | SLS
2 | REA |  |  |  | 2LLI0101 | 2REA001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralized water pump Component 50% in service. Failure of the motor/pump will reduce necessary redundancy (not periodically tested) in primary system make-up => S4 | SLM
2 | REA |  |  |  | 2LLJ0103 | 2REA002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralized water pump Component 50% in service. Failure of the motor/pump will reduce necessary redundancy (not periodically tested) in primary system make-up => S4 | SLM
2 | RIS |  |  |  | 2LLE0405 | 2RIS021PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Single stage centrifugal pump Function: To recirc the BIT for sampling purposes. Failure analysis and classification: Component used during power operation => NO C3 but S4, E6 | SLM
2 | RPE |  |  |  | B0103 | 2RPE003PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Discharge pump for RPE011PS. Component used mostly during RO when draining or filling operations are in progress. => E6 RPE 003/4 PO are the floor drains pumps in the reactor building. During the RO’s they are used to remove water drained from the reactor vessel cavity. During plant operation they are used to remove water as a result of external leakage from liquid systems in the RX. Classification has been changed. => S4, E5. | SLM
2 | RPE |  |  |  | E0406 | 2RPE004PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Discharge pump for RPE011PS. Component used mostly during RO when draining or filling operations are in progress. => E6 RPE 003/4 PO are the floor drains pumps in the reactor building. During the RO’s they are used to remove water drained from the reactor vessel cavity. During plant operation they are used to remove water as a result of external leakage from liquid systems in the RX. Classification has been changed. => S4, E5. | SLM
2 | RRB |  |  |  | 2LLC0607 | 2RRB001TB | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
2 | RRB |  |  |  | 2LLD0707 | 2RRB002TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380Vac Switchboard Function: 380Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
2 | RRB |  |  |  | 2LLC0610 | 2RRB003TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
2 | RRB |  |  |  | 2LLD0703 | 2RRB004TB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "back-up supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "back-up supply" to trace heating => S4,E5 | SHM
2 | RRB |  |  |  | 2LLC0610 | 2RRB003TB | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 Vac Switchboard Function: 380 Vac to "normal supply" trace heating circuits. Failure analysis and classification: Switchboard permanently in service and energized => I1,I4 -- Failure to supply 380 Vac "normal supply" to trace heating => S4,E5 | SHM
2 | SAP |  |  |  | 2LKF0508 | 2SAP201VA | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor operated isolation valve - SAR from SAT isolation. Valve normally open. Closed manually from C/room upon low pressure condition to protect essential air supply => S4. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | SLM
2 | SEC |  |  |  | 2LLE0302 | 2SEC009FI | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train A - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
2 | SEC |  |  |  | 2LLB0404 | 2SEC010FI | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train B - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
2 | SEC |  |  |  | 2LLE0301 | 2SEC011FI | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train A - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
2 | SEC |  |  |  | 2LLB0405 | 2SEC012FI | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Inline filter Function: Train B - washwater supply Failure analysis and classification: Installed in corrosive environment => A6 -- Failure to filter will result in loss of redundancy => S4 | SLS
2 | STR |  |  |  | 2LKA0101 | 2STR001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply water to the steam transformer Failure analysis and classification: Failure will result in loss of feedwater o the steam transformer => S4,E6 | SLM
2 | STR |  |  |  | 2LKB0209 | 2STR002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply water to the steam transformer Failure analysis and classification: Failure will result in loss of feedwater o the steam transformer => S4,E6 | SLM
2 | SXS |  |  |  | 2LKE0205 | 2SXS004PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Extended Spindle Pump. SXS 004 PO is the last line of defence in removing water from the MX should the other 2 pumps fail or be insufficient in volume. =>S4 If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | SLM
2 | TEG |  |  |  | 2LKJ0406 | 2TEG002CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Compressor for hydrogenated gas from 9TEG001BA. Function: Compress hydrogenated gas and discharge to TEG storage tanks. Failure analysis and classification: Component cycled frequently. => I2 Component failure to compress will require the standby compressor to operate. => S4 Component leak could cause a hydrogen explosion or a Nitrogen leak. => S1 | SHM
2 | TEG |  |  |  | 2LKJ0405 | 2TEG002RS | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Heater associated with the operation of iodine traps on failure -> partial or total unavailability of an iodine, chapter 9 test but no associated event -> S1 | SLM
2 | TEG |  |  |  | 2LKJ0407 | 2TEG002ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Continuous aerated vents fan. Function: Extract hazardous gasses from RPE vent pots and sampling boxes. Component 50% in service Failure analysis and classification: Component always in service and pressurised when selected. I1,I4 Component failure will require the other fan to be placed in service. => S4 Component failure could allow the escape of hazardous and radioactive gases from sampling boxes. => S1 | SLM
6 | SSM |  |  |  | 6SSM403AR | 6SSM403ZV | [10 empty] | B0301 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
9 | KRT |  |  |  | 9KRT510CR | 9KRT502PO | [10 empty] | B0600 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: To supply samples to radiation detector Failure analysis and classification: Component always in service => I1,I4 Failure will result in loss of KRT505MA sampling => S4,E6 | SHM
9 | ASG |  |  |  | 1LLC0312 | 9ASG004PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Feedwater pump 1 for 001DZ Function: Supplies feedwater to the degasser. Failure analysis and classification: Component 50% in service and only when the degasser is started up. Component failure would be backed up by the 2nd feedpump. The pump is required for redundancy as the urgency of ASG tank makeup coul cause outage delays if no feedpump is available. => S4 | SLM
9 | ASG |  |  |  | 2LLC0312 | 9ASG005PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Feedwater pump for 001DZ Function: Supplies feedwater to the degasser. Failure analysis and classification: Component 50% in service and only when the degasser is started up. Component failure would be backed up by the 2nd feedpump. The pump is required for redundancy as the urgency of ASG tank makeup coul cause outage delays if no feedpump is available. => S4 | SLM
9 | CTE |  |  |  | 9LKP0505 | 9CTE004ZV | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Exhaust fan for the electrolyser room. Component always in service. => I1 Fan ensures removal of all dangerous gasses that might form and escape during the electrolyser process. => S1 | SHM
9 | CTE |  |  |  | 9LKP0504 | 9CTE005ZV | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Exhaust fan for the electrolyser room. Component always in service. => I1 Fan ensures removal of all dangerous gasses that might form and escape during the electrolyser process. => S1 | SHM
9 | CTE |  |  |  | 9LKP0506 | 9CTE006ZV | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Exhaust fan for the electrolyser room. Component always in service. => I1 Fan ensures removal of all dangerous gasses that might form and escape during the electrolyser process. => S1 | SHM
9 | CTE |  |  |  | 9LKP0508 | 9CTE007ZV | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Exhaust fan for the electrolyser room. Component always in service. => I1 Fan ensures removal of all dangerous gasses that might form and escape during the electrolyser process. => S1 | SHM
9 | DMM |  |  |  | 1DMM002CR | 1DMM001PJ | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DMM |  |  |  | 2DMM002CR | 2DMM001PJ | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DMM |  |  |  | 9DMM001CR | 9DMM001PR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DMP |  |  |  | 9LKX0210 | 9DMP001PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DMP |  |  |  | 9LKX0201 | 9DMP002PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DMX |  |  |  | 9LLV0201 | 9DMX007PR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | DVN |  |  |  | 9DVN002BX | 9DVN002ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB supply air fan. Component used to supply air to the NAB common rooms. => E6 This component is in continuous operation. => I1 PSA Significant Component => S6. | SHM
9 | DVN |  |  |  | 9DVN005BX | 9DVN005ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | NAB exhaust air fan. Component used to exhaust air from the NAB common rooms. This component is in continuous operation. => I1 PSA Significant Component => S6. | SHM
9 | DWX |  |  |  | 9LKP0509 | 9DWX012ZV | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
9 | DWX |  |  |  | 9DWX005CR | 9DWX012ZV | [10 empty] | B0042 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
9 | DWX |  |  |  | 9DWX002CR | 9DWX026ZV | [10 empty] | B0044 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
9 | JPD |  |  |  | 9LKK0508 | 9JPD001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Supply pump to 9JPD001BA. Component only in service when selected from the control room and then only runs when a low level is reached in the tank. Component failure would reduce redundancy as the last pump will be selected to run. => S4,E6 Plant OE has shown JPD components ate prone to internal corrosion. =>A8 | SLS
9 | JPD |  |  |  | 9LKK0503 | 9JPD002PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Supply pump to 9JPD001BA. Component only in service when selected from the control room and then only runs when a low level is reached in the tank. Component failure would reduce redundancy as the last pump will be selected to run. => S4,E6 Plant OE has shown JPD components ate prone to internal corrosion. =>A8 | SLS
9 | LBH |  |  |  | 9LKN0211 | 9LBH001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LBH feeder diagram indicates that loss of LBH001RD will result in loss of LBH001TB. Therefore the loss of LBH001RD shall have the same classification as LBH001TB => C2,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
9 | LCE |  |  |  | 9LKN0609 | 9LCE001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LCE feeder diagram indicates that loss of LCE001RD will result in loss of LCE001TB. Therefore the loss of LCE001RD shall have the same classification as LCE001TB => C2,S4,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHM
9 | LHS |  |  |  | 9LLV0208 | 9LHS001PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 001 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 001 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 002 PO would be required to fulfil this function. = > S4. | SLM
9 | LHS |  |  |  | 9LLV0209 | 9LHS002PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: fuel transfer from 004 BA to 005 BA Failure analysis and classification: -- 002 PO fuel pump operates infrequently to transfer fuel from 004 BA to 005 BA during engine operation. -- Pump failure would result in 002 PO failure to transfer fuel from 004 BA to 005 BA. This would result in a reduction of redundancy and 001 PO would be required to fulfil this function. = > S4. | SLM
9 | LHS |  |  |  | 9LLV0210 | 9LHS003PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Pump Function: to supply fuel from 005 BA to engine fuel rack during engine operation. Failure analysis and classification: -- 003 PO fuel pump operates continuously to supply fuel from 005 BA to engine fuel rack during standby and engine operation. = > I1 -- 003 PO failure would result in failure to transfer fuel from 005 BA to engine fuel rack during standby conditions. This would result in a reduction of redundancy and 007 PO would be required to fulfill this function on its own. = > S4. Requirement in the SAR of both 003 and 007 PO to be operable is not critical. | SHM
9 | LHS |  |  |  | 9LLM001TR | 9LHS007ZV | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM | Fan Function: Exhausts air from the battery room Failure analysis and classification: Fan continuously in service I1,I4 Failure could result in a build-up of hydrogen leading to an explosion => S1,E5,E6 | SHM
9 | LKX |  |  |  | 9LKX0101 | 9LKX001PR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | S1 - A functional failure of the lifting equipment or lifting equipment components will result in an unacceptable increase in personnel, industrial safety risk. Lifting equipment are required to be maintained according to OHSA regulations. E6 - There are economic reasons to perform preventive maintenance on the lifting equipment or lifting equipment components, rather than to let it degrade. | SLM
9 | LKX |  |  |  | 9LKP0309 | 9LKX001TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKX001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => S4,E6,I1,I4,A6,A7 | SHS
9 | LKX |  |  |  | 9LKP0309 | 9LKX001TB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LKX001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => S4,E6,I1,I4,A6,A7 | SHS
9 | REA |  |  |  | 9LKI0309 | 9REA002AG | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Motor driven stirrer Function: To allow boron batching - inside 005 BA Failure analysis and classification: - Stirrer used extensively during unit outage, while on critical path any delay will result in outage delay. Failure to function correctly may require outage repair time < 36hrs based on Maintenances repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => S4,E6 | SLM
9 | SED |  |  |  | 9LKK0101 | 9SED001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralised water pump. Component used to pump SED water to all the end users at various levels throughout the plant. => E6 PSA Significant Component => S6. Component 50% in service. | SLM
9 | SED |  |  |  | 9LKK0207 | 9SED002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Significant |  |  | Demineralised water pump. Component used to pump SED water to all the end users at various levels throughout the plant. => E6 PSA Significant Component => S6. Component 50% in service. | SLM
0 | SEK |  |  |  | 0SEK001AR | 0SEK001MD | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Flow transmitter. Flow transmitters in the SEK system are classified E6. | ELM
0 | SEK |  |  |  | 0SEK001AR | 0SEK002MD | [10 empty] | B0901 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Flow transmitter. Flow transmitters in the SEK system are classified E6. | ELM
0 | SEK |  |  |  | 0SEK001AR | 0SEK003MD | [10 empty] | B0902 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Flow transmitter. Flow transmitters in the SEK system are classified E6. | ELM
0 | LZB |  |  |  | 9LKK0407 | 0LZB001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LZB feeder diagram indicates that loss of LZB001RD will result in loss of LZB001TB. Therefore the loss of LZB001RD shall have the same classification as LZB001TB => E5,E6,I1,I4 | EHM
0 | LZB |  |  |  | 0LZB001RD | 0LZB001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LZB feeder diagram indicates that loss of LZB001RD will result in loss of LZB001TB. Therefore the loss of LZB001RD shall have the same classification as LZB001TB => E5,E6,I1,I4 | EHM | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZB001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM
0 | LZB |  |  |  | 0LZB001TB | 0LZC001TB | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZB001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZC001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM
0 | LZC |  |  |  | 0LZB001TB | 0LZC001TB | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZB001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZC001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM
0 | LZC |  |  |  | 0LZD001TB | 0LZC001TB | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 50 Vdc Switchboard Function: 50 Vdc to various equipment - metering board. Failure analysis and classification: Switchboard permanently in service => I1,I4 -- Failure to supply auxiliary equipment => E6 CLASSIFICATION REVIEW: ERCR 36711 Classification changed to E5,E6,I1,I4 | EHM | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZC001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM
0 | LZC |  |  |  | 0LZD002TB | 0LZC001TB | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 50 Vdc Switchboard Function: 50 Vdc to various equipment - metering board. Failure analysis and classification: Switchboard permanently in service => I1,I4 -- Failure to supply auxiliary equipment => E6 CLASSIFICATION REVIEW: ERCR 36711 Classification changed to E5,E6,I1,I4 | EHM | General description: 220 V Switchboard Function: Supplies 220 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LZC001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => E5,E6,I1,I4 | EHM
0 | LZD |  |  |  | 9LKK0301 | 0LZD001RD | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LZD feeder diagram indicates that loss of LZD001RD will result in loss of LZD001TB. Therefore the loss of LZD001RD shall have the same classification as LZD001TB => E6,I1,I4 | EHM
0 | LZD |  |  |  | 9LKK0401 | 0LZD002RD | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Rectifier. Function: To convert an AC supply to a DC supply. Failure analysis and classification: Review of the LZD feeder diagram indicates that loss of LZD001RD will result in loss of LZD001TB. Therefore the loss of LZD001RD shall have the same classification as LZD001TB => E6,I1,I4 | EHM
0 | SEK |  |  |  | 9LKX0105 | 0SEK001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump. Pumps in the SEK system are classified E6. | ELM
0 | SEK |  |  |  | 9LKX0103 | 0SEK002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump. Pumps in the SEK system are classified E6. | ELM
0 | SEK |  |  |  | 9LKX0105 | 0SEK001PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump. Pumps in the SEK system are classified E6. | ELM
0 | SEK |  |  |  | 9LKX0103 | 0SEK002PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump. Pumps in the SEK system are classified E6. | ELM
1 | DVL |  |  |  | 1LLE001TB | 1DVL002JS | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380 V Switchboard Function: Supplies 380 V to various equipment. Failure analysis and classification: Review of the feeder diagram for LLE001TB, and aggregating the classifications of the supplied equipment, modified where necessary, produces a classification of => C2,C3,C6,C7,C8,C9,S1,S4,S5,S6,E5,E6,I1,I4 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | CHM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
1 | DVL |  |  |  | 1DVL002CS | 1DVL002EV | [10 empty] | B0901 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Evaporator Function: Forms part of an air conditioning unit. Failure analysis and classification: Failure will result in the inoperability of the air conditioning unit => E6 | ELM
1 | KRT |  |  |  | 1LMA027JA | 1KRT003AR | [10 empty] | B0904 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Circuit Breaker/Contactor Function: To isolate the equipment from the electrical supply, and provide protection to equipment. Failure analysis and classification: The Circuit Breaker/Contactor is a component of the switchboard. The maintenance requirements applicable to a switchboard includes the maintenance of its circuit breakers/contactors, therefore this circuit breaker/contactor is classified => E5,E6,I1,I4 | EHM | General description: Cabinet. Function: To accommodate equipment. Failure analysis and classification: 1 - All enclosures and cabinets designed to provide a controlled environment for the enclosed equipment are classified based on the effect of the total loss of the enclosure or cabinet. 2 - All enclosures and cabinets hosting only components which do not have individual trigrammes are classified based on the effect of the total loss of the enclosure or cabinet. 3 - All enclosures and cabinets hosting a combination of components with and without individual trigrammes are classified based on the effect of the total loss of the components which do not have individual trigrammes. 4 - All enclosures and cabinets hosting only components with individual trigrammes are classified as either RTM, or E6,A6 if this is necessary for environmental reasons. E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LCJ |  |  |  | 1LMJ-001AR | 1LCJ001AR | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 48 V Switchboard Function: Supplies 48 V to various equipment. Failure analysis and classification: Aggregating the classifications of the incoming and outgoing breakers produces a classification of => E5,E6,I1,I4 | EHM
1 | LTP |  |  |  | 1LTP001CR | 1RPE025PO | [10 empty] | B0916 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Temporary supply board. Provided for convenience during outages => RTF. | RTM | General description: Submersible pump for 1RPE003CU. Component used infrequently during normal unit operation. => E6 | ELM
1 | KRT |  |  |  | 1KRT001TB | 1KRT002AR | [10 empty] | B0799 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LNI |  |  |  | 1KSC001CR | 1RCP401EN | [10 empty] | B0301 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC001CR | 1RCP403EN | [10 empty] | B0302 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC001CR | 1RCP404EN | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC001CR | 1RCP411EN | [10 empty] | B0304 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP406EN | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP407EN | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP408EN | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP409EN | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | LNI |  |  |  | 1KSC002CR | 1RCP410EN | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0334 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0335 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0336 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0352 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0354 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0355 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0357 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0404 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0405 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0406 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0407 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0408 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0409 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0410 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0411 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP003RS | 1RCP001RG | [10 empty] | B0480 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RCP |  |  |  | 1RCP004RS | 1RCP002RG | [10 empty] | B0481 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description:380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | RGL |  |  |  | 1RGL002AR | 1RGL012CR | [10 empty] | B0339 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL012CR | [10 empty] | B0340 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
1 | RGL |  |  |  | 1RGL002AR | 1RGL012CR | [10 empty] | B0341 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
1 | SXS |  |  |  | 1SXS503AR | 1SXS505PO | [10 empty] | B0603 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Submersible Pump. Failure of the pump would increase the risk of flooding the SEC galleries. => E5. | ELM
1 | SXS |  |  |  | 1SXS504AR | 1SXS506PO | [10 empty] | B0703 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Submersible Pump. Failure of the pump would increase the risk of flooding the SEC galleries. => E5. | ELM
1 | ACO |  |  |  | 1ARE101CR | 1ACO005CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
1 | ACO |  |  |  | 1ACO005CR | 1ACO004CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
1 | ACO |  |  |  | 1ACO004CR | 1ACO006CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
1 | ACO |  |  |  | 1ACO006CR | 1ACO007CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the pump -> E2 | EHM
1 | ACO |  |  |  | 1LKD0307 | 1ACO001RS | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater Function: 001 MO - prevents deterioration of electrical insulation when motor not in service. Failure Analysis and Classification: Component frequently in service and energised => I1,I4 Malfunction of the heater could lead to deterioration of the motor insulation => E2,E5 | EHM
1 | ACO |  |  |  | 1LKD0408 | 1ACO002RS | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater Function: 002 MO - prevents deterioration of electrical insulation when motor not in service. Failure Analysis and Classification: Component frequently in service and energised => I1,I4 Malfunction of the heater could lead to deterioration of the motor insulation => E2,E5 | EHM
1 | AGR |  |  |  | 1LKB0308 | 1AGR101CF | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Centrifuge - 001 BA oil tank. Component always in service. I1 Malfunction will result in loss of the oil purification function => E5 | EHM
1 | AGR |  |  |  | 1LKA0305 | 1AGR102CF | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Centrifuge - 002 BA oil tank. Component always in service. I1 Malfunction will result in loss of the oil purification function => E5 | EHM
1 | AGR |  |  |  | 1LKB0307 | 1AGR001ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - 001 BA - gases and oil vapour evacuation Component always in service. => I1 Depression of about 2.5kPa helps to degas the oil (potential loss of lubrication quality). Gases together with the oil vapour are evacuated via designated channel => E5 | EHM
1 | AGR |  |  |  | 1LKA0304 | 1AGR002ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - 002 BA - gases and oil vapour evacuation Component always in service. => I1 Depression of about 2.5kPa helps to degas the oil (potential loss of lubrication quality). Gases together with the oil vapour are evacuated via designated channel => E5 | EHM
1 | ATE |  |  |  | 1ATE102AR | 1ATE621MG | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
1 | ATE |  |  |  | 1ATE101AR | 1ATE801MG | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
1 | ATE |  |  |  | 1ATE011AR | 1ATE592SN | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE013AR | 1ATE621SN | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE013AR | 1ATE622SN | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE014AR | 1ATE711SN | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE014AR | 1ATE712SN | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE011AR | 1ATE591SN | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
1 | ATE |  |  |  | 1ATE202AR | 1ATE500MG | [10 empty] | B0052 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
1 | CAP |  |  |  | 1LKC0511 | 1CAP004VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolation valve. Function: Additional or quick make up of feedwater supply to condenser at a maximum rate of 100 t/h from SER system. Valve receives opening order from control room 001 TL on request. Failure analysis and classification: Fails to open/jammed closed : Failure when required (not continuously in service, and assuming 002 VL not available automatically, but manually). Manual actuation of valve still possible locally. Manual valve 003 VL still available for emergency make-up => E6. | ELM
1 | CET |  |  |  | 1LKD0308 | 1CET001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Exhaust fan - gland steam condenser 001 CS Function: Maintains shell side of the gland steam condenser at a negative pressure. Failure analysis and classification: Fan operation is controlled from 001 TL Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Failure to function while unit on power will result in an increase of incondensable gases in main condenser, progressive decrease of the steam flow through the main turbine seals thus increase seals temperature, increase level in the barometric loop, etc. Turbine however could remain in operation for some time allowing for the fan to be repaired => E5 | EHM
1 | CEX |  |  |  | 1CEX005CR | 1CEX004CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Local control box of the isolation valve to the pump discharge power on TEM CEX On failure -> Unable to operate the valve electrically -> risk of having a pump CEX unavailable -> E6 | EHM
1 | CEX |  |  |  | 1LKF0204 | 1CEX001RS | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 001 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 | EHM
1 | CEX |  |  |  | 1LKF0203 | 1CEX002RS | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 | EHM
1 | CEX |  |  |  | 1LKF0202 | 1CEX003RS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 003 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 | EHM
1 | CFI |  |  |  | 1LKG0208 | 1CFI004CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
1 | CFI |  |  |  | 1LKG0201 | 1CFI001CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | CFI |  |  |  | 1LKG0403 | 1CFI001CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | CFI |  |  |  | 1LKG0202 | 1CFI002CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | CFI |  |  |  | 1LKG0404 | 1CFI002CR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | CFI |  |  |  | 1LKG0203 | 1CFI003CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
1 | CFI |  |  |  | 1LKG0405 | 1CFI003CR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
1 | CFI |  |  |  | 1LKG0204 | 1CFI001PO | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1LKG0205 | 1CFI002PO | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1LKG0206 | 1CFI003PO | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1LKG0102 | 1CFI004PO | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1LKG0101 | 1CFI005PO | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1LKG0402 | 1CFI006PO | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | CFI |  |  |  | 1CFI027CR | 1CFI021MO | [10 empty] | B0041 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor Function: To drive rake cutter Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI027CR | 1CFI022MO | [10 empty] | B0042 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor Function: To drive rake travelling device Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI015CR | 1CFI009MO | [10 empty] | B0043 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI015CR | 1CFI009MO | [10 empty] | B0044 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI015CR | 1CFI010MO | [10 empty] | B0045 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI017CR | 1CFI011MO | [10 empty] | B0046 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI017CR | 1CFI011MO | [10 empty] | B0047 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI017CR | 1CFI012MO | [10 empty] | B0048 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI019CR | 1CFI013MO | [10 empty] | B0049 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI019CR | 1CFI013MO | [10 empty] | B0050 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI019CR | 1CFI014MO | [10 empty] | B0051 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI021CR | 1CFI015MO | [10 empty] | B0052 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI021CR | 1CFI015MO | [10 empty] | B0053 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI021CR | 1CFI016MO | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI023CR | 1CFI017MO | [10 empty] | B0055 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 005 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI023CR | 1CFI017MO | [10 empty] | B0056 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 005 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI023CR | 1CFI018MO | [10 empty] | B0057 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 005 DG | EHS
1 | CFI |  |  |  | 1CFI025CR | 1CFI019MO | [10 empty] | B0058 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI025CR | 1CFI019MO | [10 empty] | B0059 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI025CR | 1CFI020MO | [10 empty] | B0060 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
1 | CFI |  |  |  | 1CFI003CR | 1CFI025MO | [10 empty] | B0100 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI003CR | 1CFI025MO | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI003CR | 1CFI025MO | [10 empty] | B0102 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI002CR | 1CFI024MO | [10 empty] | B0103 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI002CR | 1CFI024MO | [10 empty] | B0104 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI002CR | 1CFI024MO | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI001CR | 1CFI023MO | [10 empty] | B0106 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6, I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI001CR | 1CFI023MO | [10 empty] | B0107 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6, I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CFI |  |  |  | 1CFI001CR | 1CFI023MO | [10 empty] | B0108 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6, I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
1 | CSI |  |  |  | 1LKG0212 | 1CSI001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 001 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0312 | 1CSI002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 001 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0311 | 1CSI003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 002 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0310 | 1CSI004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 002 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0309 | 1CSI005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 003 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0308 | 1CSI006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 003 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
1 | CSI |  |  |  | 1LKG0307 | 1CSI004VC | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 001 & 002 PO interconnection | ELM
1 | CSI |  |  |  | 1LKG0306 | 1CSI005VC | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 002 & 003 PO interconnection | ELM
1 | CTA |  |  |  | 1LKA0411 | 1CTA001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CTA |  |  |  | 1LKA0412 | 1CTA002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CTA |  |  |  | 1LKA0512 | 1CTA003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CTA |  |  |  | 1LKA0511 | 1CTA004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CTA |  |  |  | 1LKA0510 | 1CTA005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CTA |  |  |  | 1LKA0509 | 1CTA006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | CVI |  |  |  | 1LKB0107 | 1CVI001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKB0105 | 1CVI002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKC0107 | 1CVI003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKC0105 | 1CVI004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump motor. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKB0211 | 1CVI005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKC0203 | 1CVI006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
1 | CVI |  |  |  | 1LKC0504 | 1CVI007VA | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 001 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 001PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | CVI |  |  |  | 1LKC0503 | 1CVI010VA | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 002 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 002PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | CVI |  |  |  | 1LKC0502 | 1CVI013VA | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 003 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 003PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | CVI |  |  |  | 1LKC0501 | 1CVI016VA | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 004 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 004 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | CVI |  |  |  | 1LKC0505 | 1CVI046VA | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 006 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 006 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | CVI |  |  |  | 1LKC0506 | 1CVI043VA | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 005 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 005 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. | ELM
1 | DEG |  |  |  | 1LLE0304 | 1DEG201CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
1 | DEG |  |  |  | 1LLD0312 | 1DEG101CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
1 | DEG |  |  |  | 1LLJ0312 | 1DEG301CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
1 | DEG |  |  |  | 1LLE0107 | 1DEG006PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLD0107 | 1DEG005PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLA0107 | 1DEG008PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLJ0107 | 1DEG007PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLC0310 | 1DEG205VD | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 201 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLB0306 | 1DEG105VD | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 101 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLE0303 | 1DEG405VD | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 401 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 | ELM
1 | DEG |  |  |  | 1LLD0311 | 1DEG305VD | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 301 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 | ELM
1 | DVC |  |  |  | 1DVC013CR | 1DVC003RS | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet / Enclosure => RTF | RTM | General description: Electric heater Function: To maintain comfortable temperature in habitable rooms and equipment within required temperatures. Failure analysis and classification: Malfunction of the heater could lead to reduced temperatures => E6 | ELM
1 | DVC |  |  |  | 1DVC013CR | 1DVC004RS | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet / Enclosure => RTF | RTM | General description: Electric heater Function: To maintain comfortable temperature in habitable rooms and equipment within required temperatures. Failure analysis and classification: Malfunction of the heater could lead to reduced temperatures => E6 | ELM
1 | DVC |  |  |  | 1LKF0412 | 1DVC010RS | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Iodine filters conditioning electric heater Purpose - to condition iodine filters while not in service - => E6 | ELM
1 | DVG |  |  |  | 1LKE0304 | 1DVG001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electrical Air Heater - DVG 003 ZV and DVG 004 ZV discharge line Component fails to generate heat => E6 | ELM
1 | DVI |  |  |  | 1LKS0204 | 1DVI001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air heater - fresh air intake duct Maintains air temperature in RRI rooms above 15°C - failure will result in alarm =>E6 (no frost in SA conditions ) | ELM
1 | DVI |  |  |  | 1LLC0308 | 1DVI001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train A Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
1 | DVI |  |  |  | 1LLD0310 | 1DVI002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train B Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
1 | DVI |  |  |  | 1LLC0309 | 1DVI003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train A Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
1 | DVI |  |  |  | 1LLB0607 | 1DVI004ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train B Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
1 | DVK |  |  |  | 1LKF0408 | 1DVK005RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - iodine filter conditioning heater inside 001 PI | ELM
1 | DVK |  |  |  | 1LKF0105 | 1DVK001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air supply fan - odd line SRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
1 | DVK |  |  |  | 1LKD0203 | 1DVK002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air supply fan - even line SRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
1 | DVK |  |  |  | 1LKF0103 | 1DVK003ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air exhaust fan - odd line SRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
1 | DVK |  |  |  | 1LKD0201 | 1DVK004ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air exhaust fan - even line SSRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
1 | DVL |  |  |  | 1LKH0302 | 1DVL102RS | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - SAP compressor room. | ELM
1 | DVL |  |  |  | 1LKH0301 | 1DVL103RS | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - SAP compressor room. | ELM
1 | DVM |  |  |  | 1DVM001AR | 1DVM001PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply 001EV. Circulates water that cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM001AR | 1DVM002PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply 001 EV. Circulates water that cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM004AR | 1DVM007PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply 004 EV. Circulates water that cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM004AR | 1DVM008PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply 004 EV. Circulates water that cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM001AR | 1DVM001ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - cooling air supply. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
1 | DVM |  |  |  | 1DVM001AR | 1DVM002ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - cooling air supply. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
1 | DVM |  |  |  | 1DVM004AR | 1DVM007ZV | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - cooling air supply. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
1 | DVM |  |  |  | 1DVM004AR | 1DVM008ZV | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - cooling air supply. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
1 | DVM |  |  |  | 1DVM001AR | 1DVM009ZV | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - exhaust air. Main ventilation fan for the ATE plant => E6. In continuous operation =>I1. | EHM
1 | DVM |  |  |  | 1DVM004AR | 1DVM019ZV | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM010CR | 1DVM020ZV | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - exhaust and mtr for lab battery rm. Cools equipment that is vital for production => E6. | ELM
1 | DVM |  |  |  | 1DVM010CR | 1DVM021ZV | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
1 | DVN |  |  |  | 1LKJ0401 | 1DVN035ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Smoke extraction fan. Component used to extract smoke from the electrical rooms after a fire. => E6 | ELM
1 | DVS |  |  |  | 1LLA0408 | 1DVS005ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from EAS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
1 | DVS |  |  |  | 1LLB0411 | 1DVS006ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from EAS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
1 | DVS |  |  |  | 1LLA0409 | 1DVS007ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
1 | DVS |  |  |  | 1LLB0412 | 1DVS008ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from RIS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
1 | DVW |  |  |  | 1LKH0401 | 1DVW003RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Iodine filter conditioning electric heather SRSM requirement - 1RO verify correct operation of the fan (and associated logic) | ELM
1 | EPP |  |  |  | 1LLB0609 | 1EPP101AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM
1 | EPP |  |  |  | 1LLB0611 | 1EPP201AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS
1 | GEV |  |  |  | 1LKF0506 | 1GEV004AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Local cabinet - 001 TS, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. | ELS
1 | GEV |  |  |  | 1LKE0105 | 1GEV001CR | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | GEV |  |  |  | 1LKE0105 | 1GEV001CR | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
1 | GEV |  |  |  | 1LKH0411 | 1GEV002CR | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM
1 | GGR |  |  |  | 1LKF0512 | 1GGR012PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - jacking oil pumps suction booster Function: Jacking oil suction booster pump when 002, 003, or 004 PO are not available. (ie in outage) Failure analysis and classification: Pump required in service when turbine alignment and coupling work is being performed. Also if suction of jacking oil pumps drops bellow 140 kPa ( 002 , 003 and 004 PO would have to fail) during turbine rundown. => E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | ELM
1 | GGR |  |  |  | 1LKH0409 | 1GGR022ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - cooling 02 0 MO (turning gear motor) Fan require in service to maintain motor temp below 75 degrees C => E5 (unit 2 70 degrees C) Component in continuous service => I1 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHM
1 | GHE |  |  |  | 1LKH0410 | 1GHE001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 3 80V Main seal oil pump taking suction from 001 DZ vacuum tank. -Provides a small amount of detrained oil back to the seal oil supply to the generator seal oil circuit, while the bulk is returned to 001 DZ on second spraying rack. - Failure resulting from blocked inlet strainer/filter in vacuum tank 001 DZ, reduction in defence of depth, requires emergency seal oil pump 003 PO to operate => E6,I1,I4 . Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | EHM
1 | GHE |  |  |  | 1LKE0303 | 1GHE005PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 380V rotary positive displacement vacuum pump. -Provides removal of oil entrained air from vacuum tank 001 DZ, keeping the tank under a constant vacuum between 70-80 mm Hg. Oil supplied from GGR system. -If 220V DC emergency pump in service 004 PO, then can only run pump for 1 hr. -Loss of function to extract from 001 DZ vacuum tank, and maintain de-aeration => No immediate effect to system. H2 purity must be monitored => E6,I1, I4. | EHM
1 | GST |  |  |  | 1LKF0510 | 1GST001RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater Function: To heat water in 001 BA Failure analysis and classification: Used exclusively during outage. No credit for 002 RS (both heaters require). - Failure to function ¿ during outage to assist vacuum drying of the alternator stator bars before GST draining => E5. ¿ used during outage to prevent condensation inside alternator (mini outage) => E5 - Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E5 | ELM
1 | GST |  |  |  | 1LKF0509 | 1GST002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater Function: To heat water in 001 BA Failure analysis and classification: Used exclusively during outage. No credit for 001 RS (both heaters require). - Failure to function ¿ during outage to assist vacuum drying of the alternator stator bars before GST draining => E5. ¿ used during outage to prevent condensation inside alternator (mini outage) => E5 - Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E5 | ELM
1 | GSY |  |  |  | 1GSY003AR | 1GSY101JS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
1 | GSY |  |  |  | 1GSY003AR | 1GSY201JS | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
1 | GSY |  |  |  | 1GSY003AR | 1GSY301JS | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
1 | LGA |  |  |  | 1LGA001TR | 1LGA001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
1 | LGA |  |  |  | 1LGA001TR | 1LGA001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
1 | LGD |  |  |  | 1LGD001TR | 1LGD001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
1 | LGD |  |  |  | 1LGD001TR | 1LGD001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
1 | LHP |  |  |  | 1LLG0207 | 1LHP001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
1 | LHP |  |  |  | 1LLG0208 | 1LHP002CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
1 | LHP |  |  |  | 1LLG0206 | 1LHP003RE | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: LHJ 002 AR (AVR) Anti-condensation heater Function: Prevent moisture and associated corrosion products in AVR cabinet. Failure analysis and classification: Failure of the heater does not impact EDG operability directly. Longer term degradation of the AVR components occur as a result of moisture and formation of corrosion products. | EHM
1 | LHP |  |  |  | 1LLG0209 | 1LHP003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHP |  |  |  | 1LLG0210 | 1LHP004ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHP |  |  |  | 1LLG0211 | 1LHP005ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHP |  |  |  | 1LLG0212 | 1LHP006ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHQ |  |  |  | 1LLW0207 | 1LHQ001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
1 | LHQ |  |  |  | 1LLW0208 | 1LHQ002CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
1 | LHQ |  |  |  | 1LLW0206 | 1LHQ003RE | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: LHJ 002 AR (AVR) Anti-condensation heater Function: Prevent moisture and associated corrosion products in AVR cabinet. Failure analysis and classification: Failure of the heater does not impact EDG operability directly. Longer term degradation of the AVR components occur as a result of moisture and formation of corrosion products. | EHM
1 | LHQ |  |  |  | 1LLW0209 | 1LHQ003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHQ |  |  |  | 1LLW0210 | 1LHQ004ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHQ |  |  |  | 1LLW0211 | 1LHQ005ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LHQ |  |  |  | 1LLW0212 | 1LHQ006ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
1 | LLN |  |  |  | 1LLA0101 | 1LLN001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM
1 | LLO |  |  |  | 1LLB0103 | 1LLO001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 | EHM
1 | LMA |  |  |  | 1LMA0254 | 1KIR001AR | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General Description: Cabinet, loose parts monitoring. All cabinets are classified as RTF. High Level Tasks are associated with the Cabinets for Maintenance Planning purposes.=>E6 | ELM
1 | LMA |  |  |  | 1LMA120CR | 1CFI001MO | [10 empty] | B0121 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA120CR | 1CFI002MO | [10 empty] | B0122 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA120CR | 1CFI003MO | [10 empty] | B0123 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA120CR | 1CFI004MO | [10 empty] | B0124 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA120CR | 1CFI005MO | [10 empty] | B0125 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA120CR | 1CFI006MO | [10 empty] | B0126 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
1 | LMA |  |  |  | 1LMA130CR | 1CFI001CR | [10 empty] | B0131 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | LMA |  |  |  | 1LMA130CR | 1CFI002CR | [10 empty] | B0132 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
1 | LMA |  |  |  | 1LMA130CR | 1CFI003CR | [10 empty] | B0133 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
1 | LMA |  |  |  | 1LMA130CR | 1CFI004CR | [10 empty] | B0134 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
1 | LMA |  |  |  | 1LMA140CR | 1CSI004VC | [10 empty] | B0141 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Motor operated isolation valve - 001 & 002 PO interconnection | ELM
1 | LMA |  |  |  | 1LMA140CR | 1CSI005VC | [10 empty] | B0142 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Motor operated isolation valve - 002 & 003 PO interconnection | ELM
1 | LMA |  |  |  | 1LMA160CR | 1KRT001AR | [10 empty] | B0161 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LMA |  |  |  | 1LMA160CR | 1KRT002AR | [10 empty] | B0162 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LMA |  |  |  | 1LMA160CR | 9KRT501AR | [10 empty] | B0163 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LMA |  |  |  | 1LMA180CR | 1GEV001AR | [10 empty] | B0181 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 001 TP, marshalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropriate. | ELS
1 | LMA |  |  |  | 1LMA180CR | 1GEV002AR | [10 empty] | B0182 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 002 TP, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. | ELS
1 | LMA |  |  |  | 1LMA180CR | 1GEV003AR | [10 empty] | B0183 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 003 TP, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. | ELS
1 | LMA |  |  |  | 1LMA180CR | 1GEV004AR | [10 empty] | B0187 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 001 TS, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. | ELS
1 | LNE |  |  |  | 1LNE0213 | 1KRT001AR | [10 empty] | B0039 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LNE |  |  |  | 1LNE0214 | 1KRT002AR | [10 empty] | B0040 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
1 | LNE |  |  |  | 1LNE0331 | 1RCP001RG | [10 empty] | B0053 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | LNE |  |  |  | 1LNE0332 | 1RCP002RG | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
1 | LNE |  |  |  | 1LNE0312 | 1KKO601AR | [10 empty] | B0062 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder for generator active and reactive power. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. | EHM
1 | LNE |  |  |  | 1LNE0313 | 1KKO801AR | [10 empty] | B0063 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder for generator active and reactive power. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. | EHM
1 | LNE |  |  |  | K0102 | 1RPN005AR | [10 empty] | B0083 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: The cabinet houses the audio speaker 403HP that gives an audible sound representing the Source Range count rate. The loss of the audio sound has no consequence. Tasks associated with High Flux Monitoring are required as a nuclear safety contingency and are to be downloaded with the outage scope. These support activity tasks are required when welding is done in the Reactor building.=>E6 | ELM
1 | LNE |  |  |  | B0708 | 1RPN005AR | [10 empty] | B0085 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: The cabinet houses the audio speaker 403HP that gives an audible sound representing the Source Range count rate. The loss of the audio sound has no consequence. Tasks associated with High Flux Monitoring are required as a nuclear safety contingency and are to be downloaded with the outage scope. These support activity tasks are required when welding is done in the Reactor building.=>E6 | ELM
1 | LNE |  |  |  | 1LNE260CR | 1REN010MG | [10 empty] | B0261 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for SG Sodium content. Component used to monitor for Sodium in any of the 3 SG s. Component generates a signal to 1REN090EN. Component generates a signal to threshold relay s 1REN545XU1/527XU1/527XU2/545XU2/529XU1/531XU1. => E6 Plant shutdown within 1HR when in Zone 5 is only required after a manual sample for confirmation => No C3 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN041MG | [10 empty] | B0262 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG001DE. Component generates 1REN054AA Ionic leakage 001DE. Component generates 1REN060EC on KIT This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN042MG | [10 empty] | B0263 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG002DE. Component generates 1REN054AA Ionic leakage 001DE. Component generates 1REN065EC on KIT This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN043MG | [10 empty] | B0264 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG003DE. Component generates 1REN056AA Ionic leakage 001DE. Component generates 1REN069EC on KIT This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN044MG | [10 empty] | B0265 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG004DE. Component generates 1REN056AA Ionic leakage 001DE. Component generates 1REN070EC on KIT This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN071MG | [10 empty] | B0266 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG1. Component generates 1REN052EC PH Low. Component generates 1REN053EC PH Hi. Component generates alarm 1REN051AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN003EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN072MG | [10 empty] | B0267 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG2. Component generates 1REN057EC PH Low. Component generates 1REN058EC PH Hi. Component generates alarm 1REN052AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN004EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN073MG | [10 empty] | B0268 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG3. Component generates 1REN063EC PH Low. Component generates 1REN064EC PH Hi. Component generates alarm 1REN053AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN005EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN081MG | [10 empty] | B0269 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG1. Component generates signal for 1REN080EN. Component generates KIT signal 1REN006EU. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN082MG | [10 empty] | B0270 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG2. Component generates signal for 1REN080EN. Component generates KIT signal 1REN007EU. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN083MG | [10 empty] | B0271 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG3. Component generates signal for 1REN080EN. Component generates KIT signal 1REN008EU. => E6 This component is always in service. => I1 | EHM
1 | LNE |  |  |  | 1LNE260CR | 1REN010MG | [10 empty] | B0272 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for SG Sodium content. Component used to monitor for Sodium in any of the 3 SG s. Component generates a signal to 1REN090EN. Component generates a signal to threshold relay s 1REN545XU1/527XU1/527XU2/545XU2/529XU1/531XU1. => E6 Plant shutdown within 1HR when in Zone 5 is only required after a manual sample for confirmation => No C3 | EHM
1 | LNE |  |  |  | 1LNE320CR | 1ARE002YP | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1SAS supply. All cabinets are classified as RTF. | RTM | General description:Pressure test point on 002GV supply. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
1 | LNE |  |  |  | 1LNE330CR | 1ARE005YD | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 001GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
1 | LNE |  |  |  | 1LNE330CR | 1ARE006YD | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 002GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
1 | LNE |  |  |  | 1LNE330CR | 1ARE007YD | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 001GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
1 | LNE |  |  |  | 1LNE400CR | 1CRF001SN | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 001SP and 001SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 001 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level HIGH: -- Failure to provide correct signal to the logic to generate KIT alarm 001 EC "001MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 004 AA "001MO COOLER HUMIDITY FAULT" => E6 | EHS
1 | LNE |  |  |  | 1LNE400CR | 1CRF001SP | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 001SP and 001SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 001 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 001 AA "001PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 005 EC "01PO-LWR BRG BLOCK pressure" => E5 | EHS
1 | LNE |  |  |  | 1LNE410CR | 1CRF005SN | [10 empty] | B0411 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 003SP and 005SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 002 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level Hi: -- Failure to provide correct signal to the logic to generate KIT alarm 007 EC "002MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 005 AA "002MO COOLER HUMIDITY FAULT" => E6 | EHS
1 | LNE |  |  |  | 1LNE410CR | 1CRF003SP | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 003SP and 005SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 002 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 002 AA "002PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 011 EC "02PO-LWR BRG BLOCK pressure" => E5 | EHS
1 | LNE |  |  |  | 1LNE420CR | 1CRF009SN | [10 empty] | B0421 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 005SP and 009SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 003 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level Hi: -- Failure to provide correct signal to the logic to generate KIT alarm 013 EC "003MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 005 AA "003MO COOLER HUMIDITY FAULT" => E6 | EHS
1 | LNE |  |  |  | 1LNE420CR | 1CRF005SP | [10 empty] | B0422 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 005SP and 009SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 003 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 003 AA "003PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 017 EC "03PO-LWR BRG BLOCK pressure" => E5 | EHS
1 | PTR |  |  |  | 1LKL0204 | 1PTR003PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Skimming pump of the SFP. Function: Removes debris from the surface of the SFP. Failure analysis: Component fails to function.=E6 Component only required to be placed in service when skimming is necessary to remove surface impurities. Pump currently remains in service continuously. => I1,I4 | EHM
1 | RCP |  |  |  | E0103 | 1RCP008RS | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
1 | RCP |  |  |  | E0103 | 1RCP009RS | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
1 | RCP |  |  |  | E0103 | 1RCP010RS | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 003 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
1 | RCP |  |  |  | 1LLD0105 | 1RCP106RS | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS1) - supplied from LLD 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLC0107 | 1RCP105RS | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS1) - supplied from LLC 107 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLD0105 | 1RCP106RS | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS1) - supplied from LLD 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLC0107 | 1RCP105RS | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS1) - supplied from LLC 107 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLD0103 | 1RCP206RS | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS2) - supplied from LLD 103 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 206 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLC0105 | 1RCP205RS | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS2) - supplied from LLC 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 205 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLD0103 | 1RCP206RS | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS2) - supplied from LLD 103 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 206 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RCP |  |  |  | 1LLC0105 | 1RCP205RS | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS2) - supplied from LLC 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 205 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
1 | RPE |  |  |  | A0103 | 1RPE001PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extraction pump for 1RPE001BA. Component used mostly during RO when draining or filling operations are in progress. Component loss during RO will be subsituted by the alternative drains pump => E6 | ELM
1 | RPE |  |  |  | A0103 | 1RPE002PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extraction pump for 1RPE001BA. Component used mostly during RO when draining or filling operations are in progress. Component loss during RO will be subsituted by the alternative drains pump => E6 | ELM
1 | RPE |  |  |  | 1LKH0504 | 1RPE029PO | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Submersible pump for 1RPE004PS. Component used frequently during normal unit operation. => E6 This component has frequent cycles of operation. => I2 | EHM
1 | SEC |  |  |  | 1LLE0611 | 1SEC011AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet. Function: Hosting instrumentation for racking screen 001 FI Failure analysis and classification: Cabinets with equipment identified by the trigramme are classified as RTM. (For corrosive service condition E6,A6 shall apply). | ELS
1 | SEC |  |  |  | 1LLB0502 | 1SEC012AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet. Function: Hosting instrumentation for racking screen 002 FI Failure analysis and classification: Cabinets with equipment identified by the trigramme are classified as RTM. (For corrosive service condition E6,A6 shall apply). | ELS
1 | SEC |  |  |  | 1LLE0711 | 1SEC005PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train A Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
1 | SEC |  |  |  | 1LLB0602 | 1SEC006PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train B Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
1 | SEC |  |  |  | 1LLE0710 | 1SEC007PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train A Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
1 | SEC |  |  |  | 1LLB0603 | 1SEC008PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train B Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
1 | SIT |  |  |  | 1LKF0201 | 1SIT003PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 1 sampling pump Component renown for frequent failure (OE) => E6 | EHM
1 | SIT |  |  |  | 1LKF0406 | 1SIT004PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 2 sampling pump Component renown for frequent failure (OE) => E6 | EHM
1 | SIT |  |  |  | 1LKF0410 | 1SIT005PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 3 sampling pump Component renown for frequent failure (OE) => E6 | EHM
1 | SIT |  |  |  | 1LKH0104 | 1SIT006PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 4 sampling pump Component renown for frequent failure (OE) => E6 | EHM
1 | SIT |  |  |  | 1LKH0103 | 1SIT007PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 5 sampling pump Component renown for frequent failure (OE) => E6 | EHM
1 | SRI |  |  |  | 1SRI001BX | 1SRI001PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component in service continuously. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 002/3 PO will take over. =>E6 | EHM
1 | SRI |  |  |  | 1SRI002BX | 1SRI002PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component 50% in service. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 003 PO will take over. =>E6 - Failure to function when required in standby will result in low SRI flow. However, this function is tested 6M =>E5, E6 | ELM
1 | SRI |  |  |  | 1SRI003BX | 1SRI003PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component 50% in service. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 002 PO will take over. =>E6 - Failure to function when required in standby will result in low SRI flow. However, this function is tested 6M =>E5, E6 | ELM
1 | SXS |  |  |  | 1LKE0101 | 1SXS005PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extended Spindle Pump. If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | ELM
1 | SXS |  |  |  | 1LKE0403 | 1SXS006PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extended Spindle Pump. Component is the lead pump. Higher No of starts. =>I2 If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | EHM
1 | TEP |  |  |  | 1LKJ0408 | 1TEP003PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Degasser recirculation and transfer pump. Component in service in all states except State 0. Component recirculates effluent through the degasser and transfers effluent to the intermediate storage tanks during State 5 Production. => E6 | ELM
1 | TEP |  |  |  | 1TEP001BX | 1TEP001PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transfer pump for 1TEP001BA. Component in service when head tank level reaches 20m3 first for tank recirculation and then to transfer effluent to the degasser during state 5. => E6 | ELM
2 | KRT |  |  |  | 2LMA027JA | 2KRT003AR | [10 empty] | B0904 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Circuit Breaker/Contactor Function: To isolate the equipment from the electrical supply, and provide protection to equipment. Failure analysis and classification: The Circuit Breaker/Contactor is a component of the switchboard. The maintenance requirements applicable to a switchboard includes the maintenance of its circuit breakers/contactors, therefore this circuit breaker/contactor is classified => E5,E6,I1,I4 | EHM | General description: Cabinet. Function: To accommodate equipment. Failure analysis and classification: 1 - All enclosures and cabinets designed to provide a controlled environment for the enclosed equipment are classified based on the effect of the total loss of the enclosure or cabinet. 2 - All enclosures and cabinets hosting only components which do not have individual trigrammes are classified based on the effect of the total loss of the enclosure or cabinet. 3 - All enclosures and cabinets hosting a combination of components with and without individual trigrammes are classified based on the effect of the total loss of the components which do not have individual trigrammes. 4 - All enclosures and cabinets hosting only components with individual trigrammes are classified as either RTM, or E6,A6 if this is necessary for environmental reasons. E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LCJ |  |  |  | 2LMJ001AR | 2LCJ001AR | [10 empty] | B0900 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Switchboard 220V AC prodtn & dist (erf). All cabinets are classified as RTF. | RTM | General description: 48 V Switchboard Function: Supplies 48 V to various equipment. Failure analysis and classification: Aggregating the classifications of the incoming and outgoing breakers produces a classification of => E5,E6,I1,I4 | EHM
2 | LTP |  |  |  | 2LTP001CR | 2RPE025PO | [10 empty] | B0916 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Temporary supply board. All cabinets are classified as RTF. | RTM | General Description: Submersible pump for 1RPE003CU. Component used infrequently during normal unit operation. => E6 | ELM
2 | KRT |  |  |  | 2KRT001TB | 2KRT002AR | [10 empty] | B0799 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | C4-loss of supply will result in all KRT auto actions occurring, including ETY isolation. C9-unavailability of KRT system until emergency power selected. E6-main power supply for KRT system. I1-continuously in service. I4-continuously energised. | CHM | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LNI |  |  |  | 2KSC001CR | 2RCP401EN | [10 empty] | B0301 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC001CR | 2RCP403EN | [10 empty] | B0302 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC001CR | 2RCP404EN | [10 empty] | B0303 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC001CR | 2RCP411EN | [10 empty] | B0304 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP406EN | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP407EN | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP408EN | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP409EN | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | LNI |  |  |  | 2KSC002CR | 2RCP410EN | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder in C/Room | EHM
2 | RCP |  |  |  | 2RCP010CR | 2RCP111RS | [10 empty] | B0307 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP112RS | [10 empty] | B0308 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP113RS | [10 empty] | B0309 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP121RS | [10 empty] | B0310 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP122RS | [10 empty] | B0311 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP123RS | [10 empty] | B0312 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP131RS | [10 empty] | B0313 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP132RS | [10 empty] | B0314 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP010CR | 2RCP133RS | [10 empty] | B0315 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP211RS | [10 empty] | B0322 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP212RS | [10 empty] | B0323 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP213RS | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP221RS | [10 empty] | B0325 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP222RS | [10 empty] | B0326 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP223RS | [10 empty] | B0327 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP231RS | [10 empty] | B0328 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP232RS | [10 empty] | B0329 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP020CR | 2RCP233RS | [10 empty] | B0330 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0334 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0335 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0336 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP030CR | 2RCP311RS | [10 empty] | B0343 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP312RS | [10 empty] | B0344 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP313RS | [10 empty] | B0345 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP321RS | [10 empty] | B0346 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP322RS | [10 empty] | B0347 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP323RS | [10 empty] | B0348 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP331RS | [10 empty] | B0349 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP332RS | [10 empty] | B0350 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP030CR | 2RCP333RS | [10 empty] | B0351 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0352 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0353 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0354 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0355 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0356 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0357 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP040CR | 2RCP411RS | [10 empty] | B0364 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP412RS | [10 empty] | B0365 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP413RS | [10 empty] | B0366 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP421RS | [10 empty] | B0367 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP422RS | [10 empty] | B0368 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP423RS | [10 empty] | B0369 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP431RS | [10 empty] | B0370 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP432RS | [10 empty] | B0371 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP040CR | 2RCP433RS | [10 empty] | B0372 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP511RS | [10 empty] | B0389 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP512RS | [10 empty] | B0390 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP513RS | [10 empty] | B0391 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP521RS | [10 empty] | B0392 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP522RS | [10 empty] | B0393 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP523RS | [10 empty] | B0394 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP531RS | [10 empty] | B0395 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP532RS | [10 empty] | B0396 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP533RS | [10 empty] | B0397 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP541RS | [10 empty] | B0398 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP542RS | [10 empty] | B0399 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP050CR | 2RCP543RS | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0403 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0404 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0405 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0406 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0407 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0408 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0409 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0410 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0411 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP060CR | 2RCP611RS | [10 empty] | B0467 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP612RS | [10 empty] | B0468 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP613RS | [10 empty] | B0469 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP621RS | [10 empty] | B0470 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP622RS | [10 empty] | B0471 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP623RS | [10 empty] | B0472 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP631RS | [10 empty] | B0473 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP632RS | [10 empty] | B0474 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP633RS | [10 empty] | B0475 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP641RS | [10 empty] | B0476 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP642RS | [10 empty] | B0477 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP060CR | 2RCP643RS | [10 empty] | B0478 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pressurizer heater. 001 RS heater board consist 3 heaters 011 RS, 012 RS and 013 RS 002 RS heater board consist 3 heaters 021 RS, 022 RS and 023 RS 003 RS heater board consist 3 heaters 031 RS, 032 RS and 033 RS 004 RS heater board consist 3 heaters 041 RS, 042 RS and 043 RS 005 RS1 heater board consist 2 heaters 051 RS and 052 RS 005 RS2 heater board consist 2 heaters 053 RS and 054 RS 006 RS1 heater board consist 2 heaters 061 RS and 062 RS 006 RS2 heater board consist 2 heaters 063 RS and 064 RS Failure of any of 3 phase heater (011 - 064 RS) wouldn’t be probably noticed by an operator => E6. (Just to maintain monitoring tasks of the bushing leak and overheating of terminals) The same shall apply to each individual heating element (111 - 643 RS) | EHS
2 | RCP |  |  |  | 2RCP003RS | 2RCP001RG | [10 empty] | B0480 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 3 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKA 103 JA Failure analysis and classification: -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RCP |  |  |  | 2RCP004RS | 2RCP002RG | [10 empty] | B0481 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380Vac switchboard for group 4 heaters Function: Supply to the three variable heaters on 001 BA - 3 phases supplied by LKB 207 JA Failure analysis and classification: Component in service during outage and power operation -- Failure to supply group 3 heaters classified as => S4,E6 --Component in service during outage and power operation => I1,I4 | SHM | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | RGL |  |  |  | 2RGL002AR | 2RGL012CR | [10 empty] | B0339 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL012CR | [10 empty] | B0340 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
2 | RGL |  |  |  | 2RGL002AR | 2RGL012CR | [10 empty] | B0341 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: The cabinet houses the three phase power connections for distribution to the RodPilot control cabinets. Complete failure of the cabinet will cause a power failure to the RodPilot that will result in a reactor trip. Complete failure of the cabinet is highly unlikely.=> C1,C2,C3,C4,C5,S4,E2,E6,I1,I4 | CHM | General description: Activation of alarm on failure with detailed information available on other panels. No influence on the operation of the plant | EHM
2 | SXS |  |  |  | 1SXS504AR | 2SXS506PO | [10 empty] | B0703 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet. Cabinets are classified as RTF. | RTM | General description: Submersible Pump. Failure of the pump would increase the risk of flooding the SEC galleries. => E5. | ELM
2 | ACO |  |  |  | 2ARE101CR | 2ACO005CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
2 | ACO |  |  |  | 2ACO005CR | 2ACO004CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
2 | ACO |  |  |  | 2ACO004CR | 2ACO006CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM
2 | ACO |  |  |  | 2ACO006CR | 2ACO007CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the isolation valve Upstream Downstream pump except S5 (SIR) -> E6 | EHM | TRICASTIN CLASSIFICATION USED => On 24/06/09 Modif classification into consistency with the pump -> E2 | EHM
2 | ACO |  |  |  | 2LKD0307 | 2ACO001RS | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater Function: 001 MO - prevents deterioration of electrical insulation when motor not in service. Failure Analysis and Classification: Component frequently in service and energised => I1,I4 Malfunction of the heater could lead to deterioration of the motor insulation => E2,E5 | EHM
2 | ACO |  |  |  | 2LKD0408 | 2ACO002RS | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater Function: 002 MO - prevents deterioration of electrical insulation when motor not in service. Failure Analysis and Classification: Component frequently in service and energised => I1,I4 Malfunction of the heater could lead to deterioration of the motor insulation => E2,E5 | EHM
2 | AGR |  |  |  | 2LKB0308 | 2AGR101CF | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Centrifuge - 001 BA oil tank. Component always in service. I1 Malfunction will result in loss of the oil purification function => E6 | EHM
2 | AGR |  |  |  | 2LKA0305 | 2AGR102CF | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Centrifuge - 002 BA oil tank. Component always in service. I1 Malfunction will result in loss of the oil purification function => E6 | EHM
2 | AGR |  |  |  | 2LKB0307 | 2AGR001ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - 001 BA - gases and oil vapour evacuation Component always in service. => I1 Depression of about 2.5kPa helps to degas the oil (potential loss of lubrication quality). Gases together with the oil vapour are evacuated via designated channel => E5 | EHM
2 | AGR |  |  |  | 2LKA0304 | 2AGR002ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - 002 BA - gases and oil vapour evacuation Component always in service. => I1 Depression of about 2.5kPa helps to degas the oil (potential loss of lubrication quality). Gases together with the oil vapour are evacuated via designated channel => E5 | EHM
2 | ATE |  |  |  | 2ATE102AR | 2ATE621MG | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
2 | ATE |  |  |  | 2ATE101AR | 2ATE801MG | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
2 | ATE |  |  |  | 2ATE011AR | 2ATE592SN | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE013AR | 2ATE621SN | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE013AR | 2ATE622SN | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE014AR | 2ATE711SN | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE014AR | 2ATE712SN | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE011AR | 2ATE591SN | [10 empty] | B0035 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate Polishing plant level sensors classified as E6. | ELM
2 | ATE |  |  |  | 2ATE202AR | 2ATE500MG | [10 empty] | B0052 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General Description: Condensate polishing plant physical chemical analysis transmitters are classified as E6. | ELM
2 | CAP |  |  |  | 2LKC0511 | 2CAP004VL | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolation valve. Function: Additional or quick make up of feedwater supply to condenser at a maximum rate of 100 t/h from SER system. Valve receives opening order from control room 001 TL on request. Failure analysis and classification: Fails to open/jammed closed : Failure when required (not continuously in service, and assuming 002 VL not available automatically, but manually). Manual actuation of valve still possible locally. Manual valve 003 VL still available for emergency make-up => E6. | ELM
2 | CET |  |  |  | 2LKD0308 | 2CET001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Exhaust fan - gland steam condenser 001 CS Function: Maintains shell side of the gland steam condenser at a negative pressure. Failure analysis and classification: Fan operation is controlled from 001 TL Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 Failure to function while unit on power will result in an increase of incondensable gases in main condenser, progressive decrease of the steam flow through the main turbine seals thus increase seals temperature, increase level in the barometric loop, etc. Turbine however could remain in operation for some time allowing for the fan to be repaired => E5 | EHM
2 | CEX |  |  |  | 2CEX005CR | 2CEX004CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Local control box of the isolation valve to the pump discharge power on TEM CEX On failure -> Unable to operate the valve electrically -> risk of having a pump CEX unavailable -> E6 | EHM
2 | CEX |  |  |  | 2LKF0204 | 2CEX001RS | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 001 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | CEX |  |  |  | 2LKF0203 | 2CEX002RS | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | CEX |  |  |  | 2LKF0202 | 2CEX003RS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 003 MO conservation. Malfunction of the heater could lead to deterioration of the insulation of the out-off-service electric motor => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | CFI |  |  |  | 2LKG0208 | 2CFI004CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
2 | CFI |  |  |  | 2LKG0201 | 2CFI001CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | CFI |  |  |  | 2LKG0403 | 2CFI001CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | CFI |  |  |  | 2LKG0202 | 2CFI002CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | CFI |  |  |  | 2LKG0404 | 2CFI002CR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | CFI |  |  |  | 2LKG0203 | 2CFI003CR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
2 | CFI |  |  |  | 2LKG0405 | 2CFI003CR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
2 | CFI |  |  |  | 2LKG0204 | 2CFI001PO | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2LKG0205 | 2CFI002PO | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2LKG0206 | 2CFI003PO | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2LKG0102 | 2CFI004PO | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2LKG0101 | 2CFI005PO | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2LKG0402 | 2CFI006PO | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | CFI |  |  |  | 2CFI015CR | 2CFI009MO | [10 empty] | B0043 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI015CR | 2CFI009MO | [10 empty] | B0044 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI015CR | 2CFI010MO | [10 empty] | B0045 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 001 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI017CR | 2CFI011MO | [10 empty] | B0046 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI017CR | 2CFI011MO | [10 empty] | B0047 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI017CR | 2CFI012MO | [10 empty] | B0048 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 002 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI019CR | 2CFI013MO | [10 empty] | B0049 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI019CR | 2CFI013MO | [10 empty] | B0050 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI019CR | 2CFI014MO | [10 empty] | B0051 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 003 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI021CR | 2CFI015MO | [10 empty] | B0052 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI021CR | 2CFI015MO | [10 empty] | B0053 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI021CR | 2CFI016MO | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 004 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI023CR | 2CFI017MO | [10 empty] | B0055 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 005 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI023CR | 2CFI017MO | [10 empty] | B0056 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 005 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI023CR | 2CFI018MO | [10 empty] | B0057 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 005 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI025CR | 2CFI019MO | [10 empty] | B0058 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI025CR | 2CFI019MO | [10 empty] | B0059 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - hoisting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI025CR | 2CFI020MO | [10 empty] | B0060 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric motor - pivoting gear on 006 DG Failure analysis and classification: Equipment only runs intermittently and then only for a few minutes. => E6, I2, I4 Component exposed to extremely corrosive environment. => A4, A6, A7 | EHS
2 | CFI |  |  |  | 2CFI003CR | 2CFI025MO | [10 empty] | B0100 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI003CR | 2CFI025MO | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI003CR | 2CFI025MO | [10 empty] | B0102 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM | General description: Electric 2 speed motor for 003 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6, I1 ,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI002CR | 2CFI024MO | [10 empty] | B0103 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI002CR | 2CFI024MO | [10 empty] | B0104 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI002CR | 2CFI024MO | [10 empty] | B0105 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 002 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. =>E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI001CR | 2CFI023MO | [10 empty] | B0106 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI001CR | 2CFI023MO | [10 empty] | B0107 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CFI |  |  |  | 2CFI001CR | 2CFI023MO | [10 empty] | B0108 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM | General description: Electric 2 speed motor for 001 TF Function: Rotate drum screen at required speed. Failure analysis and classification: Component always in service and energised when CRF pump pit is flooded. => E6,I1,I4 Component exposed to extremely corrosive environment. => A4, A6, A7 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHS
2 | CSI |  |  |  | 2LKG0212 | 2CSI001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 001 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0312 | 2CSI002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 001 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0311 | 2CSI003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 002 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0310 | 2CSI004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 002 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0309 | 2CSI005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train A hydraulic oil supply to 003 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0308 | 2CSI006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - hydraulic oil supply Function: Train B hydraulic oil supply to 003 VC actuator Failure analysis and classification: Pumps duty cycle is 50% with intermittent operation. -- Failure to function will require placing in service the standby pump 002 PO => E6 Component in corrosive environment. => A6 | ELS
2 | CSI |  |  |  | 2LKG0307 | 2CSI004VC | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 001 & 002 PO interconnection NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CSI |  |  |  | 2LKG0306 | 2CSI005VC | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 002 & 003 PO interconnection NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CTA |  |  |  | 2LKA0411 | 2CTA001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CTA |  |  |  | 2LKA0412 | 2CTA002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CTA |  |  |  | 2LKA0512 | 2CTA003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CTA |  |  |  | 2LKA0511 | 2CTA004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CTA |  |  |  | 2LKA0510 | 2CTA005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CTA |  |  |  | 2LKA0509 | 2CTA006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | CVI |  |  |  | 2LKB0107 | 2CVI001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKB0105 | 2CVI002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKC0107 | 2CVI003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKC0105 | 2CVI004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKB0211 | 2CVI005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKC0203 | 2CVI006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Vacuum pump. Function : To scavenge air and incondensible gases from condenser void applying a negative pressure simultaneously (< atmospheric pressure). Normally runs in parallel with at least one another vacuum pump. Failure Analysis and Classification: Component always in service and pressurised. => I1,I4 • Fails to pump, credit for pump redundancy => E6. | EHM
2 | CVI |  |  |  | 2LKC0504 | 2CVI007VA | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 001 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 001PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CVI |  |  |  | 2LKC0503 | 2CVI010VA | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 002 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 002PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CVI |  |  |  | 2LKC0502 | 2CVI013VA | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 003 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 003PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CVI |  |  |  | 2LKC0501 | 2CVI016VA | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 004 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 004 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CVI |  |  |  | 2LKC0505 | 2CVI046VA | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 006 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 006 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | CVI |  |  |  | 2LKC0506 | 2CVI043VA | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised isolating valve. Function : To provide isolation point to 005 PO vacuum pump air \ incondensible gas inlet from main condenser. Failure Analysis and Classification: • Valve unit (ROTORK actuator & valve) receives automatic signal to open after 10s once 005 PO has been put into service. • Fails to CLOSE/jammed OPEN; - Handwheel still available locally. Pump to remain I/S if no isolation possible => E6. • Fails to OPEN/jammed CLOSED; - Loss of function, inability to prime and set vacuum pump 001 PO in service. Credit for vacuum pump redundancy => E6. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLE0304 | 2DEG201CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
2 | DEG |  |  |  | 2LLD0312 | 2DEG101CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
2 | DEG |  |  |  | 2LLJ0312 | 2DEG301CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Group feeding box. Failure: risk of loss of the group ---> E6 | EHM
2 | DEG |  |  |  | 2LLE0107 | 2DEG006PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLD0107 | 2DEG005PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLA0107 | 2DEG008PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLJ0107 | 2DEG007PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chilled water distribution pump Malfunctioning pump can be substituted by the stand-by one (2 pumps in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLC0310 | 2DEG205VD | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 201 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLB0306 | 2DEG105VD | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 101 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLE0303 | 2DEG405VD | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 401 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DEG |  |  |  | 2LLD0311 | 2DEG305VD | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air operated control valve - 301 CS flow control valve Component failure will render chiller inoperable. Malfunctioning chiller can be substituted by the stand-by one (3 chillers in standby) => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | DVC |  |  |  | 2LKF0412 | 2DVC010RS | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Iodine filters conditioning electric heater Purpose - to condition iodine filters while not in service - => E6 | ELM
2 | DVG |  |  |  | 2LKE0304 | 2DVG001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: ELECTRICAL AIR HEATER - DVG 003 ZV AND DVG 004 ZV discharge line Component fails to generate heat => E6 | ELM
2 | DVI |  |  |  | 2LKS0204 | 2DVI001RS | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air heater - fresh air intake duct Maintains air temperature in RRI rooms above 15°C - failure will result in alarm =>E6 (no frost in SA conditions ) | ELM
2 | DVI |  |  |  | 2LLC0308 | 2DVI001ZV | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train A Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
2 | DVI |  |  |  | 2LLD0310 | 2DVI002ZV | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train B Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
2 | DVI |  |  |  | 2LLC0309 | 2DVI003ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train A Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
2 | DVI |  |  |  | 2LLB0607 | 2DVI004ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Supply fan - train B Service duty - 50% Failure could result in RRI pumps area temperature to rise too high for comfort => E6 | ELM
2 | DVK |  |  |  | 2LKF0408 | 2DVK005RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - conditioning heater in the iodine filter 001PI | ELM
2 | DVK |  |  |  | 2LKF0105 | 2DVK001ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air supply fan - odd line SRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
2 | DVK |  |  |  | 2LKD0203 | 2DVK002ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fresh air supply fan - even line SRSM requirement - 1RO shutting down test from manual actuation SRSM requirement - 1RO auto shutting down test from SI signal SRSM requirement - 1RO auto shutting down test from Hi activity KRT 013 or 014 MA OPS PT DVK 40 OPS PT KRT 189 - failure of this PT prior to unload/reload will cause delay => NO C2 | ELM
2 | DVL |  |  |  | 2LKH0302 | 2DVL102RS | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - SAP compressor room. | ELM
2 | DVL |  |  |  | 2LKH0301 | 2DVL103RS | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater - SAP compressor room. | ELM
2 | DVL |  |  |  | 2LLA0401 | 2DVL101ZV | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - stairs U2 supply Failure can be mitigated with creating draft by opening doors 0 & 24 m Lvl => E6 | EHM
2 | DVL |  |  |  | 2LLA0402 | 2DVL102ZV | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - stairs U2 exhaust. Failure can be mitigated with creating draft by opening doors 0 & 24 m Lvl => E6 | EHM
2 | DVM |  |  |  | 2DVM002AR | 2DVM003PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply to 002 EV. Circulates water that cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM002AR | 2DVM004PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply to 002EV. Circulates water that cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM003AR | 2DVM005PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply to 003EV. Circulates water that cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM003AR | 2DVM006PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Pump - recirculating supply to 003EV. Circulates water that cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM002AR | 2DVM003ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - supply air. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
2 | DVM |  |  |  | 2DVM002AR | 2DVM004ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - supply air. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
2 | DVM |  |  |  | 2DVM003AR | 2DVM005ZV | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - supply air. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
2 | DVM |  |  |  | 2DVM003AR | 2DVM006ZV | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - supply air. Main ventilation fan for the turbine hall => E6. Cycled frequently =>I2. | EHM
2 | DVM |  |  |  | 2DVM002AR | 2DVM010ZV | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - exhaust air. Main ventilation fan for the ATE plant => E6. In continuous operation =>I1. | EHM
2 | DVM |  |  |  | 2DVM003AR | 2DVM015ZV | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM006CR | 2DVM016ZV | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM006CR | 2DVM017ZV | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
2 | DVM |  |  |  | 2DVM002AR | 2DVM011ZV | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Fan - exhaust air. Cools equipment that is vital for production => E6. | ELM
2 | DVN |  |  |  | 2LKJ0401 | 2DVN036ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Smoke extraction fan. Component used to extract smoke from the electrical rooms after a fire. => E6 | ELM
2 | DVS |  |  |  | 2LLA0408 | 2DVS005ZV | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from EAS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
2 | DVS |  |  |  | 2LLB0411 | 2DVS006ZV | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from EAS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
2 | DVS |  |  |  | 2LLA0409 | 2DVS007ZV | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from RIS 001 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
2 | DVS |  |  |  | 2LLB0412 | 2DVS008ZV | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air exhaust fan from RIS 002 PO room SRSM requirement - 2 monthly start/stop test (during RPR testing) - verify correct operation => NO C3 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => E6 SRSM requirement - 1RO verify exhaust fans auto stop when air supply fan shut down => NO C2 | ELM
2 | DVW |  |  |  | 2LKH0401 | 2DVW003RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Iodine filter conditioning electric heather SRSM requirement - 1RO verify correct operation of the fan (and associated logic) NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | EPP |  |  |  | 2LLB0609 | 2EPP101AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. | ELM
2 | EPP |  |  |  | 2LLB0611 | 2EPP201AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet EPP101AR classified as Econonic - E6. Economic to carry out preventative maintenance, rather than, to allow equipment to degrade and repair upon failure. A4, A6- Exposed to harsh marine environment conditions, therefore excessive corrosion observed on cabinets. | ELS
2 | GEV |  |  |  | 2LKF0506 | 2GEV004AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Local cabinet - 001 TS, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELS
2 | GEV |  |  |  | 2LKE0105 | 2GEV001CR | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | GEV |  |  |  | 2LKE0105 | 2GEV001CR | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED | EHM
2 | GEV |  |  |  | 2LKH0411 | 2GEV002CR | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | TRICASTIN CLASSIFICATION USED Same classification as the associated cabinets (041AR, 042AR, 043AR) | EHM
2 | GGR |  |  |  | 2LKF0512 | 2GGR012PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - jacking oil pumps suction booster Function: Jacking oil suction booster pump when 002, 003, or 004 PO are not available. (ie in outage) Failure analysis and classification: Pump required in service when turbine alignment and coupling work is being performed. Also if suction of jacking oil pumps drops bellow 140 kPa ( 002 , 003 and 004 PO would have to fail) during turbine rundown. => E6 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | ELM
2 | GGR |  |  |  | 2LKH0409 | 2GGR022ZV | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan - cooling 02 0 MO (turning gear motor) Fan require in service to maintain motor temp below 75 degrees C => E5 (unit 2 70 degrees C) Component in continuous service => I1 Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO C2 | EHM
2 | GHE |  |  |  | 2LKH0410 | 2GHE001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 3 80V Main seal oil pump taking suction from 001 DZ vacuum tank. -Provides a small amount of detrained oil back to the seal oil supply to the generator seal oil circuit, while the bulk is returned to 001 DZ on second spraying rack. - Failure resulting from blocked inlet strainer/filter in vacuum tank 001 DZ, reduction in defence of depth, requires emergency seal oil pump 003 PO to operate => E6,I1,I4 . Failure to function correctly should need an outage repair time < 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => NO S7 | EHM
2 | GHE |  |  |  | 2LKE0303 | 2GHE005PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 380V rotary positive displacement vacuum pump. -Provides removal of oil entrained air from vacuum tank 001 DZ, keeping the tank under a constant vacuum between 70-80 mm Hg. Oil supplied from GGR system. -If 220V DC emergency pump in service 004 PO, then can only run pump for 1 hr. -Loss of function to extract from 001 DZ vacuum tank, and maintain de-aeration => No immediate effect to system. H2 purity must be monitored => E6,I1, I4. | EHM
2 | GST |  |  |  | 2LKF0510 | 2GST001RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater Function: To heat water in 001 BA Failure analysis and classification: Used exclusively during outage. No credit for 002 RS (both heaters require). - Failure to function ¿ during outage to assist vacuum drying of the alternator stator bars before GST draining => E5. ¿ used during outage to prevent condensation inside alternator (mini outage) => E5 - Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E5 | ELM
2 | GST |  |  |  | 2LKF0509 | 2GST002RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater Function: To heat water in 001 BA Failure analysis and classification: Used exclusively during outage. No credit for 001 RS (both heaters require). - Failure to function ¿ during outage to assist vacuum drying of the alternator stator bars before GST draining => E5. ¿ used during outage to prevent condensation inside alternator (mini outage) => E5 - Failure to function correctly may require outage repair time < 36hrs based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => E5 | ELM
2 | GSY |  |  |  | 2GSY003AR | 2GSY101JS | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
2 | GSY |  |  |  | 2GSY003AR | 2GSY201JS | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
2 | GSY |  |  |  | 2GSY003AR | 2GSY301JS | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To house specified GSY equipment (with trigrammes). Failure analysis and classification: Cabinets housing specified GSY equipment (with trigrammes) are classified => RTM | RTM | General description: Isolator Function: To isolate the equipment from the electrical supply. Failure analysis and classification: The isolator is a FEG sub-component of the FEG functional location. The maintenance requirements applicable to the FEG includes the maintenance of its isolator(s), therefore this isolator is classified => E5,E6,I1,I4 | EHM
2 | LGA |  |  |  | 2LGA001TR | 2LGA001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
2 | LGA |  |  |  | 2LGA001TR | 2LGA001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
2 | LGD |  |  |  | 2LGD001TR | 2LGD001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
2 | LGD |  |  |  | 2LGD001TR | 2LGD001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 | CHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
2 | LHP |  |  |  | 2LLG0207 | 2LHP001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
2 | LHP |  |  |  | 2LLG0208 | 2LHP002CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
2 | LHP |  |  |  | 2LLG0206 | 2LHP003RE | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: LHJ 002 AR (AVR) Anti-condensation heater Function: Prevent moisture and associated corrosion products in AVR cabinet. Failure analysis and classification: Failure of the heater does not impact EDG operability directly. Longer term degradation of the AVR components occur as a result of moisture and formation of corrosion products. | EHM
2 | LHP |  |  |  | 2LLG0209 | 2LHP003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHP |  |  |  | 2LLG0210 | 2LHP004ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHP |  |  |  | 2LLG0211 | 2LHP005ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHP |  |  |  | 2LLG0212 | 2LHP006ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHQ |  |  |  | 2LLW0207 | 2LHQ001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
2 | LHQ |  |  |  | 2LLW0208 | 2LHQ002CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
2 | LHQ |  |  |  | 2LLW0206 | 2LHQ003RE | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: LHJ 002 AR (AVR) Anti-condensation heater Function: Prevent moisture and associated corrosion products in AVR cabinet. Failure analysis and classification: Failure of the heater does not impact EDG operability directly. Longer term degradation of the AVR components occur as a result of moisture and formation of corrosion products. | EHM
2 | LHQ |  |  |  | 2LLW0209 | 2LHQ003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHQ |  |  |  | 2LLW0210 | 2LHQ004ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHQ |  |  |  | 2LLW0211 | 2LHQ005ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LHQ |  |  |  | 2LLW0212 | 2LHQ006ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
2 | LLN |  |  |  | 2LLA0101 | 2LLN001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | LLO |  |  |  | 2LLB0103 | 2LLO001TR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transformer - 380V AC / 220V AC. Non-essential supply, 220 V AC => E6 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | LMA |  |  |  | 2LMA120CR | 2CFI001MO | [10 empty] | B0121 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA120CR | 2CFI002MO | [10 empty] | B0122 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA120CR | 2CFI003MO | [10 empty] | B0123 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA120CR | 2CFI004MO | [10 empty] | B0124 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA120CR | 2CFI005MO | [10 empty] | B0125 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA120CR | 2CFI006MO | [10 empty] | B0126 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Washwater pump motor for the drum and rake screens, supplied from CRF 001 PO discharge - parallel to 002 PO. Function: Supplies wash water. Failure analysis and classification: Pumps duty cycle is about 50%. Two pumps normally in service and pressurised, one on each CRF pump in service. -- Failure to function will require placing in service the standby pump from CRF 001 PO => E6 -- Failure to function as a standby-pump will require two pumps to be placed in service from the another CRF pump in service until repair effected => E6 Component in extremely corrosive environment. => A6 | ELS
2 | LMA |  |  |  | 2LMA130CR | 2CFI001CR | [10 empty] | B0131 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | LMA |  |  |  | 2LMA130CR | 2CFI002CR | [10 empty] | B0132 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Connection box of SN and SP monitoring grids DeltaP TFs and leakiness: default risk isolated ACL -> E6 | EHM
2 | LMA |  |  |  | 2LMA130CR | 2CFI003CR | [10 empty] | B0133 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
2 | LMA |  |  |  | 2LMA130CR | 2CFI004CR | [10 empty] | B0134 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED Same classification as the sensors (SN, SP) -> Consideration of the worst case, namely: On Failure -> risk of not identifying the clogging drum -> Risk degradation pump FIU. | EHM
2 | LMA |  |  |  | 2LMA140CR | 2CSI004VC | [10 empty] | B0141 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 001 & 002 PO interconnection NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | LMA |  |  |  | 2LMA140CR | 2CSI005VC | [10 empty] | B0142 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated isolation valve - 002 & 003 PO interconnection NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELM
2 | LMA |  |  |  | 2LMA160CR | 2KRT001AR | [10 empty] | B0161 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LMA |  |  |  | 2LMA160CR | 2KRT002AR | [10 empty] | B0162 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LMA |  |  |  | 2LMA180CR | 2GEV001AR | [10 empty] | B0181 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 001 TP, marshalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropriate. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELS
2 | LMA |  |  |  | 2LMA180CR | 2GEV002AR | [10 empty] | B0182 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 002 TP, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELS
2 | LMA |  |  |  | 2LMA180CR | 2GEV003AR | [10 empty] | B0183 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 003 TP, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELS
2 | LMA |  |  |  | 2LMA180CR | 2GEV004AR | [10 empty] | B0187 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution box. All cabinets are classified as RTF. | RTM | General description: Local cabinet - 001 TS, mashalling kiosk hosting transformer control equipment - located outside All cabinets are classified as RTF, however, due to its location, E6 would be appropiate. NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | ELS
2 | LNE |  |  |  | 2LNE0213 | 2KRT001AR | [10 empty] | B0039 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LNE |  |  |  | 2LNE0214 | 2KRT002AR | [10 empty] | B0040 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
2 | LNE |  |  |  | 2LNE0331 | 2RCP001RG | [10 empty] | B0053 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Controller Function: Controlling operation of the 003 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 3 (031,32 or 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 3 (031,32 or 033 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 3 (031,32 and 033 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | LNE |  |  |  | 2LNE0332 | 2RCP002RG | [10 empty] | B0054 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Controller Function: Controlling operation of the 004 RS (PRZR variable heaters) according to the signal from 014 MP Failure analysis and classification: Component continuously in service and energized => I1,i4. -- Failure to control individual heater within the group 4 (041,42 or 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control individual heater within the group 4 (041,42 or 043 RS - permanently energized) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - not energizing) will have minor effect on PRZR pressure control => E6 -- Failure to control whole group 4 (041,42 and 043 RS - permanently energized) will have minor (noticeable?) effect on PRZR pressure control => E6 | ELM
2 | LNE |  |  |  | 2LNE0312 | 2KKO601AR | [10 empty] | B0062 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder for generator active and reactive power. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. | EHM
2 | LNE |  |  |  | 2LNE0313 | 2KKO801AR | [10 empty] | B0063 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Recorder for generator active and reactive power. Function: To display and record the selected variable parameter data. Failure analysis and classification: Recorder is in continuous service and is continuously energised => I1,I4. Recorder failure is monitored by the operator and has no direct effect on plant operation. Failure to display the current value of the parameter could impair operator fault finding and decision making => E6. | EHM
2 | LNE |  |  |  | B0708 | 2RPN005AR | [10 empty] | B0085 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: The cabinet houses the audio speaker 403HP that gives an audible sound representing the Source Range count rate. The loss of the audio sound has no consequence. Tasks associated with High Flux Monitoring are required as a nuclear safety contingency and are to be downloaded with the outage scope. These support activity tasks are required when welding is done in the Reactor building.=>E6 | ELM
2 | LNE |  |  |  | 2LNE260CR | 2REN010MG | [10 empty] | B0261 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for SG Sodium content. Component used to monitor for Sodium in any of the 3 SG s. Component generates a signal to 1REN090EN. Component generates a signal to threshold relay s 1REN545XU1/527XU1/527XU2/545XU2/529XU1/531XU1. => E6 Plant shutdown within 1HR when in Zone 5 is only required after a manual sample for confirmation => No C3 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN041MG | [10 empty] | B0262 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG001DE. Component generates 1REN054AA Ionic leakage 001DE. Component generates 1REN060EC on KIT This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN042MG | [10 empty] | B0263 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG002DE. Component generates 1REN054AA Ionic leakage 001DE. Component generates 1REN065EC on KIT This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN043MG | [10 empty] | B0264 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG003DE. Component generates 1REN056AA Ionic leakage 001DE. Component generates 1REN069EC on KIT This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN044MG | [10 empty] | B0265 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for conductivity downstream 1APG004DE. Component generates 1REN056AA Ionic leakage 001DE. Component generates 1REN070EC on KIT This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN071MG | [10 empty] | B0266 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG1. Component generates 1REN052EC PH Low. Component generates 1REN053EC PH Hi. Component generates alarm 1REN051AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN003EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN072MG | [10 empty] | B0267 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG2. Component generates 1REN057EC PH Low. Component generates 1REN058EC PH Hi. Component generates alarm 1REN052AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN004EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN073MG | [10 empty] | B0268 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for PH on SG3. Component generates 1REN063EC PH Low. Component generates 1REN064EC PH Hi. Component generates alarm 1REN053AA. Component generates signal for 1REN070EN. Component generates KIT signal 1REN005EU. Component warns the operator of a possible SG tube leak. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN081MG | [10 empty] | B0269 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG1. Component generates signal for 1REN080EN. Component generates KIT signal 1REN006EU. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN082MG | [10 empty] | B0270 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG2. Component generates signal for 1REN080EN. Component generates KIT signal 1REN007EU. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN083MG | [10 empty] | B0271 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for Conductivity on SG3. Component generates signal for 1REN080EN. Component generates KIT signal 1REN008EU. => E6 This component is always in service. => I1 | EHM
2 | LNE |  |  |  | 2LNE260CR | 2REN010MG | [10 empty] | B0272 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1APG. All cabinets are classified as RTF. | RTM | General description: Analyser for SG Sodium content. Component used to monitor for Sodium in any of the 3 SG s. Component generates a signal to 1REN090EN. Component generates a signal to threshold relay s 1REN545XU1/527XU1/527XU2/545XU2/529XU1/531XU1. => E6 Plant shutdown within 1HR when in Zone 5 is only required after a manual sample for confirmation => No C3 NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | EHM
2 | LNE |  |  |  | 2LNE320CR | 2ARE002YP | [10 empty] | B0324 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet -1SAS supply to 1ARE. All cabinets are classified as RTF. | RTM | General description:Pressure test point on 002GV supply. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
2 | LNE |  |  |  | 2LNE330CR | 2ARE005YD | [10 empty] | B0331 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 2SAS supply to 2ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 001GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
2 | LNE |  |  |  | 2LNE330CR | 2ARE006YD | [10 empty] | B0332 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 2SAS supply to 2ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 002GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
2 | LNE |  |  |  | 2LNE330CR | 2ARE007YD | [10 empty] | B0333 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 2SAS supply to 2ARE. All cabinets are classified as RTF. | RTM | General description: Flow rate measurement test point on 001GV supply line. High pressure (> 7 MPa) test points are classified as E6,A2. | ELS
2 | LNE |  |  |  | 2LNE400CR | 2CRF001SN | [10 empty] | B0401 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 001SP and 001SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 001 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level HIGH: -- Failure to provide correct signal to the logic to generate KIT alarm 001 EC "001MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 004 AA "001MO COOLER HUMIDITY FAULT" => E6 | EHS
2 | LNE |  |  |  | 2LNE400CR | 2CRF001SP | [10 empty] | B0402 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 001SP and 001SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 001 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 001 AA "001PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 005 EC "01PO-LWR BRG BLOCK pressure" => E5 | EHS
2 | LNE |  |  |  | 2LNE410CR | 2CRF005SN | [10 empty] | B0411 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 003SP and 005SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 002 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level Hi: -- Failure to provide correct signal to the logic to generate KIT alarm 007 EC "002MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 005 AA "002MO COOLER HUMIDITY FAULT" => E6 | EHS
2 | LNE |  |  |  | 2LNE410CR | 2CRF003SP | [10 empty] | B0412 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 003SP and 005SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 002 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 002 AA "002PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 011 EC "02PO-LWR BRG BLOCK pressure" => E5 | EHS
2 | LNE |  |  |  | 2LNE420CR | 2CRF009SN | [10 empty] | B0421 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 005SP and 009SN. All cabinets are classified as RTF. | RTM | General description: Level switch Function: 003 MO - liquid detection (cooler leak or condensation) Failure analysis and classification: Component always in service, energized and in corrosive environment => I1,I4,A6 At level Hi: -- Failure to provide correct signal to the logic to generate KIT alarm 013 EC "003MO HUMIDITY DET" => E6 -- Failure to provide correct signal to the logic to generate KSC alarm 005 AA "003MO COOLER HUMIDITY FAULT" => E6 | EHS
2 | LNE |  |  |  | 2LNE420CR | 2CRF005SP | [10 empty] | B0422 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet - supply to 1CRF 005SP and 009SN. All cabinets are classified as RTF. | RTM | General description: Pressure switch Function: 003 PO oil pressure in lower gearing block. Failure analysis and classification: Component permanently in service, energized and in corrosive environment => I1,I4,A6 At pressure LOW: -- Failure to provide correct signal to the logic to generate KSC alarm 003 AA "003PO OIL DEFECT" => E5 -- Failure to provide correct signal to the logic to generate KIT alarm 017 EC "03PO-LWR BRG BLOCK pressure" => E5 | EHS
2 | PTR |  |  |  | 2LKL0204 | 2PTR003PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Skimming pump of the SFP. Function: Removes debris from the surface of the SFP. Failure analysis: Component fails to function.=E6 Component only required to be placed in service when skimming is necessary to remove surface impurities. Pump currently remains in service continuously. => I1,I4 | EHM
2 | RCP |  |  |  | E0103 | 2RCP008RS | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
2 | RCP |  |  |  | E0103 | 2RCP009RS | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 002 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
2 | RCP |  |  |  | E0103 | 2RCP010RS | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 003 MO stator heater Possible high cost of repair of the motor if heater malfunction during pump outage => E1, E2, E5 | ELM
2 | RCP |  |  |  | 2LLD0105 | 2RCP106RS | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS1) - supplied from LLD 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
2 | RCP |  |  |  | 2LLC0107 | 2RCP105RS | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS1) - supplied from LLC 107 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
2 | RCP |  |  |  | 2LLD0105 | 2RCP106RS | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 6 (006 RS1) - supplied from LLD 105 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 060 CR common to both sub-groups 006 RS1 & 006 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
2 | RCP |  |  |  | 2LLC0107 | 2RCP105RS | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - 2 pressurizer ON-OFF heaters - sub-group 5 (005 RS1) - supplied from LLC 107 JA Loss of the entire subgroup comprising 6 individual heating element is very unlikely. More probable would be failure of the terminal box 050 CR common to both sub-groups 005 RS1 & 005 RS2 making entire 105 RS inoperable. This will result in loss of heating efficiency of the pressurizer => E6 | ELM
2 | RPE |  |  |  | A0103 | 2RPE001PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extraction pump for 1RPE001BA. Component used mostly during RO when draining or filling operations are in progress. Component loss during RO will be subsituted by the alternative drains pump => E6 | ELM
2 | RPE |  |  |  | A0103 | 2RPE002PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extraction pump for 1RPE001BA. Component used mostly during RO when draining or filling operations are in progress. Component loss during RO will be subsituted by the alternative drains pump => E6 | ELM
2 | RPE |  |  |  | 2LKH0504 | 2RPE029PO | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Submersible pump for 1RPE004PS. Component used frequently during normal unit operation. => E6 This component has frequent cycles of operation. => I2 | EHM
2 | SEC |  |  |  | 2LLE0611 | 2SEC011AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet. Function: Hosting instrumentation for racking screen 001 FI Failure analysis and classification: Cabinets with equipment identified by the trigramme are classified as RTM. (For corrosive service condition E6,A6 shall apply). | ELS
2 | SEC |  |  |  | 2LLB0502 | 2SEC012AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet. Function: Hosting instrumentation for racking screen 002 FI Failure analysis and classification: Cabinets with equipment identified by the trigramme are classified as RTM. (For corrosive service condition E6,A6 shall apply). | ELS
2 | SEC |  |  |  | 2LLE0711 | 2SEC005PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train A Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
2 | SEC |  |  |  | 2LLB0602 | 2SEC006PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train B Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
2 | SEC |  |  |  | 2LLE0710 | 2SEC007PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train A Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
2 | SEC |  |  |  | 2LLB0603 | 2SEC008PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump Function: Washwater supply - Train B Failure analysis and classification: Pump duty cycle of approx. 50% => NO I1 Installed in corrosive environment => A6 -- Failure to pump will require repair (NO S4) => E6. With the consideration that there is another (redundant) pump available on the same train and "other means" to backwash intake filters. | ELS
2 | SIT |  |  |  | 2LKF0201 | 2SIT003PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 1 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SIT |  |  |  | 2LKF0406 | 2SIT004PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 2 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SIT |  |  |  | 2LKF0410 | 2SIT005PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 3 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SIT |  |  |  | 2LKH0104 | 2SIT006PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 4 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SIT |  |  |  | 2LKH0103 | 2SIT007PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 5 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SIT |  |  |  | 2LKH0102 | 2SIT008PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pump - CEX condenser water box 6 sampling pump Component renown for frequent failure (OE) => E6 | EHM
2 | SRI |  |  |  | 2SRI001BX | 2SRI001PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component in service continuously. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 002/3 PO will take over. =>E6 | EHM
2 | SRI |  |  |  | 2SRI002BX | 2SRI002PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component 50% in service. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 003 PO will take over. =>E6 - Failure to function when required in standby will result in low SRI flow. However, this function is tested 6M =>E5, E6 | ELM
2 | SRI |  |  |  | 2SRI003BX | 2SRI003PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Horizontal centrifugal type pump Failure analysis and classification: 2 out 3 100% parallel pumps need to run at any one given time. 001 PO runs continuously, 002/3 PO run on a 6M regime. Component 50% in service. Failure can have the following consequences: - Failure to function during normal operation will result in no loss of system. The standby pump 002 PO will take over. =>E6 - Failure to function when required in standby will result in low SRI flow. However, this function is tested 6M =>E5, E6 | ELM
2 | SXS |  |  |  | 2LKE0101 | 2SXS005PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extended Spindle Pump. If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | ELM
2 | SXS |  |  |  | 2LKE0403 | 2SXS006PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Extended Spindle Pump. Component is the lead pump. Higher No of starts. =>I2 If the bushes of extended spindle pumps are not renewed before excessive wear occurs, shaft shear can occur which in turn can cause server damage to the impeller. =>E2, E6. | EHM
2 | TEP |  |  |  | 2LKJ0408 | 2TEP004PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Degasser recirculation and transfer pump. Component in service in all states except State 0. Component recirculates effluent through the degasser and transfers effluent to the intermediate storage tanks during State 5 Production. => E6 | ELM
2 | TEP |  |  |  | 2TEP002BX | 2TEP002PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Transfer pump for 2TEP008BA. Component in service when head tank level reaches 20m3 first for tank recirculation and then to transfer effluent to the degasser during state 5. => E6 | ELM
6 | DNL |  |  |  | 6LKL001AR | 6DNL001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNL |  |  |  | 6LKL001AR | 6DNL002CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNL |  |  |  | 6LKL001AR | 6DNL003CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN004AR | 6DNN001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN002CR | 6DNN002CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN004AR | 6DNN003CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN004CR | 6DNN004CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN004AR | 6DNN005CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DNN |  |  |  | 6LKN006CR | 6DNN006CR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DSN |  |  |  | 6LKN004CR | 6DSN001CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local cabinet. All cabinets are classified as RTF. | RTM | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
6 | DWC |  |  |  | 6LKC001CR | 6DWC402AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWC |  |  |  | 6LKC001CR | 6DWC401AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE601AR | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE602AR | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE603AR | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 6LKN002AR | 6DWE603AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Distribution cabinet. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWE |  |  |  | 0LKO322AR | 6DWE605AR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA322AR | 6DWI302AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA523AR | 6DWI309AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA423AR | 6DWI313AR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA423AR | 6DWI313AR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA423AR | 6DWI313AR | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKA423AR | 6DWI313AR | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKE001AR | 6DWI301AR | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kv/380 minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKF001AR | 6DWI304AR | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 6,6kV/380V minisubs. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6LKB001AR | 6DWI306AR | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: 380 volt main distribution board. All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6DWI313AR | 6DWI303AR | [10 empty] | B0389 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWI |  |  |  | 6DWI304AR | 6DWI305AR | [10 empty] | B0400 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWL |  |  |  | 6LKL001AR | 6DWL501AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWL |  |  |  | 6LKL001AR | 6DWL502AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWL |  |  |  | 6LKL001AR | 6DWL503AR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Main distribution board (LLW). All cabinets are classified as RTF. | RTM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | DWP |  |  |  | 6DWP101AR | 6DWP102AR | [10 empty] | B0101 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM | General description: Cabinet Function: To contain unspecified equipment supplying ventilation and/or air conditioning equipment Failure analysis and classification: All small panels supplying ventilation and/or air conditioning equipment are classified => E6 | ELM
6 | LKN |  |  |  | 6LKN010CR | 6LKN001CO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cold room chiller compressor. It would not be economic to let this component run to failure => E6. | EHM
6 | LKN |  |  |  | 6LKN011CR | 6LKN002CO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Cold room chiller compressor. It would not be economic to let this component run to failure => E6. | EHM
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL | [10 empty] | B0503 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC700CR | 6SSC001DL | [10 empty] | B0506 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL | [10 empty] | B0515 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC700CR | 6SSC001DL | [10 empty] | B0517 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL | [10 empty] | B0518 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL | [10 empty] | B0535 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL | [10 empty] | B0536 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL | [10 empty] | B0543 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL | [10 empty] | B0544 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSC001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL | [10 empty] | B0503 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD700CR | 6SSD001DL | [10 empty] | B0506 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL | [10 empty] | B0513 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD700CR | 6SSD001DL | [10 empty] | B0515 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL | [10 empty] | B0525 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL | [10 empty] | B0535 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL | [10 empty] | B0536 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL | [10 empty] | B0543 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL | [10 empty] | B0544 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Inverter. Function: To convert a DC supply to an AC supply. Failure analysis and classification: Component permanently energised and in service => I1,I4 Review of the SSC feeder diagram indicates that loss of SSD001DL will result in loss of supplies to Security related equipment => E6 | EHM
9 | CTE |  |  |  | 1LKH0209 | 9CTE001PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Main seawater supply pump to 9CTE. Component in service 50% Component failure would require the other Units pump to be placed in service. => E6 | ELM
9 | CTE |  |  |  | 2LKH0209 | 9CTE002PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Main seawater supply pump to 9CTE. Component in service 50% Component failure would require the other Units pump to be placed in service. => E6 | ELM
9 | CTE |  |  |  | 9LKP0201 | 9CTE004PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Continuous Chlorination supply pump. Component always in service when selected. => I1 Component operates in corrosive environment. => A6 Component failure will require the last pump to be placed in service. => E6 | EHM
9 | CTE |  |  |  | 9LKP0609 | 9CTE005PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Continuous Chlorination supply pump. Component always in service when selected. => I1 Component operates in corrosive environment. => A6 Component failure will require the last pump to be placed in service. => E6 | EHM
9 | CTE |  |  |  | 9LKP0404 | 9CTE008PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Acid wash supply pump. Component placed in service for acid wash on a weekly basis. => I2 Component failure would require repair before acid washing of electrolysers could be done. => E6 | EHM
9 | CTE |  |  |  | 9LKP0405 | 9CTE009PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Caustic soda supply pump. Component placed in service for acid wash on a weekly basis. => I2 Component failure would require repair before acid washing of electrolysers could be done. => E6 | EHM
9 | CTE |  |  |  | 9LKP0406 | 9CTE001RD | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Rectifier and control cabinet. Component always in service and energised when line is in service. => I1,I4 Component used to rectify the AC supply and control the DC current to the electrolysers. => E6 | EHM
9 | CTE |  |  |  | 9LKP0407 | 9CTE002RD | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Rectifier and control cabinet. Component always in service and energised when line is in service. => I1,I4 Component used to rectify the AC supply and control the DC current to the electrolysers. => E6 | EHM
9 | CTE |  |  |  | 9LKP0107 | 9CTE001ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air circulation fan for Hydrogen purging. Component used to purge the gas separation tanks and is continuously in service when the line is in service. => I1 Component operates in an extremely corrosive environment. => A6 Component failure would result in a low air flow in the CTE line and the current will be tripped to the electrolysers until the standby fan is place in service. => E6 | EHS
9 | CTE |  |  |  | 9LKP0105 | 9CTE002ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air circulation fan for Hydrogen purging. Component used to purge the gas separation tanks and is continuously in service when the line is in service. => I1 Component operates in an extremely corrosive environment. => A6 Component failure would result in a low air flow in the CTE line and the current will be tripped to the electrolysers until the standby fan is place in service. => E6 | EHS
9 | CTE |  |  |  | 9LKP0103 | 9CTE003ZV | [10 empty] | B0018 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Air circulation fan for Hydrogen purging. Component used to purge the gas separation tanks and is continuously in service when the line is in service. => I1 Component operates in an extremely corrosive environment. => A6 Component failure would result in a low air flow in the CTE line and the current will be tripped to the electrolysers until the standby fan is place in service. => E6 | EHS
9 | DNZ |  |  |  | 9DNZM01CR | 9RCP001PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Reactor Coolant Pump Motor Function: Spare Failure analysis and classification: Spare, will be tested prior to use => E6 | ELM
9 | DSN |  |  |  | 9DSN001AR | 9DSNA01CR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | DSN |  |  |  | 9DSN001AR | 9DSNB02CR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | DSN |  |  |  | 9DSN001AR | 9DSNC03CR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | DSN |  |  |  | 9DSN001AR | 9DSND04CR | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | DSN |  |  |  | 9DSN001AR | 9DSNE05CR | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | GRV |  |  |  | 9LKZ0201 | 9GRV001RE | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heat exchanger heating carbon dioxide | ELM
9 | KRT |  |  |  | 9KRT566CR | 9DSNB02CR | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Box (Small panel) Function: To contain unspecified equipment supplying 220 V power and/or lighting Failure analysis and classification: All small panels supplying 220 V power and/or lighting are classified => E6 | ELM
9 | LGE |  |  |  | 9LGE001TR | 9LGE001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
9 | LGE |  |  |  | 9LGE001TR | 9LGE001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
9 | LGF |  |  |  | 9LGF001TR | 9LGF001AR | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
9 | LGF |  |  |  | 9LGF001TR | 9LGF001AR | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Earthing transformer. Function : To provide signal to earth fault alarm and limit earth current to approximately 1 0 A. Failure analysis and classification: COMMENT: The associated earthing resistor in adjacent enclosure 001 AR is seen as part of the earthing transformer. -- Failure of the transformer to limit the earth fault current of approximately 10 A could/will result in severe damage in the event of an earth fault on 6.6 Kev circuit => S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure of the transformer to provide correct signal (loss of signal) to the protection circuit will result in loss of alarm 002 AA "FEEDER OR BOARD FAULT"=> S1,E2 ,E5 ,I1,I4 ,A6,A7. -- Failure to function correctly may require outage repair time > 36 hours based on Maintenance’s repair time, Ops PTW implementation (isolation and preparation of plant for repair), and other supporting activities => C2 Classification updated - not SPV. Following system engineering review of SPVs at the beginning of 2016, this component screened out, i.e. are no longer SPVs. | SHS | General description: Enclosure. Function : To house the earthing resistor. Failure analysis and classification: COMMENT: The earthing resistor is seen as part of the earthing transformer. Enclosures and cabinets hosting components with individual trigrammes and exposed to corrosive environments are classified as E6,A6. | ELS
9 | LHS |  |  |  | 9LLV0204 | 9LHS001CO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
9 | LHS |  |  |  | 9LLV0205 | 9LHS002CO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Compressor Function: Compressed Air Supply Failure analysis and classification: -- Simultaneous failure of both 001/2 CO will result in inability to charge 001/2/3 BA for EDG startup and operation. However, simultaneous failure is unlikely and 001/2 CO could be lined up to both 001/2 BA. => E2, E6 | ELM
9 | LHS |  |  |  | 9LLV0311 | 9LHS003RE | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: LHJ 002 AR (AVR) Anti-condensation heater Function: Prevent moisture and associated corrosion products in AVR cabinet. Failure analysis and classification: Failure of the heater does not impact EDG operability directly. Longer term degradation of the AVR components occur as a result of moisture and formation of corrosion products. | EHM
9 | LHS |  |  |  | 9LLV0308 | 9LHS003ZV | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
9 | LHS |  |  |  | 9LLV0307 | 9LHS004ZV | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
9 | LHS |  |  |  | 9LLV0306 | 9LHS005ZV | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
9 | LHS |  |  |  | 9LLV0305 | 9LHS006ZV | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Fan Function: Radiator forced ventilation cooling Failure analysis and classification: -- Fan failure will result in increased heat load to engine. 1 out of 4 fans may be out of service and full operability will be maintained. => E2, E3, E4, E5, E6, A4 | ELS
9 | LHS |  |  |  | 9LLV0207 | 9LHS001RS | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Electric heater Function: To maintain the room temperature within specification Failure analysis and classification: Component permanently in energised and in service => I1,I4 Malfunction of the heater could lead to deterioration of the protected equipment => E5,E6 | EHM
9 | LKI |  |  |  | 9LKI002CR | 9RCP001PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Reactor Coolant Pump Motor Function: Spare Failure analysis and classification: Spare, will be tested prior to use => E6 | ELM
9 | LLM |  |  |  | 9LLM001CR | 9LLM001TR | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Lighting control box from unit 1. All cabinets are classified as RTF. | RTM | TRICASTIN CLASSIFICATION USED 380V power circuit breaker of the subarray On failure: - Loss of power subarray -> E6 | EHM
9 | LNF |  |  |  | 9LNF0352 | 9KRT501AR | [10 empty] | B0019 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | E5-failure of fans will lead to degradation of all the RDUs in the cabinet and subsequently channel operation. I1-fans continuously in service. I4-fans continuously energised. | EHM
9 | REA |  |  |  | 9REA005CR | 9REA003RS | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - batching tank 005 BA Component extensively used during unit outage. Failure of one (out of five) heater would not create any substantial delays => NO C2 | ELM
9 | REA |  |  |  | 9REA005CR | 9REA004RS | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - batching tank 005 BA Component extensively used during unit outage. Failure of one (out of five) heater would not create any substantial delays => NO C2 | ELM
9 | REA |  |  |  | 9REA005CR | 9REA005RS | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - batching tank 005 BA Component extensively used during unit outage. Failure of one (out of five) heater would not create any substantial delays => NO C2 | ELM
9 | REA |  |  |  | 9REA005CR | 9REA006RS | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - batching tank 005 BA Component extensively used during unit outage. Failure of one (out of five) heater would not create any substantial delays => NO C2 | ELM
9 | REA |  |  |  | 9REA005CR | 9REA007RS | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Heater - batching tank 005 BA Component extensively used during unit outage. Failure of one (out of five) heater would not create any substantial delays => NO C2 | ELM
9 | SDA |  |  |  | 9LKN0409 | 9SDA001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pre treated water supply pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 9LKN0408 | 9SDA002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pre treated water supply pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 9LKN0407 | 9SDA003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Pre treated water supply pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 9LKN0103 | 9SDA004PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Filter bed demineralised water pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 9LKN0105 | 9SDA005PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Filter bed demineralised water pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 9LKN0107 | 9SDA006PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Filter bed demineralised water pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDA |  |  |  | 1ATE102AR | 9SDA391MG | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDA |  |  |  | 1ATE102AR | 9SDA301MG | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDA |  |  |  | 1ATE102AR | 9SDA162MG | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDA |  |  |  | 1ATE102AR | 9SER001VD | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Motorised supply isolation valve from SDA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | SDA |  |  |  | 1ATE102AR | 9SER002VD | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Motorised supply isolation valve from SDA. Component opens to supply demineralised water to 9SER002BA. => E6,I2 | EHM
9 | SDA |  |  |  | 1ATE102AR | 9SER005VD | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Motorised outlet isolation valve from 9SER001BA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | SDA |  |  |  | 1ATE102AR | 9SER006VD | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF | RTM | General description: Motorised outlet isolation valve from 9SER002BA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | SDX |  |  |  | 9LKN0410 | 9SDX151AG | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Agitating mechanism. Minimal classification of E6. | ELM
9 | SDX |  |  |  | 9LKN0411 | 9SDX152AG | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Agitating mechanism. Minimal classification of E6. | ELM
9 | SDX |  |  |  | 9LKN0205 | 9SDX001CO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: E6 - minimum E6 classification on compressor. I2 - cyclic operation of component. | EHM
9 | SDX |  |  |  | 9LKN0207 | 9SDX002CO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: E6 - minimum E6 classification on compressor. I2 - cyclic operation of component. | EHM
9 | SDX |  |  |  | 9LKN0209 | 9SDX003CO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: E6 - minimum E6 classification on compressor. I2 - cyclic operation of component. | EHM
9 | SDX |  |  |  | 9LKN0510 | 9SDX001PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Caustic soda supply pump to 003 BA and 004 BA. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0509 | 9SDX002PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Caustic soda supply pump to 003 BA and 004 BA. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0508 | 9SDX003PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Ammonia supply pump to 005 BA and 006 BA. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0507 | 9SDX004PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Ammonia supply pump to 005 BA and 006 BA. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0506 | 9SDX005PO | [10 empty] | B0013 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Diluted NH3 supply pump to ATE system. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0505 | 9SDX006PO | [10 empty] | B0014 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Diluted NH3 supply pump to ATE system. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0504 | 9SDX007PO | [10 empty] | B0015 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Diluted NH3 supply pump to ATE system. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0503 | 9SDX008PO | [10 empty] | B0016 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Diluted NH3 supply pump to SDA system. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0502 | 9SDX009PO | [10 empty] | B0017 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Diluted NH3 supply pump to SDA system. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0707 | 9SDX017PO | [10 empty] | B0020 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 019 BA pit effluent lifting discharge pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0705 | 9SDX018PO | [10 empty] | B0021 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 019 BA pit effluent lifting discharge pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0703 | 9SDX019PO | [10 empty] | B0022 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 020 BA pit effluent lifting discharge pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0701 | 9SDX020PO | [10 empty] | B0023 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 020 BA pit effluent lifting discharge pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0412 | 9SDX021PO | [10 empty] | B0024 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Active physical effluent pit no 5 pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0602 | 9SDX022PO | [10 empty] | B0025 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Active physical effluent pit no 6 pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9SDX101BN | 9SDX035RS | [10 empty] | B0026 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Minimum E6 for trace heating elements on tank. I2-cyclic operation of heaters to keep temperature between 20-25deg c. | EHM
9 | SDX |  |  |  | 9SDX101BN | 9SDX036RS | [10 empty] | B0027 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Minimum E6 for trace heating elements on tank. I2-cyclic operation of heaters to keep temperature between 20-25deg c. | EHM
9 | SDX |  |  |  | 9SDX102BN | 9SDX037RS | [10 empty] | B0028 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Minimum E6 for trace heating elements on tank. I2-cyclic operation of heaters to keep temperature between 20-25deg c. | EHM
9 | SDX |  |  |  | 9SDX102BN | 9SDX038RS | [10 empty] | B0029 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Minimum E6 for trace heating elements on tank. I2-cyclic operation of heaters to keep temperature between 20-25deg c. | EHM
9 | SDX |  |  |  | 9SDX002CR | 9SDX091RS | [10 empty] | B0030 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Immersion heater. Minimum classification of E6 | ELM
9 | SDX |  |  |  | 9SDX002CR | 9SDX092RS | [10 empty] | B0031 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Immersion heater. Minimum classification of E6 | ELM
9 | SDX |  |  |  | 9SDX002CR | 9SDX093RS | [10 empty] | B0032 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Immersion heater. Minimum classification of E6 | ELM
9 | SDX |  |  |  | 9LKN0309 | 9SDX025PO | [10 empty] | B0033 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 019 BA immersed mixing pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0310 | 9SDX026PO | [10 empty] | B0034 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 020 BA immersed mixing pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9SDX001AR | 9SDX231MG | [10 empty] | B0043 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets and alarm panels classified as RTF. | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDX |  |  |  | 9SDX001AR | 9SDX232MG | [10 empty] | B0044 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets and alarm panels classified as RTF. | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDX |  |  |  | 2ATE101AR | 9SDX013PO | [10 empty] | B0045 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General description: 012 BA neutralisation pit pH metering pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9SDX001AR | 9SDX233MG | [10 empty] | B0047 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets and alarm panels classified as RTF. | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDX |  |  |  | 9SDX001AR | 9SDX234MG | [10 empty] | B0048 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets and alarm panels classified as RTF. | RTM | General description: Minimum classification of E6 for chemical analysers. | ELM
9 | SDX |  |  |  | 9SDA201AR | 9SDX024PO | [10 empty] | B0049 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets classified as RTF. | RTM | General description: pH metering pit 012 BA pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9SDA201AR | 9SDX023PO | [10 empty] | B0050 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: All cabinets classified as RTF. | RTM | General description: pH metering pit 019 BA pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 2ATE101AR | 9SDX014PO | [10 empty] | B0052 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Cabinet Function: Failure analysis and classification: All enclosures and cabinets hosting components with individual trigrammes (and not A6) are classifies as RTF NOTE: This text, and the associated Classification and Hidden status, have been copied directly from the corresponding Unit 1 trigramme. They must be validated for applicability. | RTM | General description: 013 BA neutralisation pit pH metering pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0308 | 9SDX027PO | [10 empty] | B0055 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: SDA aluminium sulphate injection pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0307 | 9SDX028PO | [10 empty] | B0056 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: SDA aluminium sulphate injection pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0306 | 9SDX029PO | [10 empty] | B0057 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: SDA aluminium sulphate injection pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0305 | 9SDX030PO | [10 empty] | B0058 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: SDA aluminium sulphate injection pump. Classified as E6, I1 due to service conditions. | EHM
9 | SDX |  |  |  | 9LKN0304 | 9SDX153AG | [10 empty] | B0059 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Agitating mechanism. Minimal classification of E6. | ELM
9 | SDX |  |  |  | 9LKN0303 | 9SDX154AG | [10 empty] | B0060 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Agitating mechanism. Minimal classification of E6. | ELM
9 | SED |  |  |  | 9LKK0405 | 9SED008VD | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Filling isolation valve of 9SED001BA. Component used for filling of 9SED001BA. | ELM
9 | SEP |  |  |  | 9LKK0512 | 9SEP606VE | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated valve. Motor operated valves in the SEP system are classified E6. | ELM
9 | SEP |  |  |  | 9LKK0511 | 9SEP607VE | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated valve. Motor operated valves in the SEP system are classified E6. | ELM
9 | SEP |  |  |  | 9LKK0510 | 9SEP611VE | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated valve. Motor operated valves in the SEP system are classified E6. | ELM
9 | SEP |  |  |  | 9LKK0509 | 9SEP613VE | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor operated valve. Motor operated valves in the SEP system are classified E6. | ELM
9 | SER |  |  |  | 9LKN0101 | 9SER001PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Demineralised water transfer pump. Component used to supply and pressurise the SER supply header. => E6 One of the three pumps is always in service, therefore <50% in service. | ELM
9 | SER |  |  |  | 9LKN0201 | 9SER002PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Demineralised water transfer pump. Component used to supply and pressurise the SER supply header. => E6 One of the three pumps is always in service, therefore <50% in service. | ELM
9 | SER |  |  |  | 9LKN0203 | 9SER003PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Demineralised water transfer pump. Component used to supply and pressurise the SER supply header. => E6 One of the three pumps is always in service, therefore <50% in service. | ELM
9 | SER |  |  |  | 9LKN0605 | 9SER001VD | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised supply isolation valve from SDA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | SER |  |  |  | 9LKN0606 | 9SER002VD | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised supply isolation valve from SDA. Component opens to supply demineralised water to 9SER002BA. => E6,I2 | EHM
9 | SER |  |  |  | 9LKN0607 | 9SER005VD | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised outlet isolation valve from 9SER001BA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | SER |  |  |  | 9LKN0608 | 9SER006VD | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motorised outlet isolation valve from 9SER002BA. Component opens to supply demineralised water to 9SER001BA. => E6,I2 | EHM
9 | TEP |  |  |  | 9LKI0407 | 9TEP005PO | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEP001EV water feed pump. Component used to feed the water to the evaporator loop. Component failure makes the evaporator unavailable for treatment of waste water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0408 | 9TEP006PO | [10 empty] | B0002 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEP002EV water feed pump. Component used to feed the water to the evaporator loop. Component failure makes the evaporator unavailable for treatment of waste water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0103 | 9TEP007PO | [10 empty] | B0003 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Intermediate storage tank recirculation and transfer pump 9TEU007PO. Component used for recirculation and transfer operations. Component is the only pump for the intermediate storage tanks. => E6 | ELM
9 | TEP |  |  |  | 9LKI0409 | 9TEP008PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEP001EV loop concentrate recirculation pump. Component used to recirculate the concentrate in the evaporator loop. Component failure makes the evaporator unavailable for treatment of borated water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0412 | 9TEP009PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEP001EV loop concentrate recirculation pump. Component used to recirculate the concentrate in the evaporator loop. Component failure makes the evaporator unavailable for treatment of borated water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0411 | 9TEP010PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEU002EV distillate pump. Component used to drain distillate during production. Component failure makes the evaporator unavailable for treatment of waste water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0410 | 9TEP011PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TEU001EV distillate pump. Component used to drain distillate during production. Component failure makes the evaporator unavailable for treatment of waste water. => E6 | ELM
9 | TEP |  |  |  | 9LKI0512 | 9TEP012PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Distillate recirculation and transfer pump 9TEP012PO. Component used for recirculation and transfer operations. Component is the only pump for the distillate tank. => E6 | ELM
9 | TEP |  |  |  | 9LKI0511 | 9TEP013PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Distillate recirculation and transfer pump 9TEP013PO. Component used for recirculation and transfer operations. Component is the only pump for the distillate tank. => E6 | ELM
9 | TEP |  |  |  | 9LKI0510 | 9TEP014PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Concentrate recirculation and transfer pump 9TEP014PO. Component used for recirculation and transfer operations. Component is the only pump for the distillate tank. => E6 | ELM
9 | TES |  |  |  | 9LKI0509 | 9TES001AG | [10 empty] | B0001 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: 9TES001BA stirrer. Component always in service. => I1 Component used to mix the concentrate in 9TES001BA for homogenisation. => E6 | EHM
9 | TES |  |  |  | 9LKI0501 | 9TES004MO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Motor Function: To open/close door B Failure analysis and classification: Koeberg maintenance records and international experience supports having Planned Maintenance (PM) activities at regular intervals =>E6 | ELM
9 | TEU |  |  |  | 9LKI0711 | 9TEU001PO | [10 empty] | B0004 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Process drains pump 9TEU001PO. Component used frequently for recirculation and draining operations. => I2 Component is the only pump for the process drains tanks. 9TEU018BA available as backup if the pump should fail. => E6 | EHM
9 | TEU |  |  |  | 9LKI0710 | 9TEU002PO | [10 empty] | B0005 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Floor drains pump 9TEU002PO. Component used frequently for recirculation and draining operations. => I2 Component is the only pump for the floor drains tanks. 9TEU018BA available as backup if the pump should fail. => E6 | EHM
9 | TEU |  |  |  | 9LKI0709 | 9TEU003PO | [10 empty] | B0006 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Service drains pump 9TEU003PO. Component used frequently for recirculation and draining operations. => I2 Component is the only pump for the service drains tanks. 9TEU018BA available as backup if the pump should fail. => E6 | EHM
9 | TEU |  |  |  | 9LKI0708 | 9TEU004PO | [10 empty] | B0007 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Chemical drains pump 9TEU004PO. Component used frequently for recirculation and draining operations. => I2 Component is the only pump for the chemical drains tanks. 9TEU018BA available as backup if the pump should fail. => E6 | EHM
9 | TEU |  |  |  | 9LKI0707 | 9TEU008PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Distillate pump 9TEU008PO. Component used frequently for recirculation and draining operations. => I2 Component is the only pump for the distillate tanks. => E6 | EHM
9 | TEU |  |  |  | 9LKI0703 | 9TEU014PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic |  |  | General description: Additional storage tank transfer/recirculation pump 9TEU014PO. Component used infrequently for recirculation and draining operations. Component used for transfer of water from 9TEU018BA when the tank is filled. Failure of this pump will mean that 9TEU 018 BA cannot be recirculated for sampling to make a decision on processing. =>E5, E6 | ELM
9 | XCA |  |  |  | 9XCA004AR | 9XPA001PO | [10 empty] | B0008 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local control ctrl cabinet for XCA & XPA. | RTM | General description: Fuel oil pump. Component exposed to the elements. => A6. Component used to deliver fuel oil to the burners when the boilers are in service. => E6. | ELS
9 | XCA |  |  |  | 9XCA004AR | 9XPA002PO | [10 empty] | B0009 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local control ctrl cabinet for XCA & XPA. | RTM | General description: Fuel oil pump. Component exposed to the elements. => A6. Component used to deliver fuel oil to the burners when the boilers are in service. => E6. | ELS
9 | XCA |  |  |  | 9XCA004AR | 9XPA003PO | [10 empty] | B0010 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local control ctrl cabinet for XCA & XPA. | RTM | General description: Fuel oil pump. Component exposed to the elements. => A6. Component used to deliver fuel oil to the burners when the boilers are in service. => E6. | ELS
9 | XCA |  |  |  | 9XCA004AR | 9XCA010PO | [10 empty] | B0011 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local control ctrl cabinet for XCA & XPA. | RTM | General description: Pmp N2H4 dsg to blr water supply. | ELM
9 | XCA |  |  |  | 9XCA004AR | 9XCA010PO | [10 empty] | B0012 |  |  | Yes |  |  |  | FDR | 4 RO |  |  | 4 RO |  | V&T |  |  |  | Economic | General description: Local control ctrl cabinet for XCA & XPA. | RTM | General description: Pmp N2H4 dsg to blr water supply. | ELM

## CAMP I&C (hidden)
UNIT | SYSTEM | ER CLASS | CATEG | RGNB | EQUIPMENT MARK_FROM | EQUIPMENT MARK_TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | CORE | Dimensions (mm2) | Cable Size & Core | CBTYP | CABLE NUMBER | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) / FDR TEST | FREQ. | START DATE | TYPE OF TEST (ONLINE) | FREQ. | START DATE | V&T INSPECTIONS | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | SAMPLE SELCTED FOR V&T | SAMPLE SELCTED FOR IR | SAMPLE SELCTED FOR VLF-TD | SAMPLE SELCTED FOR PD | MANUFACTURER | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE

## KIT (hidden)
UNIT | SYSTEM | ER CLASS | CATEG | RGNB | EQUIPMENT_FROM | EQUIPMENT_TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | Cores | Dimensions (mm2) | Cable Size & Core | CBTYP | Cable_No | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) / FDR TEST | FREQ. | START DATE | TYPE OF TEST (ONLINE) | FREQ. | START DATE | V&T INSPECTIONS | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0001 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0002 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0005 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0006 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0009 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0010 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0013 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0014 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0017 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0018 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0021 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0022 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0025 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0026 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0029 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0030 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0033 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0034 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0037 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0038 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0041 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0042 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0045 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0046 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0049 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0050 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0053 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0054 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0057 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0058 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0061 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0062 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0065 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0066 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0069 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0070 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0073 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0074 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0077 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0078 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0081 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0082 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0085 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0086 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0089 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0090 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0093 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0094 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0097 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0098 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0101 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0102 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0105 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0106 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0109 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0113 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 12 | 0 |  |  | 64 | 0.3 |  | NA | 1KITE0114 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR | [6 empty] | 64 | 0.3 | 64c x 0,22mm2 |  | 1KITE0114 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0117 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR | [8 empty] | 32 x 0,22 mm2 |  | 1KITE0118 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  |  |  | 50 |  |  |  |  | 32 x 0.22 | NA | 1KITE0118 | SITE RUN | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0121 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0125 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0129 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0133 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0137 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0141 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0145 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0149 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0153 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0157 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0161 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0165 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0169 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0173 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0177 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0181 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0185 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0189 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0193 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0197 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0201 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0205 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0209 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0213 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0217 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0221 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0225 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0229 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0233 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0237 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0241 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0245 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0249 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0253 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0257 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0261 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0265 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0269 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0273 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0277 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0281 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0285 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0289 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0293 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0297 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0301 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0305 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0309 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0313 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0317 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR | [8 empty] | 32 x 0,22 mm2 |  | 1KITE0318 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0321 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0325 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0329 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0333 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0337 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0341 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0345 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0349 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0353 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0357 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0361 |  | In
1 | KIT |  |  |  | 1KIT365BN | 1KIT105AR |  |  |  | 8 |  |  |  |  | 64x0.35 | NA | 1KITE0365 | IND | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  |  |  | 20 |  |  |  |  | 32 x 0.22 | NA | 1KITE0381 | SITE RUN | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0401 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0403 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0405 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0407 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0409 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0411 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0413 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0415 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0417 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0801 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0802 |  | In
1 | KIT |  |  |  | 1KIT004CQ | 1KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0805 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0806 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0810 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0814 |  | In
1 | KIT |  |  |  | 1KIT002CQ | 1KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0818 |  | In
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0821 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT003CQ |  | 0 | 0 | 1 |  |  | 3 | 1.5 |  | NA | 1KITE0823 |  | Out
1 | KIT |  |  |  | 1KIT003CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0825 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0833 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0837 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0841 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0845 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0849 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0853 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0857 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0861 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0865 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0869 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0873 |  | In
1 | KIT |  |  |  | 1KIT001CQ | 1KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0877 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0921 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0925 |  | In
1 | KIT |  |  |  | 1KIT005CQ | 1KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0927 |  | In
1 | KIT |  |  |  | 1KIT005CQ | 1KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0928 |  | In
1 | KIT |  |  |  | 1KIT005CQ | 1KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0929 |  | In
1 | KIT | [13 empty] | Spare |  | 1KITE0930 |  | Out
1 | KIT |  |  |  | 1KIT005CQ | 1KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0934 |  | In
1 | KIT |  |  |  | 1KIT005CQ | 1KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 1KITE0935 |  | In
1 | KIT |  |  |  | 1KIT401AR | 1KIT401CR | [8 empty] | 1p Fibre optic cable-Armoured |  | 1KITF0401 |  | In
1 | KIT |  |  |  | 1KIT401CR | 1KIT401AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0401 | IND - IND | In
1 | KIT |  |  |  | 1KIT401CR | 1KIT402CR | [8 empty] | 1p Fibre optic cable-Armoured |  | 1KITF0402 |  | In
1 | KIT |  |  |  | 1KIT401AR | 1KIT402CR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0402 | IND | In
1 | KIT |  |  |  | 1KIT401CR | 1KIT407CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0403 |  | In
1 | KIT |  |  |  | 1KIT401CR | 1KIT405CR |  |  |  | 190 |  |  |  |  | FIBRE 8 Core | A | 1KITF0403 | IND,1L5JT2A,1L4JT2A,IND,9L4LB2A,IND,9L3831A,9N3411A,9N3B11A,9N2021A-F,IND,9N2051C,IND | In
1 | KIT |  |  |  | 1KIT402CR | 1KIT408CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0404 |  | In
1 | KIT |  |  |  | 1KIT402CR | 1KIT406CR |  |  |  | 150 |  |  |  |  | FIBRE 8 Core | A | 1KITF0404 | IND,9L5LB2A,9L4LB2A,9L3LB2A,IND,9L3831A,9N3411A,9N3B11A,9N2B11A,9N2021A-F,IND,9N2051C,IND | In
1 | KIT |  |  |  | 1GRH002AR | 1KIT403CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0405 |  | In
1 | KIT |  |  |  | 1GRH002AR | 1KIT404CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0406 |  | In
1 | KIT |  |  |  | 1GRH002AR | 1KIT403CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0407 |  | In
1 | KIT |  |  |  | 1GRH002AR | 1KIT404CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0408 |  | In
1 | KIT |  |  |  | 1KIT403CR | 9KIT411CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0409 |  | In
1 | KIT |  |  |  | 1KIT405CR | 1KIT406AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 1KITF0409 | IND | In
1 | KIT |  |  |  | 1KIT404CR | 9KIT412CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0410 |  | In
1 | KIT |  |  |  | 1KIT406CR | 1KIT406AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0410 | IND | In
1 | KIT |  |  |  | 1GEX001AR | 1KIT405CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0411 |  | In
1 | KIT |  |  |  | 9KIT491CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0411 | IND-IND | In
1 | KIT |  |  |  | 1GEX001AR | 1KIT406CR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0412 |  | In
1 | KIT |  |  |  | 1KIT405CR | 1KIT409CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0413 |  | In
1 | KIT |  |  |  | 9KIT491CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0413 | IND | In
1 | KIT |  |  |  | 1KIT406CR | 1KIT410AR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0414 |  | In
1 | KIT |  |  |  | 1KIT407CR | 1KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0415 |  | In
1 | KIT |  |  |  | 1KIT407CR | 1KIT402AR |  |  |  | 45 |  |  |  |  | FIBRE | NA | 1KITF0415 | IND-IND | In
1 | KIT |  |  |  | 1KIT408CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0416 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT010AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 1KITF0416 | IND-IND | In
1 | KIT |  |  |  | 9KIT411CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0417 |  | Out
1 | KIT |  |  |  | 1KIT407CR | 1KIT402AR |  |  |  | 45 |  |  |  |  | FIBRE | NA | 1KITF0417 | IND-IND | In
1 | KIT |  |  |  | 9KIT412CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0418 |  | Out
1 | KIT |  |  |  | 1KIT402AR | 1KIT010AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 1KITF0418 | IND-IND | In
1 | KIT |  |  |  | 9KIT411CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0419 |  | Out
1 | KIT |  |  |  | 1KIT407CR | 1KIT406AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0419 | IND-IND | In
1 | KIT |  |  |  | 9KIT412CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0420 |  | Out
1 | KIT |  |  |  | 1KIT406AR | 1KIT010AR |  |  |  | 35 |  |  |  |  | FIBRE | NA | 1KITF0420 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0421 |  | Out
1 | KIT |  |  |  | 1KIT407CR | 1KIT406AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 1KITF0421 | IND | In
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0422 |  | Out
1 | KIT |  |  |  | 1KIT406AR | 1KIT010AR |  |  |  | 35 |  |  |  |  | FIBRE | NA | 1KITF0422 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0423 |  | Out
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0424 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0424 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0425 |  | Out
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0426 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0426 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0427 |  | Out
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0428 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0428 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0429 |  | Out
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0430 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0430 | IND-IND | In
1 | KIT |  |  |  | 9KIT413CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0431 |  | Out
1 | KIT |  |  |  | 9KIT414CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0432 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0432 | IND-IND | In
1 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0433 |  | Out
1 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0434 |  | Out
1 | KIT |  |  |  | 1KIT408CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0434 | IND-IND | In
1 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0435 |  | Out
1 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0436 |  | Out
1 | KIT |  |  |  | 1KIT410CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0436 | IND-IND | In
1 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0437 |  | Out
1 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0438 |  | Out
1 | KIT |  |  |  | 1KIT410CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0438 | IND-IND | In
1 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0439 |  | Out
1 | KIT |  |  |  | 1KIT409CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0439 | IND-IND | In
1 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0440 |  | Out
1 | KIT |  |  |  | 1KIT410CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0440 | IND-IND | In
1 | KIT |  |  |  | 9KIT417CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0441 |  | Out
1 | KIT |  |  |  | 1KIT409CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0441 | IND-IND | In
1 | KIT |  |  |  | 9KIT418CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0442 |  | Out
1 | KIT |  |  |  | 1KIT410CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0442 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0443 |  | In
1 | KIT |  |  |  | 1KIT411CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0443 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0444 |  | In
1 | KIT |  |  |  | 1KIT412CR | 1KIT010AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0444 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0445 |  | In
1 | KIT |  |  |  | 1KIT406AR | 1KIT407AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0445 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0446 |  | In
1 | KIT |  |  |  | 1KIT406AR | 1KIT407AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0446 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0447 |  | In
1 | KIT |  |  |  | 1KIT403AR | 1KIT402AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 1KITF0447 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0448 |  | In
1 | KIT |  |  |  | 1KIT403AR | 1KIT402AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 1KITF0448 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0449 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT404AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0449 | IND-IND | In
1 | KIT |  |  |  | 9KIT010AR | 1KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0450 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT404AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0450 | IND-IND | In
1 | KIT |  |  |  | 1KIT406AR | 1KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0451 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT405AR |  |  |  | 38 |  |  |  |  | FIBRE | NA | 1KITF0451 | IND-IND | In
1 | KIT |  |  |  | 1KIT406AR | 1KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0452 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT405AR |  |  |  | 38 |  |  |  |  | FIBRE | NA | 1KITF0452 | IND-IND | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0453 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0454 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0455 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0456 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0457 |  | In
1 | KIT |  |  |  | 1KIT402AR | 1KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0458 |  | In
1 | KIT |  |  |  | 1KIT411CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0459 |  | In
1 | KIT |  |  |  | 1KIT412CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0460 |  | In
1 | KIT |  |  |  | 1KIT411CR | 1KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0461 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT408AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 1KITF0461 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0462 |  | In
1 | KIT |  |  |  | 1KIT414CR | 1KIT408AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0462 | IND | In
1 | KIT |  |  |  | 1KIT411CR | 1KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0463 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT408AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 1KITF0463 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0464 |  | In
1 | KIT |  |  |  | 1KIT414CR | 1KIT408AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0464 | IND | In
1 | KIT |  |  |  | 1KIT411CR | 1KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0465 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT412AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 1KITF0465 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0466 |  | In
1 | KIT |  |  |  | 1KIT414CR | KIT412AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 1KITF0466 | IND | In
1 | KIT |  |  |  | 1KIT411CR | 1KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0467 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT412AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 1KITF0467 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0468 |  | In
1 | KIT |  |  |  | 1KIT414CR | 1KIT412AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 1KITF0468 | IND | In
1 | KIT |  |  |  | 1KIT411CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0469 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1GSE002AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0469 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0470 |  | In
1 | KIT |  |  |  | 1KIT414CR | 1GSE002AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0470 | IND | In
1 | KIT |  |  |  | 1KIT411CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0471 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1GSE002AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0471 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0472 |  | In
1 | KIT |  |  |  | 1KIT414CR | 1GSE002AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0472 | IND | In
1 | KIT |  |  |  | 1KIT409CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0473 |  | In
1 | KIT |  |  |  | 1KIT412AR | 1GSE001AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0473 | IND | In
1 | KIT |  |  |  | 1KIT410CR | 1GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0474 |  | In
1 | KIT |  |  |  | 1KIT412AR | 1GSE001AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0474 | IND | In
1 | KIT |  |  |  | 1KIT413CR | 1GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0475 |  | In
1 | KIT |  |  |  | 1KIT415CR | 1GSE001AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0475 | IND | In
1 | KIT |  |  |  | 1KIT414CR | 1GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0476 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0477 |  | In
1 | KIT |  |  |  | 1KIT412AR | 1KIT411AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0477 | IND | In
1 | KIT |  |  |  | 1KIT414CR | 1GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0478 |  | In
1 | KIT |  |  |  | 1KIT412AR | 1KIT411AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 1KITF0478 | IND | In
1 | KIT |  |  |  | 1KIT413CR | 1GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0479 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT410AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0479 | IND | In
1 | KIT |  |  |  | 1KIT412AR | 1KIT411AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0480 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT410AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0480 | IND | In
1 | KIT |  |  |  | 1KIT412AR | 1KIT411AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0481 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT409AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0481 | IND-IND | In
1 | KIT |  |  |  | 1KIT412AR | 1KIT411AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0482 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT409AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0482 | IND-IND | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0483 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0484 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0485 |  | In
1 | KIT |  |  |  | 1KIT415CR | 1GSE001AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0485 | IND | In
1 | KIT |  |  |  | 1KIT408AR | 1KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0486 |  | In
1 | KIT |  |  |  | 1KIT411CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0487 |  | In
1 | KIT |  |  |  | 1KIT415CR | 1GSE001AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0487 | IND | In
1 | KIT |  |  |  | 1KIT412CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 1KITF0488 |  | In
1 | KIT |  |  |  | 1KIT415CR | 1GSE001AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 1KITF0489 | IND | In
9 | KIT |  |  |  | 1KIT415CR | 9KIT490CR |  |  |  | 50 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0491 | IND | In
1 | KIT |  |  |  | 1KIT415CR | 1KIT413AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 1KITF0493 | IND | In
1 | KIT |  |  |  | 1KIT408CR | 1KIT414CR |  |  |  | 32 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0494 | IND | In
1 | KIT |  |  |  | 1KIT408CR | 1KIT414CR |  |  |  | 32 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0496 | IND | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT104AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0501 |  | In
1 | KIT |  |  |  | 1KIT501CR | 9KIT415CR | [6 empty] | 12 | 5 | 4p Fibre optic cable-Armoured |  | 1KITF0501 |  | In
1 | KIT |  |  |  | 1KIT409CR | 1KIT501CR |  |  |  | 55 |  |  | 12 | 5 | FIBRE 8 CORE | A | 1KITF0501 | G, IND, 1L6573H - L, 1L6642A - C, 1L6673B, 1L6LB2A, 9L5LB | In
1 | KIT |  |  |  | 1KIT502CR | 9KIT416CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0502 |  | In
1 | KIT |  |  |  | 1KIT410CR | 1KIT502CR |  |  |  | 80 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0502 | G, IND, 1L6573H - L, 1L6642A - C, 1L6673B, 1L6LB2A, 9L5LB | In
1 | KIT |  |  |  | 1KIT501CR | 9KIT415CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0503 |  | In
1 | KIT |  |  |  | 1KIT409CR | 1KIT501CR |  |  |  | 55 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0503 | G, IND, 1L6573H - L, 1L6642A - C, 1L6673B, 1L6LB2A, 9L5LB | In
1 | KIT |  |  |  | 1KIT502CR | 9KIT416CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0504 |  | In
1 | KIT |  |  |  | 1KIT410CR | 1KIT502CR |  |  |  | 80 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0504 | G, IND, 1L6573H - L, 1L6642A - C, 1L6673B, 1L6LB2A, 9L5LB | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT106AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0505 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT413CR | [6 empty] | 12 | 5 | 4p Fibre optic cable-Armoured |  | 1KITF0505 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT501CR |  |  |  | 15 |  |  | 12 | 5 | FIBRE 8 CORE | A | 1KITF0505 | IND,1L6571D-A,IND | In
1 | KIT |  |  |  | 1KIT502CR | 1KIT414CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0506 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT415CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0507 |  | In
1 | KIT |  |  |  | 1KIT413CR | 1KIT501CR |  |  |  | 15 |  |  |  |  | FIBRE 8 CORE | A | 1KITF0507 | IND | In
1 | KIT |  |  |  | 1KIT502CR | 1KIT416CR | [8 empty] | 4p Fibre optic cable-Armoured |  | 1KITF0508 |  | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT105AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0509 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0509 |  | In
1 | KIT |  |  |  | 1KIT407CR | 1KIT501CR |  |  |  | 35 |  |  | 12 | 5 | FIBRE 8 CORE | A | 1KITF0509 | IND | In
1 | KIT |  |  |  | 1KIT502CR | 1KIT502AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0510 |  | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT107AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0511 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0511 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0512 |  | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT108AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0513 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0513 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0514 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0515 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0516 |  | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT101AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0517 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0517 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0518 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0519 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0520 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0521 |  | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0521 | IND | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0522 |  | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT102AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0523 |  | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0523 |  | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  | 12 | 5 | FIBRE | NA | 1KITF0523 | IND | In
1 | KIT |  |  |  | 1KIT501CR | 1KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0524 |  | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0525 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0527 | IND-IND | In
1 | KIT |  |  |  | 1KIT201CR | 1KIT103AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0529 |  | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  | 12 | 5 | FIBRE | NA | 1KITF0529 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0531 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0533 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0535 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0537 | IND | In
1 | KIT |  |  |  | 1KIT505CR | 1KIT504AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 1KITF0539 | IND | In
1 | KIT |  |  |  | 1KIT501ZL | 1KIT501AR |  |  |  | 25 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0561 | IND | In
1 | KIT |  |  |  | 1KIT502ZL | 1KIT502AR |  |  |  | 20 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0562 | IND | In
1 | KIT |  |  |  | 1KIT503ZL | 1KIT501AR |  |  |  | 30 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0563 | IND | In
1 | KIT |  |  |  | 1KIT504ZL | 1KIT502AR |  |  |  | 20 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0564 | IND | In
1 | KIT |  |  |  | 1KIT505ZL | 1KIT501AR |  |  |  | 30 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0565 | IND | In
1 | KIT |  |  |  | 1KIT506ZL | 1KIT501AR |  |  |  | 30 |  |  |  |  | FIBRE 4 CORE | NA | 1KITF0566 | IND | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT104AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0601 |  | In
1 | KIT |  |  |  | 9KIT010AR | 9KIT413CR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 1KITF0601 |  | Out
1 | KIT |  |  |  | 1KIT411CR | 9KIT202CC | [8 empty] | 1p Fibre OptIc Cable |  | 1KITF0603 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT106AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0605 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT105AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0609 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT107AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0611 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT108AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0613 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT101AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0617 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT102AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0623 |  | In
1 | KIT |  |  |  | 1KIT202CR | 1KIT103AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 1KITF0629 |  | In
1 | KIT |  |  |  | 1GSE001AR | 1KIR | [8 empty] | 4PAIR FIBRE OPTIC CABLE-ARMOURED |  | 1KITF0901 |  | Out
1 | KIT |  |  |  | 1RPN011CR | 1KIT105AR |  |  |  | 10 |  |  |  |  | 16P ERF | NA | 1KITG0??? | IND | In
1 | KIT |  |  |  | 1KRG152AR | 1KIT106AR |  |  |  | 33 |  |  |  |  | 16P ERF | NA | 1KITG0??? | (506/504BN IN KRG 152AR) 1ND 1L6 6651C,J 6642B 6681BC IND | In
1 | KIT |  |  |  | 1KRG152AR | 1KIT106AR |  |  |  | 34 |  |  |  |  | 16PR ERF | NA | 1KITG0??? | IND 1L6 6681BA 6642B 6651JHGFDC IND (106AR C13) | In
1 | KIT |  |  |  | 1SAS001CQ | 1KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0008 |  | In
1 | KIT |  |  |  | 1KRG143AR | 1KIT106ARC9 |  |  |  | 19 |  |  |  |  | 16P ERF | NA | 1KITG0143 | IND | In
1 | KIT |  |  |  | 1KIT408AR | 1GRE001AR | [8 empty] | CAT5E UTP Line 1 |  | 1KITG0401 |  | In
1 | KIT |  |  |  | 1GRE001AR | 1GSE002AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0401 | IND | Out
1 | KIT |  |  |  | 1KIT408AR | 1GRE001AR | [8 empty] | CAT5E UTP Line 2 |  | 1KITG0402 |  | In
1 | KIT |  |  |  | 1GSE002AR | 1GRE001AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0402 | IND | Out
1 | KIT |  |  |  | 1KIT408AR | 1GRE001AR | [8 empty] | CAT5E UTP Line 1 |  | 1KITG0403 |  | In
1 | KIT |  |  |  | 1KIT408AR | 1GRE001AR | [8 empty] | CAT5E UTP Line 2 |  | 1KITG0404 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 1 |  | 1KITG0405 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 2 |  | 1KITG0406 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 1 |  | 1KITG0407 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 2 |  | 1KITG0408 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 1 |  | 1KITG0409 |  | In
1 | KIT |  |  |  | 1KIT411AR | 1GSE001AR | [8 empty] | CAT5E UTP Line 2 |  | 1KITG0410 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT501ZL | [8 empty] | CAT5E UTP |  | 1KITG0501 |  | In
1 | KIT |  |  |  | 1KRG152AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0502 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0502 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT501ZL | [8 empty] | CAT5E UTP |  | 1KITG0503 |  | In
1 | KIT |  |  |  | 1KRG152AR | 1KIT106ARC7 |  |  |  | 34 |  |  |  |  | 16P ERF | NA | 1KITG0503 | IND 1L6 6681BA 6642B 6651JHGFDC IND | In
1 | KIT |  |  |  | 1KRG155AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0504 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0504 |  | In
1 | KIT |  |  |  | 1KRG155AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0505 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT502ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0505 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT505ZL | [8 empty] | CAT5E UTP |  | 1KITG0506 |  | In
1 | KIT |  |  |  | 1KRG113AR | 1KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0507 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT505ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0507 |  | In
1 | KIT |  |  |  | 1KRG113AR | 1KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0508 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT505ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0508 |  | In
1 | KIT |  |  |  | 1KRG113AR | 1KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0509 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT503ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0509 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT506ZL | [8 empty] | CAT5E UTP |  | 1KITG0510 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT503ZL | [8 empty] | CAT5E UTP |  | 1KITG0511 |  | In
1 | KIT |  |  |  | 1KRG124AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0512 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT506ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0512 |  | In
1 | KIT |  |  |  | 1KRG124AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0513 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT507ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0513 |  | In
1 | KIT |  |  |  | 1KRG124AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0514 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT508ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0514 |  | In
1 | KIT |  |  |  | 1KRG124AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0515 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT507ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0515 |  | In
1 | KIT |  |  |  | 1KRG133AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0516 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT508ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0516 |  | In
1 | KIT |  |  |  | 1KRG133AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0517 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT509ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0517 |  | In
1 | KIT |  |  |  | 1KRG133AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0518 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT510ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0518 |  | In
1 | KIT |  |  |  | 1KRG133AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0519 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT509ZL | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0519 |  | In
1 | KIT |  |  |  | 1KRG143AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0520 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 2 |  | 1KITG0520 |  | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0521 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 2 |  | 1KITG0522 |  | In
1 | KIT |  |  |  | 1RPN010CR | 1KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0523 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 4 |  | 1KITG0523 |  | In
1 | KIT |  |  |  | 1KRG158AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0524 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 4 |  | 1KITG0524 |  | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 6 |  | 1KITG0525 |  | In
1 | KIT |  |  |  | 1KIT507ZL | 1KIT501AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0525 | IND | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 6 |  | 1KITG0526 |  | In
1 | KIT |  |  |  | 1KIT508ZL | 1KIT502AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0526 | IND | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT501HI | [8 empty] | CAT5E UTP TO BLACK & WHITE PRINTER IN MCR |  | 1KITG0527 |  | In
1 | KIT |  |  |  | 1KIT507ZL | 1KIT501AR |  |  |  | 10 |  |  |  |  | CAT6 | NA | 1KITG0527 | IND | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT503HI | [8 empty] | CAT5E UTP TO COLOUR PRINTER IN MCR |  | 1KITG0528 |  | In
1 | KIT |  |  |  | 1KIT508ZL | 1KIT502AR |  |  |  | 15 |  |  |  |  | CAT6 | NA | 1KITG0528 | IND | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT502ZL | [8 empty] | CAT5E UTP TO BLACK & WHITE PRINTER IN KIT ROOM |  | 1KITG0529 |  | In
1 | KIT |  |  |  | 1KIT507ZL | 1KIT501AR |  |  |  | 10 |  |  |  |  | CAT5 | NA | 1KITG0529 | IND | In
1 | KIT |  |  |  | 1KIT501AR | 1KIT504ZL | [8 empty] | CAT5E UTP TO COLOUR PRINTER IN KIT ROOM |  | 1KITG0530 |  | In
1 | KIT |  |  |  | 1KIT508ZL | 1KIT502AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0530 | IND | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0531 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT501HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0531 |  | In
1 | KIT |  |  |  | 1KIT507ZL | 1KIT501AR |  |  |  | 10 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0531 | IND | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0532 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT502HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0532 |  | In
1 | KIT |  |  |  | 1KIT508ZL | 1KIT502AR |  |  |  | 15 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0532 | IND | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0533 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT503HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 1KITG0533 |  | In
1 | KIT |  |  |  | 1KIT509ZL | 1KIT501AR |  |  |  | 10 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0533 | IND | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT504HI | [8 empty] | CAT5E UTP |  | 1KITG0534 |  | In
1 | KIT |  |  |  | 1KIT510ZL | 1KIT502AR |  |  |  | 15 |  |  |  |  | CAT5 | NA | 1KITG0534 | IND | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0535 |  | In
1 | KIT |  |  |  | 1KIT502AR | 1KIT510ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO TURBINE WORKSTATION 2KVM |  | 1KITG0535 |  | In
1 | KIT |  |  |  | 1KIT509ZL | 1KIT501AR |  |  |  | 10 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0535 | IND | In
1 | KIT |  |  |  | 1KBS002AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0536 |  | In
1 | KIT |  |  |  | 1KIT503AR | 1KIT512ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER "A" KVM |  | 1KITG0536 |  | In
1 | KIT |  |  |  | 1KIT510ZL | 1KIT502AR |  |  |  | 15 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0536 | IND | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0537 |  | In
1 | KIT |  |  |  | 1KIT503AR | 1KIT514ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION 1 KVM |  | 1KITG0537 |  | In
1 | KIT |  |  |  | 1KIT509ZL | 1KIT501AR |  |  |  | 10 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0537 | IND | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0538 |  | In
1 | KIT |  |  |  | 1KIT504AR | 1KIT516ZL | [6 empty] | SP | 0.2 | CAT5E UTP O COMBO SERVER" B"KVM |  | 1KITG0538 |  | In
1 | KIT |  |  |  | 1KIT510ZL | 1KIT502AR |  |  |  | 15 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0538 | IND | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0539 |  | In
1 | KIT |  |  |  | 1KIT504AR | 1KIT518ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION 2 KVM |  | 1KITG0539 |  | In
1 | KIT |  |  |  | 1KIT509ZL | 1KIT501AR |  |  |  | 10 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0539 | IND | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0540 |  | In
1 | KIT |  |  |  | 1KIT505AR | 1KIT520ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO KIT WORKSTATION 1 KVM |  | 1KITG0540 |  | In
1 | KIT |  |  |  | 1KIT510ZL | 1KIT502AR |  |  |  | 15 |  |  | SP | 0.2 | CAT6 | NA | 1KITG0540 | IND | In
1 | KIT |  |  |  | 1KIT506AR | 1KIT522ZL | [8 empty] | CAT5E UTP TO KIT WORKSTATION 2 KVM |  | 1KITG0541 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0542 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0543 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0544 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0545 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0547 |  | In
1 | KIT |  |  |  | 1KIT504AR | 1KIT502AR |  |  |  | 10 |  |  |  |  | CAT5 | NA | 1KITG0550 | IND | In
1 | KIT |  |  |  | 1KBS004AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0552 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0554 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0555 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0557 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0558 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0559 |  | In
1 | KIT |  |  |  | 1KRG702AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0561 |  | In
1 | KIT |  |  |  | 1KIT501HI | 1KIT502AR |  |  |  | 35 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0561 | IND | In
1 | KIT |  |  |  | 1KIT502HI | 1KIT502AR |  |  |  | 35 |  |  |  |  | CAT5 | NA | 1KITG0562 | IND | In
1 | KIT |  |  |  | 1KRG702AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0563 |  | In
1 | KIT |  |  |  | 1KIT503HI | 1KIT502AR |  |  |  | 10 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0563 | IND | In
1 | KIT |  |  |  | 1KRG702AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0564 |  | In
1 | KIT |  |  |  | 1KIT504HI | 1KIT502AR |  |  |  | 10 |  |  | SP | 0.2 | CAT5 | NA | 1KITG0564 | IND | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0567 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0568 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0572 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0574 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0575 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0577 |  | In
1 | KIT |  |  |  | 1KBS003AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0578 |  | In
1 | KIT |  |  |  | 1KRG158AR | 1KIT410AR | [8 empty] | 8P X 0.22mm2 INSTRUMENT PVC |  | 1KITG0599 |  | In
1 | KIT |  |  |  | 1KBS004AR | 1KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0621 |  | In
1 | KIT |  |  |  | 1KRG162AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0661 |  | In
1 | KIT |  |  |  | 9KRG701AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0681 |  | In
1 | KIT |  |  |  | 9KRG701AR | 1KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0682 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0701 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0702 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0703 |  | In
1 | KIT |  |  |  | 1KBS001AR | 1KIT104AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0704 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0951 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0952 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0953 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0954 |  | In
1 | KIT |  |  |  | 1KIT108AR | 1KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 1KITG0955 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0001 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0002 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0005 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0006 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0009 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0010 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0013 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0014 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0017 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0018 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0021 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0022 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0025 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0026 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0029 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0030 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0033 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0034 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0037 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0038 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0041 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0042 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0045 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0046 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0049 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0050 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0053 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0054 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0057 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0058 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0061 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0062 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0065 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0066 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0069 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0070 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0073 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0074 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0077 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0078 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0081 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0082 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0085 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0086 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0089 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0090 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0093 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0094 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0097 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0098 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0101 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0102 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0105 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0106 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0109 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0113 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 15 | 0 |  |  | 64 | 0.3 |  | NA | 2KITE0114 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR | [6 empty] | 64 | 0.3 | 64c x 0,22mm2 |  | 2KITE0114 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0117 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR | [8 empty] | 32 x 0,22 mm2 |  | 2KITE0118 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  |  |  | 15 |  |  |  |  | 32 x 0.22 | NA | 2KITE0118 | IND - IND | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0121 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0125 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0129 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0133 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0137 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0141 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0145 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0149 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0153 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0157 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0161 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0165 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0169 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0173 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0177 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0181 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0185 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0189 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0193 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0197 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0201 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0205 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0209 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0213 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0217 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0221 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0225 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0229 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0233 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0237 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0241 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0245 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0249 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0253 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0257 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0261 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0265 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0269 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0273 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0277 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0281 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0285 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0289 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0293 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0297 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0301 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0305 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0309 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0313 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0317 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR | [8 empty] | 32 x 0,22 mm2 |  | 2KITE0318 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0321 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0325 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0329 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0333 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0337 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0341 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0345 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0349 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0353 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0357 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0361 |  | In
2 | KIT |  |  |  | 2KIT365BN | 2KIT105AR |  |  |  | 12 |  |  |  |  | 64x0.35 | NA | 2KITE0365 | IND | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  |  |  | 25 |  |  |  |  | 32 x 0.22 | NA | 2KITE0381 | IND, 2L6321G-F, IND | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0401 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0403 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0405 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0407 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0409 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0411 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0413 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0415 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0417 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0801 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0802 |  | In
2 | KIT |  |  |  | 2KIT004CQ | 2KIT107AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0805 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0806 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0810 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0814 |  | In
2 | KIT |  |  |  | 2KIT002CQ | 2KIT103AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0818 |  | In
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0821 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT003CQ |  | 0 | 0 | 1 |  |  | 3 | 1.5 |  | NA | 2KITE0823 |  | Out
2 | KIT |  |  |  | 2KIT003CQ | 2KIT105AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0825 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0833 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0837 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0841 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0845 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0849 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT101AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0853 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0857 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0861 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0865 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0869 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0873 |  | In
2 | KIT |  |  |  | 2KIT001CQ | 2KIT102AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0877 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0921 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0925 |  | In
2 | KIT |  |  |  | 2KIT005CQ | 2KIT108AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0927 |  | In
2 | KIT |  |  |  | 2KIT005CQ | 2KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0928 |  | In
2 | KIT |  |  |  | 2KIT005CQ | 2KIT108AR |  | 20 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0929 |  | In
2 | KIT | [13 empty] | Spare |  | 2KITE0930 |  | Out
2 | KIT |  |  |  | 2KIT005CQ | 2KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0934 |  | In
2 | KIT |  |  |  | 2KIT005CQ | 2KIT108AR |  | 0 | 0 | 1 |  |  | 64 | 0.3 |  | NA | 2KITE0935 |  | In
2 | KIT |  |  |  | 2KIT405CR | 2KIT401CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0401 |  | In
2 | KIT |  |  |  | 2KIT401CR | 2KIT401AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0401 |  | In
2 | KIT |  |  |  | 2KIT406CR | 2KIT402CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0402 |  | In
2 | KIT |  |  |  | 2KIT401AR | 2KIT402CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0402 |  | In
2 | KIT |  |  |  | 2KIT409CR | 2KIT403CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0403 |  | In
2 | KIT |  |  |  | 2KIT407CR | 2KIT401CR |  |  |  | 190 |  |  |  |  | FIBRE | A | 2KITF0403 | IND,9L5LB2A,9L4LB2A,9L3LB2A,IND,9L3831A,9N3411A,9N3B11A,9N2B11A,9N2021A-F,IND,9N2051C,IND | In
2 | KIT |  |  |  | 2KIT410CR | 2KIT404CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0404 |  | In
2 | KIT |  |  |  | 2KIT402CR | 2KIT408CR |  |  |  | 190 |  |  |  |  | FIBRE | A | 2KITF0404 | IND,9L5LB2A,9L4LB2A,9L3LB2A,IND,9L3831A,9N3411A,9N3B11A,9N2B11A,9N2021A-F,IND,9N2051C,IND | In
2 | KIT |  |  |  | 2KIT415CR | 2KIT408CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0405 |  | In
2 | KIT |  |  |  | 2KIT403CR | 2GRH002AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0405 |  | In
2 | KIT |  |  |  | 2KIT416CR | 2KIT408CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0406 |  | In
2 | KIT |  |  |  | 2GRH002AR | 2KIT404CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0406 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2KIT411CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0407 |  | In
2 | KIT |  |  |  | 2KIT403CR | 2GRH002AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0407 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2KIT411CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0408 |  | In
2 | KIT |  |  |  | 2GRH002AR | 2KIT404CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0408 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT402CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0409 |  | In
9 | KIT |  |  |  | 2KIT403CR | 9KIT421CR |  |  |  | 210 |  |  |  |  | FIBRE | A | 2KITF0409 | IND,2L55J2A,2L45J2A,IND,2M3541A,IND, (30m TRAY WORK) | In
9 | KIT |  |  |  | 2KIT403CR | 9KIT421CR |  |  |  | 210 |  |  |  |  | FIBRE | A | 2KITF0409 | IND,2L55J2A,2L45J2A,IND,2M3541A,IND, (30m TRAY WORK) | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT402CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0410 |  | In
9 | KIT |  |  |  | 2KIT404CR | 9KIT422CR |  |  |  | 210 |  |  |  |  | FIBRE | A | 2KITF0410 | IND,2L55J2A,2L45J2A,IND,2M3541A,IND, (30m TRAY WORK) | In
2 | KIT |  |  |  | 2KIT409CR | 2KIT402CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0411 |  | In
2 | KIT |  |  |  | 2KIT405CR | 2GEX001AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0411 |  | In
2 | KIT |  |  |  | 2KIT410CR | 2KIT402CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0412 |  | In
2 | KIT |  |  |  | 2GEX001AR | 2KIT406CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0412 |  | In
2 | KIT |  |  |  | 2KIT408CR | 2KIT406CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0413 |  | In
2 | KIT |  |  |  | 2KIT405CR | 2KIT409CR |  |  |  | 190 |  |  |  |  | FIBRE | A | 2KITF0413 | IND,2L6511B-C,2L6511D,2L6721A,2L6501H-E,IND,2L65J2A,2L55J2A,2L45J2A,IND,2M3541A,IND | In
2 | KIT |  |  |  | 2KIT407CR | 2KIT406CR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0414 |  | In
2 | KIT |  |  |  | 2KIT406CR | 2KIT410CR |  |  |  | 210 |  |  |  |  | FIBRE | A | 2KITF0414 | IND,2L6511G-C,2L6511D,2L6721A,2L6501H-E,IND,2L65J2A,2L55J2A,2L45J2A,IND,2M3541A,IND | In
2 | KIT |  |  |  | 2KIT405CR | 2KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0415 |  | In
2 | KIT |  |  |  | 2KIT407CR | 2KIT406AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0415 |  | In
2 | KIT |  |  |  | 2KIT406CR | 2KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0416 |  | In
2 | KIT |  |  |  | 2KIT408CR | 2KIT406AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0416 |  | In
2 | KIT |  |  |  | 2KIT403CR | 2GEX001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0417 |  | In
9 | KIT |  |  |  | 9KIT421CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0417 |  | Out
2 | KIT |  |  |  | 2KIT404CR | 2GEX001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0418 |  | In
9 | KIT |  |  |  | 9KIT422CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0418 |  | Out
2 | KIT |  |  |  | 2KIT401CR | 2KIT401AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0419 |  | In
9 | KIT |  |  |  | 9KIT421CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0419 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT401AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0420 |  | In
9 | KIT |  |  |  | 9KIT422CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0420 |  | Out
2 | KIT |  |  |  | 2KIT408AR | 2KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0421 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0421 |  | Out
2 | KIT |  |  |  | 2KIT408AR | 2KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0422 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0422 |  | Out
2 | KIT |  |  |  | 2KIT408AR | 2KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0423 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0423 |  | Out
2 | KIT |  |  |  | 2KIT408AR | 2KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0424 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0424 |  | Out
2 | KIT |  |  |  | 2KIT411AR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0425 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0425 |  | Out
2 | KIT |  |  |  | 2KIT411AR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0426 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0426 |  | Out
2 | KIT |  |  |  | 2KIT402AR | 2KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0427 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0427 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0428 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0428 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0429 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0429 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0430 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0430 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0431 |  | In
9 | KIT |  |  |  | 9KIT423CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0431 |  | Out
2 | KIT |  |  |  | 2KIT402CR | 2KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0432 |  | In
9 | KIT |  |  |  | 9KIT424CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0432 |  | Out
2 | KIT |  |  |  | 2KIT406CR | 2KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0433 |  | In
9 | KIT |  |  |  | 9KIT425CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0433 |  | Out
2 | KIT |  |  |  | 2KIT406CR | 2KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0434 |  | In
9 | KIT |  |  |  | 9KIT426CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0434 |  | Out
2 | KIT |  |  |  | 2KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0435 |  | In
9 | KIT |  |  |  | 9KIT425CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0435 |  | Out
2 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0436 |  | Out
9 | KIT |  |  |  | 9KIT426CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0436 |  | Out
2 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0437 |  | Out
9 | KIT |  |  |  | 9KIT425CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0437 |  | Out
2 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0438 |  | Out
9 | KIT |  |  |  | 9KIT426CR | 9KIT020AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0438 |  | Out
2 | KIT |  |  |  | 9KIT415CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0439 |  | Out
2 | KIT |  |  |  | 9KIT416CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0440 |  | Out
2 | KIT |  |  |  | 9KIT417CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0441 |  | Out
2 | KIT |  |  |  | 9KIT418CR | 9KIT010AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0442 |  | Out
2 | KIT |  |  |  | 9KIT010AR | 2KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0443 |  | In
9 | KIT |  |  |  | 2KIT406AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0443 |  | In
9 | KIT |  |  |  | 2KIT406AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0444 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0445 |  | In
9 | KIT |  |  |  | 2KIT406AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0445 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT406AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0446 |  | In
9 | KIT |  |  |  | 2KIT406AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0446 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0447 |  | In
9 | KIT |  |  |  | 2KIT402AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0447 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0448 |  | In
9 | KIT |  |  |  | 2KIT402AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0448 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0449 |  | In
9 | KIT |  |  |  | 2KIT402AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0449 |  | In
2 | KIT |  |  |  | 9KIT010AR | 2KIT402AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0450 |  | In
9 | KIT |  |  |  | 2KIT402AR | 9KIT020AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0450 |  | In
2 | KIT |  |  |  | 2KIT406AR | 2KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0451 |  | In
2 | KIT |  |  |  | 2KIT407AR | 2KIT406AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0451 |  | In
2 | KIT |  |  |  | 2KIT406AR | 2KIT407AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0452 |  | In
2 | KIT |  |  |  | 2KIT407AR | 2KIT406AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0452 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0453 |  | In
2 | KIT |  |  |  | 2KIT403AR | 2KIT402AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0453 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT403AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0454 |  | In
2 | KIT |  |  |  | 2KIT403AR | 2KIT402AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0454 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0455 |  | In
2 | KIT |  |  |  | 2KIT404AR | 2KIT402AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0455 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT404AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0456 |  | In
2 | KIT |  |  |  | 2KIT404AR | 2KIT402AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0456 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0457 |  | In
2 | KIT |  |  |  | 2KIT405AR | 2KIT402AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 2KITF0457 |  | In
2 | KIT |  |  |  | 2KIT402AR | 2KIT405AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0458 |  | In
2 | KIT |  |  |  | 2KIT405AR | 2KIT402AR |  |  |  | 25 |  |  |  |  | FIBRE | NA | 2KITF0458 |  | In
2 | KIT |  |  |  | 2KIT411CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0459 |  | In
2 | KIT |  |  |  | 9KIT423CR | 2KIT411CR |  |  |  | 80 |  |  |  |  | FIBRE | A | 2KITF0459 | IND,2L6511B-C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND | In
2 | KIT |  |  |  | 2KIT412CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0460 |  | In
9 | KIT |  |  |  | 2KIT412CR | 9KIT424CR |  |  |  | 50 |  |  |  |  | FIBRE | A | 2KITF0460 | IND,(5m TRAY WORK) | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0461 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT408CR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0461 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0462 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT408AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0462 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0463 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT408AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0463 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT408AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0464 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT408AR |  |  |  | 60 |  |  |  |  | FIBRE | NA | 2KITF0464 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0465 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT412AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0465 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0466 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT412AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0466 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0467 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2KIT412AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0467 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT412AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0468 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2KIT412AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0468 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0469 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2GSE002AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0469 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0470 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2GSE002AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0470 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0471 |  | In
2 | KIT |  |  |  | 2KIT411CR | 2GSE002AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0471 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0472 |  | In
2 | KIT |  |  |  | 2KIT412CR | 2GSE002AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0472 |  | In
2 | KIT |  |  |  | 2KIT409CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0473 |  | In
2 | KIT |  |  |  | 2KIT409CR | 2GSE002AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0473 |  | In
2 | KIT |  |  |  | 2KIT410CR | 2GSE002AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0474 |  | In
2 | KIT |  |  |  | 2KIT410CR | 2GSE002AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0474 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0475 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0475 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0476 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0476 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0477 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0477 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0478 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0478 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0479 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2GSE001AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0479 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0480 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2GSE001AR |  |  |  | 40 |  |  |  |  | FIBRE | NA | 2KITF0480 |  | In
2 | KIT |  |  |  | 2KIT412AR | 2KIT411AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0481 |  | In
2 | KIT |  |  |  | 2KIT411AR | 2KIT412AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 2KITF0481 |  | In
2 | KIT |  |  |  | 2KIT412AR | 2KIT411AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0482 |  | In
2 | KIT |  |  |  | 2KIT411AR | 2KIT412AR |  |  |  | 30 |  |  |  |  | FIBRE | NA | 2KITF0482 |  | In
2 | KIT |  |  |  | 2KIT408AR | 2KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0483 |  | In
2 | KIT |  |  |  | 2KIT410AR | 2KIT408AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0483 |  | In
2 | KIT |  |  |  | 2KIT408AR | 2KIT410AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0484 |  | In
2 | KIT |  |  |  | 2KIT410AR | 2KIT408AR |  |  |  | 50 |  |  |  |  | FIBRE | NA | 2KITF0484 |  | In
2 | KIT |  |  |  | 2KIT408AR | 2KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0485 |  | In
2 | KIT |  |  |  | 2KIT409AR | 2KIT408AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0485 |  | In
2 | KIT |  |  |  | 2KIT408AR | 2KIT409AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0486 |  | In
2 | KIT |  |  |  | 2KIT409AR | 2KIT408AR |  |  |  | 15 |  |  |  |  | FIBRE | NA | 2KITF0486 |  | In
2 | KIT |  |  |  | 2KIT411CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0487 |  | In
9 | KIT |  |  |  | 2KIT411CR | 9KIT423CR |  |  |  | 80 |  |  |  |  | FIBRE | A | 2KITF0487 | IND,2L6511B-C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND | In
2 | KIT |  |  |  | 2KIT412CR | 9KIT413CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0488 |  | In
9 | KIT |  |  |  | 2KIT412CR | 9KIT424CR |  |  |  | 60 |  |  |  |  | FIBRE | A | 2KITF0488 | IND | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT104AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0501 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT407CR | [6 empty] | 12 | 5 | 4p Fibre OptIc Cable-Armoured |  | 2KITF0501 |  | In
9 | KIT |  |  |  | 2KIT501CR | 9KIT425CR |  |  |  | 85 |  |  | 12 | 5 | FIBRE | A | 2KITF0501 | IND,2L6511C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND | In
9 | KIT |  |  |  | 2KIT501CR | 9KIT417CR |  |  |  | 85 |  |  | 12 | 5 | FIBRE | A | 2KITF0501 | IND,2L6511C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND (40m TRAY WORK,76x76) | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT408CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0502 |  | In
9 | KIT |  |  |  | 2KIT502CR | 9KIT418CR |  |  |  | 85 |  |  |  |  | FIBRE | A | 2KITF0502 | IND,2L6511C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND (40m TRAY WORK,76x76) | In
1 | KIT |  |  |  | 9KIT426CR | 12KIT502CR |  |  |  | 85 |  |  |  |  | FIBRE | A | 2KITF0502 | IND,2L6511C-D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND | Out
2 | KIT |  |  |  | 2KIT501CR | 2KIT411CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0503 |  | In
9 | KIT |  |  |  | 2KIT501CR | 9KIT425CR |  |  |  | 85 |  |  |  |  | FIBRE | A | 2KITF0503 | IND,2L6511C,2L6511D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND (40m TRAY WORK,76x76) | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT412CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0504 |  | In
1 | KIT |  |  |  | 9KIT426CR | 12KIT502CR |  |  |  | 85 |  |  |  |  | FIBRE | A | 2KITF0504 | IND,2L6511C-D,2L6721A,2L6502H-K,IND,2L60J2A,2L50J2A,IND | Out
2 | KIT |  |  |  | 2KIT201CR | 2KIT106AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0505 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT413CR | [6 empty] | 12 | 5 | 4p Fibre OptIc Cable-Armoured |  | 2KITF0505 |  | In
2 | KIT |  |  |  | 2KIT413CR | 2KIT501CR |  |  |  | 20 |  |  | 12 | 5 | FIBRE | A | 2KITF0505 | IND,2L6511B-C,IND | In
9 | KIT |  |  |  | 2KIT413CR | 9KIT425CR |  |  |  | 80 |  |  | 12 | 5 | FIBRE | NA | 2KITF0505 | IND,2L6511B-C,2L6511D,2L6721A,2L6501H-K,IND,2L60J2A,2L50J2A,IND | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT414CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0506 |  | In
2 | KIT |  |  |  | 2KIT414CR | 2KIT502CR |  |  |  | 40 |  |  |  |  | FIBRE | A | 2KITF0506 | IND | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT415CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0507 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT416CR | [8 empty] | 4p Fibre OptIc Cable-Armoured |  | 2KITF0508 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT105AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0509 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT107AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0511 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 2KITF0511 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR |  |  |  | 20 |  |  | 12 | 5 | FIBRE | NA | 2KITF0511 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT502AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0512 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT502AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0512 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT108AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0513 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 2KITF0513 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR |  |  |  | 20 |  |  | 12 | 5 | FIBRE | NA | 2KITF0513 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT502AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0514 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT502AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0514 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0515 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0515 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT502AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0516 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT501AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0516 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT101AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0517 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 2KITF0517 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR |  |  |  | 20 |  |  | 12 | 5 | FIBRE | NA | 2KITF0517 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT501AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0518 |  | In
2 | KIT |  |  |  | 2KIT502CR | 2KIT501AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0518 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0519 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0519 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0520 |  | In
2 | KIT |  |  |  | 2KIT504AR | 2KIT502CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0520 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0521 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0521 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0522 |  | In
2 | KIT |  |  |  | 2KIT504AR | 2KIT502CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0522 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT102AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0523 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [6 empty] | 12 | 5 | 1p Fibre OptIc Cable |  | 2KITF0523 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR |  |  |  | 20 |  |  | 12 | 5 | FIBRE | NA | 2KITF0523 |  | In
2 | KIT |  |  |  | 2KIT501CR | 2KIT504AR | [8 empty] | 1p Fibre OptIc Cable |  | 2KITF0524 |  | In
2 | KIT |  |  |  | 2KIT504AR | 2KIT502CR |  |  |  | 20 |  |  |  |  | FIBRE | NA | 2KITF0524 |  | In
2 | KIT |  |  |  | 2KIT201CR | 2KIT103AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0529 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT104AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0601 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT106AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0605 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT105AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0609 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT107AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0611 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT108AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0613 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT101AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0617 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT102AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0623 |  | In
2 | KIT |  |  |  | 2KIT202CR | 2KIT103AR |  | 0 | 0 | 1 |  |  | 12 | 5 | 5 | OPFI | 2KITF0629 |  | In
2 | KIT |  |  |  | 2GSE001AR | 2KIR | [8 empty] | 4PAIR FIBRE OPTIC CABLE-ARMOURED |  | 2KITF0901 |  | Out
2 | KIT |  |  |  | 2KRG152AR | 2KIT106AR |  |  |  | 20 |  |  |  |  | 16P ERF | NA | 2KITG0??? | (506/504BN IN KRG 152AR) IND 2L6 6511HF 6621CD IND | In
2 | KIT |  |  |  | 2RPN011CR | 2KIT105AR |  |  |  | 10 |  |  |  |  | 16P ERF | NA | 2KITG0??? | IND | In
2 | KIT |  |  |  | 2KRG152AR | 2KIT106AR |  |  |  | 22 |  |  |  |  | 16PR ERF | NA | 2KITG0??? | IND 2L6 6511HF 6621ABCD IND..(106AR C13) | In
2 | KIT |  |  |  | 2SAS001CQ | 2KIT105AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0008 |  | In
2 | KIT |  |  |  | 2KRG143AR | 2KIT106ARC9 |  |  |  | 25 |  |  |  |  | 16P ERF | NA | 2KITG0143 | IND 2L6 6511H F 6621C D IND | In
2 | KIT |  |  |  | 2GRE001AR | 2GSE002AR | [8 empty] | CAT5E UTP |  | 2KITG0401 |  | Out
2 | KIT |  |  |  | 2GRE001AR | 2GSE002AR | [8 empty] | CAT5E UTP |  | 2KITG0402 |  | Out
2 | KIT |  |  |  | 2GRE001AR | 2GSE002AR | [8 empty] | CAT5E UTP T |  | 2KITG0403 |  | Out
2 | KIT |  |  |  | 2GRE001AR | 2GSE002AR | [8 empty] | CAT5E UTP |  | 2KITG0404 |  | Out
2 | KIT |  |  |  | 2KIT501AR | 2KIT505AR | [8 empty] | CAT5E UTP O KIT OPERATORS WORKSTATION 1 |  | 2KITG0501 |  | In
2 | KIT |  |  |  | 2KRG152AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0502 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT501AR | [6 empty] | SP | 0.2 | CAT5E UTP TO REACTOR WORKSTATION 1 |  | 2KITG0502 |  | In
2 | KIT |  |  |  | 2KIT504ZL | 2KIT502AR |  |  |  | 35 |  |  | SP | 0.2 | CAT5 | NA | 2KITG0502 | IND | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT506AR | [8 empty] | CAT5E UTPO TO KIT OPERATORS WORKSTATION 2 |  | 2KITG0503 |  | In
2 | KIT |  |  |  | 2KRG152AR | 2KIT106ARC7 |  |  |  | 22 |  |  |  |  | 16P ERF | NA | 2KITG0503 | IND 2L6 6511H F 6621C D IND | In
2 | KIT |  |  |  | 2KRG155AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0504 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT505AR | [6 empty] | SP | 0.2 | CAT5E UTP TO KIT OPERATORS WORKSTATION 2 |  | 2KITG0504 |  | In
2 | KIT |  |  |  | 2KIT504ZL | 2KIT502AR |  |  |  | 35 |  |  | SP | 0.2 | CAT5 | NA | 2KITG0504 | IND | In
2 | KIT |  |  |  | 2KRG155AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0505 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT502AR | [6 empty] | SP | 0.2 | CAT5E UTPO KIT OPERATORS WORKSTATION |  | 2KITG0505 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT506AR | [8 empty] | CAT5E UTP TO KIT OPERATORS WORKSTATION 2 |  | 2KITG0506 |  | In
2 | KIT |  |  |  | 2KRG113AR | 2KIT105AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0507 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER |  | 2KITG0507 |  | In
2 | KIT |  |  |  | 2KRG113AR | 2KIT105AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0508 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER A |  | 2KITG0508 |  | In
2 | KIT |  |  |  | 2KRG113AR | 2KIT105AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0509 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER |  | 2KITG0509 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504AR | [8 empty] | CAT5E UTP O COMBO SERVER B |  | 2KITG0510 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [8 empty] | CAT5E UTP TO ENGINEERING WORKSTATION 1 |  | 2KITG0511 |  | In
2 | KIT |  |  |  | 2KRG124AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0512 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION1 |  | 2KITG0512 |  | In
2 | KIT |  |  |  | 2KRG124AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0513 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION2 |  | 2KITG0513 |  | In
2 | KIT |  |  |  | 2KRG124AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0514 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION2 |  | 2KITG0514 |  | In
2 | KIT |  |  |  | 2KRG124AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0515 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 1 |  | 2KITG0515 |  | In
2 | KIT |  |  |  | 2KRG133AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0516 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 1 |  | 2KITG0516 |  | In
2 | KIT |  |  |  | 2KRG133AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0517 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 3 |  | 2KITG0517 |  | In
2 | KIT |  |  |  | 2KRG133AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0518 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 3 |  | 2KITG0518 |  | In
2 | KIT |  |  |  | 2KRG133AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0519 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 5 |  | 2KITG0519 |  | In
2 | KIT |  |  |  | 2KRG143AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0520 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 5 |  | 2KITG0520 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0521 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 2 |  | 2KITG0522 |  | In
2 | KIT |  |  |  | 2RPN010CR | 2KIT105AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0523 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 4 |  | 2KITG0523 |  | In
2 | KIT |  |  |  | 2KRG158AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0524 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504AR | [6 empty] | SP | 0.2 | CAT5E UTP TO APPLICATION SERVER 4 |  | 2KITG0524 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 6 |  | 2KITG0525 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504AR | [8 empty] | CAT5E UTP TO APPLICATION SERVER 6 |  | 2KITG0526 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT501HI | [8 empty] | CAT5E UTP TO BLACK & WHITE PRINTER IN MCR |  | 2KITG0527 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT503HI | [8 empty] | CAT5E UTP TO COLOUR PRINTER IN MCR |  | 2KITG0528 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT502HI | [8 empty] | CAT5E UTP TO BLACK & WHITE PRINTER IN KIT ROOM |  | 2KITG0529 |  | In
2 | KIT |  |  |  | 2KIT501AR | 2KIT504HI | [8 empty] | CAT5E UTP TO COLOUR PRINTER IN KIT ROOM |  | 2KITG0530 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0531 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT501HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 2KITG0531 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0532 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT502HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 2KITG0532 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0533 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT503HI | [6 empty] | SP | 0.2 | CAT5E UTP |  | 2KITG0533 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT504HI | [8 empty] | CAT5E UTP |  | 2KITG0534 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0535 |  | In
2 | KIT |  |  |  | 2KIT502AR | 2KIT510ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO TURBINE WORKSTATION 2 KVM |  | 2KITG0535 |  | In
2 | KIT |  |  |  | 2KBS002AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0536 |  | In
2 | KIT |  |  |  | 2KIT503AR | 2KIT512ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER "A" KVM |  | 2KITG0536 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0537 |  | In
2 | KIT |  |  |  | 2KIT503AR | 2KIT514ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION 1 KVM |  | 2KITG0537 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0538 |  | In
2 | KIT |  |  |  | 2KIT504AR | 2KIT516ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO COMBO SERVER "B" KVM |  | 2KITG0538 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0539 |  | In
2 | KIT |  |  |  | 2KIT504AR | 2KIT518ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO ENGINEERING WORKSTATION 2 KVM |  | 2KITG0539 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0540 |  | In
2 | KIT |  |  |  | 2KIT505AR | 2KIT520ZL | [6 empty] | SP | 0.2 | CAT5E UTP TO KIT WORKSTATION 1 KVM |  | 2KITG0540 |  | In
2 | KIT |  |  |  | 2KIT506AR | 2KIT522ZL | [8 empty] | CAT5E UTP TO KIT WORKSTATION 2 KVM |  | 2KITG0541 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT106AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0542 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0543 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0544 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0545 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0547 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0551 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0554 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0555 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0557 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0558 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0559 |  | In
2 | KIT |  |  |  | 2KRG702AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0562 |  | In
2 | KIT |  |  |  | 2KRG702AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0564 |  | In
2 | KIT |  |  |  | 2KRG702AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0566 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0567 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0570 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0572 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0574 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0575 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0577 |  | In
2 | KIT |  |  |  | 2KBS003AR | 2KIT107AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0578 |  | In
2 | KIT |  |  |  | 2KRG158AR | 2KIT410AR | [8 empty] | 8P X 0.22mm2 INSTRUMENT PVC |  | 2KITG0599 |  | In
2 | KIT |  |  |  | 2KBS004AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0621 |  | In
2 | KIT |  |  |  | 2KRG172AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0661 |  | In
2 | KIT |  |  |  | 9KRG701AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0681 |  | In
2 | KIT |  |  |  | 9KRG701AR | 2KIT107AR |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0682 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0701 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0702 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0703 |  | In
2 | KIT |  |  |  | 2KBS001AR | 2KIT104AR |  | 20 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0704 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0951 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0952 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0953 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0954 |  | In
2 | KIT |  |  |  | 2KIT108AR | 2KIT005CQ |  | 0 | 0 | 1 |  |  | SP | 0.2 |  | BI | 2KITG0955 |  | In
9 | KIT |  |  |  | 9KIT491CR | 9KIT492CR |  |  |  | 605 |  |  |  |  | FIBRE 8 CORE | A | 9KITF0401 | F, 2L5251G - A, 2L5JB2A, 2L4JB2A, 9L3JB | Out
9 | KIT |  |  |  | 9KIT492CR | 9KIT493CR |  |  |  | 351 |  |  |  |  | FIBRE 8 CORE | A | 9KITF0402 | IND | Out
9 | KIT |  |  |  | 9KIT492CR | 9KIT002FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0403 |  | Out
9 | KIT |  |  |  | 9KIT492CR | 9KIT002FX |  |  |  | 5 |  |  |  |  | FIBRE | NA | 9KITF0403 | IND | Out
9 | KIT |  |  |  | 9KIT493CR | 0SIM502AR | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0404 |  | Out
0 | KIT |  |  |  | 9KIT493CR | 0SIM502AR |  |  |  | 10 |  |  |  |  | FIBRE | NA | 9KITF0404 | IND | Out
9 | KIT |  |  |  | 9KIT492CR | 9KIT002FX |  |  |  | 5 |  |  |  |  | 8 PR | NA | 9KITF0405 | IND | Out
9 | KIT |  |  |  | 9KIT492CR | 9KIT002FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0406 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 9KIT001FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0411 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 9KIT001FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0412 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 9KIT001FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0413 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 9KIT001FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0414 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 9KIT001FX | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0415 |  | Out
9 | KIT |  |  |  | 9KIT490CR | 0ESC002CR | [8 empty] | 1p Fibre Optic Cable |  | 9KITF0416 |  | Out
9 | KIT |  |  |  | 9KIT001FX | SYSTEM1 | [8 empty] | CAT5 UTP |  | 9KITG0400 |  | Out
9 | KIT |  |  |  | 9KIT002FX | 9KIT001HX | [8 empty] | CAT5 UTP |  | 9KITG0411 |  | Out
9 | KIT |  |  |  | 9KIT002FX | 9KIT002HX | [8 empty] | CAT5 UTP |  | 9KITG0412 |  | Out
9 | KIT |  |  |  | 9KIT002FX | 9KIT003HX | [8 empty] | CAT5 UTP |  | 9KITG0413 |  | Out
9 | KIT |  |  |  | 9KIT002FX | 9KIT001HI | [8 empty] | CAT5 UTP |  | 9KITG0414 |  | Out
9 | KIT |  |  |  | 9KIT002FX | 9KIT002HI | [8 empty] | CAT5 UTP |  | 9KITG0415 |  | Out

## Harsh Environment Cables (hidden)
UNIT | SYSTEM | ER CLASS | CATEG | RGNB | COMPONENT FROM | COMPONENT TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | CABLE CORES | Dimensions (mm2) | CABLE SIZE (mm2) | CBTYP | CABLE NUMBER | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) | FREQ. | START DATE (Outage) | TYPE OF TEST (ONLINE) | FREQ. | START DATE | TYPE OF TEST VISUAL / TACTILE | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE
1-2 | ABP |  |  |  | LKA0306 | ABP027VV |  | 107 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0307 | ABP011VV |  | 78 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0308 | ABP007VV |  | 77 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0309 | ABP003VV |  | 82 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0310 | ABP023VV |  | 79 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0311 | ABP019VV |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKA0312 | ABP015VV |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0301 | ABP009VV |  | 69 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0302 | ABP005VV |  | 67 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0303 | ABP001VV |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0304 | ABP021VV |  | 71 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0305 | ABP017VV |  | 75 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0306 | ABP013VV |  | 83 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0308 | ABP035VL |  | 92 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0309 | ABP036VL |  | 86 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ABP |  |  |  | LKC0401 | ABP025VV |  | 108 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO004CR | ACO001VL |  | 67 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO004CR | ACO006CR |  | 67 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO005CR | ACO003VL |  | 85 |  |  |  |  | 4 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO005CR | ACO004CR |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO006CR | ACO006VL |  | 77 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO006CR | ACO007CR |  | 69 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ACO007CR | ACO011VL |  | 78 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | ARE101CR | ACO005CR |  | 92 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ACO |  |  |  | LGD0101 | ACO002PO |  | 99 |  |  |  |  | 3 |  | 240 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | ACO |  |  |  | LGD0301 | ACO001PO |  | 106 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | ACO |  |  |  | LKD0307 | ACO001RS |  | 82 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ACO |  |  |  | LKD0408 | ACO002RS |  | 74 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGM |  |  |  | LKF0505 | AGM001PO |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKA0304 | AGR002ZV |  | 62 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKA0305 | AGR102CF |  | 70 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKB0307 | AGR001ZV |  | 89 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKB0308 | AGR101CF |  | 87 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKD0406 | AGR003PO |  | 33 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LKD0407 | AGR006PO |  | 109 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LLC0101 | AGR004PO |  | 11 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AGR |  |  |  | LLE0202 | AGR005PO |  | 89 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0301 | AHP011VL |  | 102 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0302 | AHP005VL |  | 89 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0303 | AHP001VL |  | 86 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0401 | AHP001VV |  | 123 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0402 | AHP002VV |  | 123 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0403 | AHP007VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKA0404 | AHP008VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0402 | AHP006VL |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0403 | AHP010VL |  | 93 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0404 | AHP004VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0405 | AHP005VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0406 | AHP010VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0407 | AHP011VV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0805 | AHP018VL |  | 120 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | AHP |  |  |  | LKC0806 | AHP027VL |  | 120 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APA |  |  |  | 9LGE0101 | APA003PO |  | 248 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | APA |  |  |  | 9LGE0101 | APA003PO |  | 248 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | APA |  |  |  | 9LGE0101 | APA003PO |  | 248 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | APA |  |  |  | APA002CR | APA001VL |  | 94 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APA |  |  |  | APA003CR | APA003VL |  | 79 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APA |  |  |  | APA004CR | APA005VL |  | 160 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APA |  |  |  | LKS0202 | APA001RS |  | 157 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APG |  |  |  | LKC0412 | APG010VL |  | 184 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP003CR | APP001VL |  | 6 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP004CR | APP003VL |  | 9 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP005CR | APP011VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP006CR | APP013VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP007CR | APP005VL |  | 31 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | APP |  |  |  | APP008CR | APP015VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE054MD |  | Site Run |  |  |  |  | 1PTB |  | 1 |  | M0020 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE055MD |  | Site Run |  |  |  |  | 1PTB |  | 1 |  | M0021 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE056MD |  | Site Run |  |  |  |  | 1PTB |  | 1 |  | M0022 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | PN1L513 | ARE058MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0301 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L513 | ARE059MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0303 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L513 | ARE060MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0305 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L529 | ARE055MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0307 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L529 | ARE056MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0309 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L529 | ARE057MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0311 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L515 | ARE052MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0313 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L515 | ARE053MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0315 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L515 | ARE054MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0317 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L533 | ARE010MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0319 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L533 | ARE020MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0321 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L533 | ARE030MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0323 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | KRG033AR | ARE043MD |  | 81 |  |  |  |  | 1PTB |  | 1 |  | M0325 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG033AR | ARE044MD |  | 81 |  |  |  |  | 1PTB |  | 1 |  | M0326 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG033AR | ARE045MD |  | 81 |  |  |  |  | 1PTB |  | 1 |  | M0327 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE046MD |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0328 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE047MD |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0329 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | KRG042AR | ARE048MD |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0330 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | X1
1-2 | ARE |  |  |  | PN1L522 | ARE061MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0331 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L517 | ARE062MN |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0349 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | PN1L518 | ARE063MN |  | 190 |  |  |  |  | 1PTB |  | 1 |  | M0365 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ARE |  |  |  | 1ARE101CR | ARE030VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | 1ARE102CR | ARE028VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | 1ARE103CR | ARE029VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKA0405 | ARE036VL |  | 71 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKA0406 | ARE247VL |  | 74 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKA0407 | ARE035VL |  | 75 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKA0408 | ARE246VL |  | 70 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKC0408 | ARE245VL |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ARE |  |  |  | LKC0411 | ARE034VL |  | 80 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ASG |  |  |  | LHA0601 | ASG001PO |  | 49 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | ASG |  |  |  | LHB0701 | ASG002PO |  | 76 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | ASG |  |  |  | LKH0202 | ASG032PO |  | 113 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ASG |  |  |  | LLA0312 | ASG012PO |  | 86 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ASG |  |  |  | LLB0310 | ASG022PO |  | 69 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X1
1-2 | ATE |  |  |  | 9LKN0512 | ATE001PO |  | 60 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE004CR | ATE901VL |  | 44 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE005CR | ATE907VL |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE006CR | ATE913VL |  | 24 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE007CR | ATE903VL |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE008CR | ATE909VL |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE009CR | ATE915VL |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE010CR | ATE011PO |  | 200 |  |  |  |  | 3 |  | 2.5 |  | B0054 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE011AR | ATE592SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0030 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
1-2 | ATE |  |  |  | ATE011AR | ATE591SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0035 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
1-2 | ATE |  |  |  | ATE013AR | ATE621SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0031 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
1-2 | ATE |  |  |  | ATE013AR | ATE622SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0032 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
1-2 | ATE |  |  |  | ATE014AR | ATE711SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0033 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
1-2 | ATE |  |  |  | ATE014AR | ATE712SN |  | 18 |  |  |  |  | 3 |  | 2.5 |  | B0034 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 48 Vdc | NO | AR | X1
0 | LZZ |  |  |  | 2LKS0105 | 0LZZ002TR |  | 273 |  |  |  |  | 3 |  | 35 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | SEK |  |  |  | 0SEK001AR | 0SEK001MD |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0900 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
0 | SEK |  |  |  | 0SEK001AR | 0SEK002MD |  | 32 |  |  |  |  | 3 |  | 2.5 |  | B0901 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
1-2 | ATE |  |  |  | LGD0901 | ATE901PO |  | 20 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | ATE |  |  |  | LGD0902 | ATE902PO |  | 20 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | ATE |  |  |  | LGD0903 | ATE903PO |  | 24 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CAP |  |  |  | LKC0511 | CAP004VL |  | 122 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CAP |  |  |  | LKC0512 | CAP008VL |  | 111 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CET |  |  |  | LKC0409 | CET001VV |  | 177 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CET |  |  |  | LKC0410 | CET010VV |  | 185 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CET |  |  |  | LKD0308 | CET001ZV |  | 177 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | CEX004CR | CEX001VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | CEX005CR | CEX007VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | CEX005CR | CEX004CR |  | 17 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | CEX006CR | CEX013VL |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LGA0501 | CEX003PO |  | 64 |  |  |  |  | 3 |  | 240 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CEX |  |  |  | LGA0701 | CEX002PO |  | 17 |  |  |  |  | 3 |  | 240 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CEX |  |  |  | LGA1001 | CEX001PO |  | 57 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CEX |  |  |  | LKA0409 | CEX003VL |  | 112 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LKA0410 | CEX009VL |  | 111 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LKA0610 | CEX015VL |  | 110 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LKF0202 | CEX003RS |  | 123 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LKF0203 | CEX002RS |  | 118 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CEX |  |  |  | LKF0204 | CEX001RS |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | LGE |  |  |  | 9LGE001TR | 9LGE001AR |  | 7 |  |  |  |  | 1 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE001TR | 9LGE001AR |  | 7 |  |  |  |  | 1 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGF001TR | 9LGF001AR |  | 7 |  |  |  |  | 1 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGF001TR | 9LGF001AR |  | 7 |  |  |  |  | 1 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 6.6 kV | NO | SR | L1
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA |  | 19 |  |  |  |  | 2 |  | 16 |  | B0021 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA |  | 1 |  |  |  |  | 2 |  | 16 |  | B0022 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | CFI |  |  |  | CFI001CR | CFI023MO |  | 4 |  |  |  |  | 3 |  | 2.5 |  | B0106 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI001CR | CFI023MO |  | 4 |  |  |  |  | 3 |  | 6 |  | B0107 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI001CR | CFI023MO |  | 7 |  |  |  |  | 3 |  | 6 |  | B0108 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI002CR | CFI024MO |  | 4 |  |  |  |  | 3 |  | 6 |  | B0103 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI002CR | CFI024MO |  | 4 |  |  |  |  | 3 |  | 6 |  | B0104 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI002CR | CFI024MO |  | 4 |  |  |  |  | 3 |  | 2.5 |  | B0105 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI003CR | CFI025MO |  | 25 |  |  |  |  | 3 |  | 6 |  | B0100 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI003CR | CFI025MO |  | 25 |  |  |  |  | 3 |  | 6 |  | B0101 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI003CR | CFI025MO |  | 4 |  |  |  |  | 3 |  | 2.5 |  | B0102 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI015CR | CFI009MO |  | 25 |  |  |  |  | 3 |  | 6 |  | B0043 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI015CR | CFI009MO |  | 7 |  |  |  |  | 3 |  | 6 |  | B0044 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI015CR | CFI010MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0045 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI017CR | CFI011MO |  | 7 |  |  |  |  | 3 |  | 6 |  | B0046 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI017CR | CFI011MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0047 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI017CR | CFI012MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0048 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI019CR | CFI013MO |  | 25 |  |  |  |  | 3 |  | 6 |  | B0049 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI019CR | CFI013MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0050 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI019CR | CFI014MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0051 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI021CR | CFI015MO |  | 7 |  |  |  |  | 3 |  | 6 |  | B0052 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI021CR | CFI015MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0053 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI021CR | CFI016MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0054 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI023CR | CFI017MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0055 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI023CR | CFI017MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0056 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI023CR | CFI018MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0057 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI025CR | CFI019MO |  | 7 |  |  |  |  | 3 |  | 2.5 |  | B0058 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI025CR | CFI019MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0059 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI025CR | CFI020MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0060 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI027CR | CFI021MO |  | 25 |  |  |  |  | 3 |  | 6 |  | B0041 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | CFI027CR | CFI022MO |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0042 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0101 | CFI005PO |  | 65 |  |  |  |  | 3 |  | 16 |  | B0033 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0102 | CFI004PO |  | 53 |  |  |  |  | 3 |  | 16 |  | B0032 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0201 | CFI001CR |  | 38 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0202 | CFI002CR |  | 25 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0203 | CFI003CR |  | 34 |  |  |  |  | 3 |  | 16 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0204 | CFI001PO |  | 60 |  |  |  |  | 3 |  | 2.5 |  | B0029 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0205 | CFI002PO |  | 61 |  |  |  |  | 3 |  | 16 |  | B0030 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0206 | CFI003PO |  | 53 |  |  |  |  | 3 |  | 16 |  | B0031 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0208 | CFI004CR |  | 34 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0402 | CFI006PO |  | 69 |  |  |  |  | 3 |  | 16 |  | B0034 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0403 | CFI001CR |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0404 | CFI002CR |  | 36 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | LKG0405 | CFI003CR |  | 34 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CRF |  |  |  | LGA0101 | CRF003PO |  | 39 |  |  |  |  | 3 |  | 240 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CRF |  |  |  | LGA0201 | CRF002PO |  | 39 |  |  |  |  | 3 |  | 240 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CRF |  |  |  | LGA0401 | CRF001PO |  | 329 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CRF |  |  |  | LKG0210 | CRF004PO |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CRF |  |  |  | LKG0211 | CRF005PO |  | 39 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CRF |  |  |  | LKG0301 | CRF001RS |  | 50 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CRF |  |  |  | LKG0401 | CRF003RS |  | 26 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CRF |  |  |  | LKG0412 | CRF002RS |  | 36 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0212 | CSI001PO |  | 58 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0306 | CSI005VC |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0307 | CSI004VC |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0308 | CSI006PO |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0309 | CSI005PO |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0310 | CSI004PO |  | 41 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0311 | CSI003PO |  | 41 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CSI |  |  |  | LKG0312 | CSI002PO |  | 58 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | CTE |  |  |  | 9CTE102AR | 9CTE001TR |  | 12 |  |  |  |  | 3 |  | 240 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
9 | CTE |  |  |  | 9CTE202AR | 9CTE002TR |  | 13 |  |  |  |  | 3 |  | 240 |  | A0004 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
9 | CTE |  |  |  | 9LGE0601 | 9CTE101AR |  | 417 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
9 | CTE |  |  |  | 9LGF0601 | 9CTE201AR |  | 430 |  |  |  |  | 3 |  | 240 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | CVI |  |  |  | LKB0105 | CVI002PO |  | 119 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKB0107 | CVI001PO |  | 124 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKB0211 | CVI005PO |  | 121 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0105 | CVI004PO |  | 92 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0107 | CVI003PO |  | 86 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0201 | CVI020VA |  | 106 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0202 | CVI019VA |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0203 | CVI006PO |  | 90 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0310 | CVI021VA |  | 103 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0501 | CVI016VA |  | 111 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0502 | CVI013VA |  | 98 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0503 | CVI010VA |  | 104 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0504 | CVI007VA |  | 118 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0505 | CVI046VA |  | 102 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0506 | CVI043VA |  | 103 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CVI |  |  |  | LKC0812 | CVI003VV |  | 116 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | DEG |  |  |  | PN1L312 | DEG044VD |  | 72 |  |  |  |  | 12 |  | 1.5 |  | C0027 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 3
1-2 | DEG |  |  |  | LHA0901 | DEG201CO |  | 221 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | N1
1-2 | DEG |  |  |  | LHA1001 | DEG401CO |  | 222 |  |  |  |  | 3 |  | 50 |  | A0004 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | N1
1-2 | DEG |  |  |  | LHB0901 | DEG101CO |  | 26 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | N1
1-2 | DEG |  |  |  | LHB1001 | DEG301CO |  | 211 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | N1
1-2 | DEG |  |  |  | LLA0107 | DEG008PO |  | 215 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLB0306 | DEG105VD |  | 108 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLB0307 | DEG045VD |  | 133 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLB0308 | DEG013VD |  | 26 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLC0310 | DEG205VD |  | 145 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLD0107 | DEG005PO |  | 152 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLD0311 | DEG305VD |  | 156 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLD0312 | DEG101CR |  | 164 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLE0107 | DEG006PO |  | 170 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLE0303 | DEG405VD |  | 211 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLE0304 | DEG201CR |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLJ0107 | DEG007PO |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DEG |  |  |  | LLJ0312 | DEG301CR |  | 203 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
0 | SEK |  |  |  | 0SEK001AR | 0SEK003MD |  | 33 |  |  |  |  | 3 |  | 2.5 |  | B0902 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | DEL |  |  |  | LLA0105 | DEL001GF |  | 75 |  |  |  |  | 3 |  | 185 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DEL |  |  |  | LLA0105 | DEL001GF |  | 68 |  |  |  |  | 3 |  | 185 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DEL |  |  |  | LLA0309 | DEL001PO |  | 81 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DEL |  |  |  | LLB0107 | DEL002GF |  | 49 |  |  |  |  | 3 |  | 185 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DEL |  |  |  | LLB0107 | DEL002GF |  | 49 |  |  |  |  | 3 |  | 185 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DEL |  |  |  | LLB0302 | DEL002PO |  | 46 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
6 | SSM |  |  |  | 6SSM403AR | 6SSM403ZV |  | 53 |  |  |  |  | 4 |  | 5 |  | B0301 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | DVN |  |  |  | 9DVN002BX | 9DVN002ZV |  | 86 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
9 | DVN |  |  |  | 9DVN005BX | 9DVN005ZV |  | 169 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
9 | REA |  |  |  | 9REA005CR | 9REA003RS |  | 117 |  |  |  |  | 3 |  | 6 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DVC |  |  |  | LKF0412 | DVC010RS |  | 120 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVC |  |  |  | LLA0207 | DVC003ZV |  | 114 |  |  |  |  | 3 |  | 50 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVC |  |  |  | LLA0308 | DVC001ZV |  | 115 |  |  |  |  | 3 |  | 2.5 |  | B0025 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVC |  |  |  | LLB0101 | DVC004ZV |  | 68 |  |  |  |  | 3 |  | 50 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVC |  |  |  | LLB0303 | DVC002ZV |  | 56 |  |  |  |  | 3 |  | 2.5 |  | B0024 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVE |  |  |  | LKC0807 | DVE001CR |  | 85 |  |  |  |  | 2 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0303 | DVE007ZV |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0033 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0304 | DVE005ZV |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0031 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0304 | DVE013ZV |  | 31 |  |  |  |  | 3 |  | 2.5 |  | B0039 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0305 | DVE002ZV |  | 30 |  |  |  |  | 3 |  | 2.5 |  | B0029 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0305 | DVE011ZV |  | 133 |  |  |  |  | 3 |  | 2.5 |  | B0037 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0306 | DVE001ZV |  | 28 |  |  |  |  | 3 |  | 2.5 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLA0306 | DVE009ZV |  | 133 |  |  |  |  | 3 |  | 2.5 |  | B0035 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0301 | DVE003ZV |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0301 | DVE010ZV |  | 63 |  |  |  |  | 3 |  | 2.5 |  | B0034 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0401 | DVE004ZV |  | 19 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0401 | DVE012ZV |  | 63 |  |  |  |  | 3 |  | 2.5 |  | B0036 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0402 | DVE006ZV |  | 33 |  |  |  |  | 3 |  | 2.5 |  | B0030 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLB0402 | DVE008ZV |  | 63 |  |  |  |  | 3 |  | 2.5 |  | B0032 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVE |  |  |  | LLI0308 | DVE014ZV |  | 102 |  |  |  |  | 3 |  | 2.5 |  | B0041 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | E1
1-2 | DVF |  |  |  | LLA0302 | DVF001ZV |  | 90 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | CUS |  | 380 Vac | NO | NSA | E1
1-2 | DVF |  |  |  | LLB0403 | DVF002ZV |  | 94 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | CUS |  | 380 Vac | NO | NSA | E1
1-2 | DVG |  |  |  | LKE0304 | DVG001RS |  | 95 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVG |  |  |  | LLI0306 | DVG003ZV |  | 80 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVG |  |  |  | LLI0307 | DVG001ZV |  | 74 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | G1
1-2 | DVG |  |  |  | LLI0412 | DVG003ZV |  | 77 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVG |  |  |  | LLJ0310 | DVG004ZV |  | 120 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVG |  |  |  | LLJ0311 | DVG002ZV |  | 108 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVG |  |  |  | LLJ0411 | DVG004ZV |  | 105 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | G1
1-2 | DVH |  |  |  | LLA0103 | DVH001ZV |  | 108 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | H1
1-2 | DVH |  |  |  | LLB0105 | DVH002ZV |  | 38 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | H1
1-2 | DVK |  |  |  | KRG024AR | DVK100MP |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0100 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | K1
1-2 | DVK |  |  |  | KRG013AR | DVK101MP |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0101 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | K1
1-2 | DVK |  |  |  | LKD0201 | DVK004ZV |  | 255 |  |  |  |  | 3 |  | 70 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LKD0203 | DVK002ZV |  | 254 |  |  |  |  | 3 |  | 50 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LKF0103 | DVK003ZV |  | 255 |  |  |  |  | 3 |  | 70 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LKF0105 | DVK001ZV |  | 238 |  |  |  |  | 3 |  | 50 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LKF0408 | DVK005RS |  | 263 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LLI0304 | DVK005ZV |  | 253 |  |  |  |  | 3 |  | 6 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LLI0305 | DVK003RS |  | 245 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LLJ0308 | DVK006ZV |  | 202 |  |  |  |  | 3 |  | 6 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
1-2 | DVK |  |  |  | LLJ0309 | DVK002RS |  | 203 |  |  |  |  | 3 |  | 35 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K2
9 | REA |  |  |  | 9REA005CR | 9REA004RS |  | 66 |  |  |  |  | 3 |  | 6 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DVL |  |  |  | LKH0301 | DVL103RS |  | 83 |  |  |  |  | 3 |  | 2.5 |  | B0020 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LKH0302 | DVL102RS |  | 82 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLA0401 | DVL101ZV |  | 56 |  |  |  |  | 3 |  | 2.5 |  | B0021 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLA0402 | DVL102ZV |  | 60 |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLA0403 | DVL103ZV |  | 30 |  |  |  |  | 3 |  | 2.5 |  | B0025 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLA0404 | DVL201ZV |  | 81 |  |  |  |  | 3 |  | 16 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLA0405 | DVL202ZV |  | 77 |  |  |  |  | 3 |  | 16 |  | B0029 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLB0406 | DVL104ZV |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0022 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLB0407 | DVL204ZV |  | 68 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLB0408 | DVL203ZV |  | 73 |  |  |  |  | 3 |  | 6 |  | B0024 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVL |  |  |  | LLE001TB | DVL002JS |  | 82 |  |  |  |  | 3 |  | 6 |  | B0900 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
9 | REA |  |  |  | 9REA005CR | 9REA005RS |  | 22 |  |  |  |  | 3 |  | 6 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
9 | REA |  |  |  | 9REA005CR | 9REA006RS |  | 25 |  |  |  |  | 3 |  | 6 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
9 | REA |  |  |  | 9REA005CR | 9REA007RS |  | 26 |  |  |  |  | 3 |  | 6 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
9 | SDA |  |  |  | ATE102AR | 9SDA162MG |  | 67 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
1-2 | DVN |  |  |  | LKJ0103 | DVN007ZV |  | 75 |  |  |  |  | 3 |  | 70 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DVN |  |  |  | LKJ0401 | DVN035ZV |  | 78 |  |  |  |  | 3 |  | 6 |  | B0017 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DVS |  |  |  | LLA0406 | DVS001ZV |  | 220 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLA0407 | DVS003ZV |  | 212 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLA0408 | DVS005ZV |  | 232 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLA0409 | DVS007ZV |  | 209 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLB0409 | DVS002ZV |  | 145 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLB0410 | DVS004ZV |  | 130 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLB0411 | DVS006ZV |  | 138 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVS |  |  |  | LLB0412 | DVS008ZV |  | 133 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | DVW |  |  |  | LKH0401 | DVW003RS |  | 122 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DVW |  |  |  | LKH0402 | DVW003ZV |  | 123 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DVW |  |  |  | LLA0410 | DVW001RS |  | 153 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DVW |  |  |  | LLB0512 | DVW002RS |  | 99 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DVW |  |  |  | LLC0307 | DVW001ZV |  | 174 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DVW |  |  |  | LLD0307 | DVW002ZV |  | 133 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | W1
1-2 | DWS |  |  |  | LLA0307 | DWS003ZV |  | 294 |  |  |  |  | 3 |  | 16 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | DWS |  |  |  | LLB0304 | DWS004ZV |  | 230 |  |  |  |  | 3 |  | 16 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | DWS |  |  |  | LLD0305 | DWS002RS |  | 242 |  |  |  |  | 3 |  | 35 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | DWS |  |  |  | LLI0403 | DWS001RS |  | 298 |  |  |  |  | 3 |  | 35 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | DWS |  |  |  | LLI0404 | DWS001ZV |  | 297 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | DWS |  |  |  | LLJ0307 | DWS002ZV |  | 266 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | X2
1-2 | EAS |  |  |  | PN1L528 | DVK005MT |  | 71 |  |  |  |  | 1PTB |  | 1 |  | M0003 | [16 empty] | Significant | [11 empty] | M | PVC VZBA |  | 30 Vdc | NO | SR | 2
1-2 | EAS |  |  |  | PN1L528 | DVK006MT |  | 74 |  |  |  |  | 1PTB |  | 1 |  | M0004 | [16 empty] | Significant | [11 empty] | M | PVC VZBA |  | 30 Vdc | NO | SR | 2
1-2 | EAS |  |  |  | LHA0201 | EAS001PO |  | 229 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | K1
1-2 | EAS |  |  |  | LHB0201 | EAS002PO |  | 147 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | K1
1-2 | EAS |  |  |  | LLC0301 | EAS131VB |  | 259 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLC0302 | EAS013VB |  | 249 |  |  |  |  | 3 |  | 6 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLC0303 | EAS009VB |  | 263 |  |  |  |  | 3 |  | 6 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLC0304 | EAS007VB |  | 260 |  |  |  |  | 3 |  | 6 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLC0305 | EAS001VB |  | 258 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLC0401 | EAS133VB |  | 255 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0301 | EAS014VB |  | 157 |  |  |  |  | 3 |  | 6 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0302 | EAS010VB |  | 163 |  |  |  |  | 3 |  | 6 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0303 | EAS008VB |  | 161 |  |  |  |  | 3 |  | 6 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0304 | EAS002VB |  | 154 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0401 | EAS132VB |  | 156 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EAS |  |  |  | LLD0402 | EAS134VB |  | 156 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | EBA |  |  |  | EBA001CR | EBA001VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0601 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 3
1-2 | EBA |  |  |  | EBA001CR | EBA003VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0602 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 3
1-2 | EBA |  |  |  | EBA001CR | EBA013VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0603 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 19 |  | 1.5 |  | C0604 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | EBA001CR | EBA015VA |  | 85 |  |  |  |  | 12 |  | 1.5 |  | C0606 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 20 |  |  |  |  | 2 |  | 1.5 |  | C0607 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001TO |  | 70 |  |  |  |  | 2 |  | 1.5 |  | C0609 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 85 |  |  |  |  | 2 |  | 6 |  | C0610 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 76 |  |  |  |  | 2 |  | 6 |  | C0611 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0612 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0613 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0614 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0615 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0616 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | PN1L312 | EBA001CR |  | 70 |  |  |  |  | 2 |  | 6 |  | C0617 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EBA |  |  |  | EBA007CR | EBA006VA |  | 70 |  |  |  |  | 7 |  | 1.5 |  | C0619 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | EBA007CR | EBA007VA |  | 70 |  |  |  |  | 2 |  | 7 |  | C0620 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | EBA007CR | EBA008VA |  | 115 |  |  |  |  | 2 |  | 7 |  | C0621 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | EBA007CR | EBA009VA |  | 20 |  |  |  |  | 2 |  | 7 |  | C0622 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | PN1L312 | EBA007CR |  | 20 |  |  |  |  | 19 |  | 1.5 |  | C0627 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | EBA007CR | EBA006VA |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0698 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 2
1-2 | EBA |  |  |  | PN1L343 | EBA002TO |  | 20 |  |  |  |  | 2 |  | 1.5 |  | C0710 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP002CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0312 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | EPP |  |  |  | PN1L526 | EPP002CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0313 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | EPP |  |  |  | PN1L526 | EPP002CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0314 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | EPP |  |  |  | PN1L526 | EPP003CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0327 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP003CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0328 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP003CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0329 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP004CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0338 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP004CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0339 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP005CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0350 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP005CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0351 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP006CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0362 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP006CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0363 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP006CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0364 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | EPP |  |  |  | PN1L526 | EPP007CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0378 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP007CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0379 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP007CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0380 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP007CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0381 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP008CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0397 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP008CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0398 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP008CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0399 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP008CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0400 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP009CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0401 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP009CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0415 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP009CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0416 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP009CR |  | 20 |  |  |  |  | 8PTB |  | 1 |  | M0417 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | EPP |  |  |  | PN1L526 | EPP007CR |  | 20 |  |  |  |  | 2PTB |  | 1 |  | M0421 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
9 | SDA |  |  |  | ATE102AR | 9SDA301MG |  | 48 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDA |  |  |  | ATE102AR | 9SDA391MG |  | 51 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX101BN | 9SDX035RS |  | 9 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX101BN | 9SDX036RS |  | 11 |  |  |  |  | 3 |  | 2.5 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX102BN | 9SDX037RS |  | 12 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX102BN | 9SDX038RS |  | 13 |  |  |  |  | 3 |  | 2.5 |  | B0029 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX002CR | 9SDX091RS |  | 11 |  |  |  |  | 3 |  | 50 |  | B0030 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX002CR | 9SDX092RS |  | 14 |  |  |  |  | 3 |  | 50 |  | B0031 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX002CR | 9SDX093RS |  | 7 |  |  |  |  | 3 |  | 50 |  | B0032 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX001AR | 9SDX231MG |  | 22 |  |  |  |  | 3 |  | 2.5 |  | B0043 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX001AR | 9SDX232MG |  | 106 |  |  |  |  | 3 |  | 2.5 |  | B0044 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX001AR | 9SDX233MG |  | 10 |  |  |  |  | 3 |  | 2.5 |  | B0047 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDX001AR | 9SDX234MG |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0048 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X1
9 | SDA |  |  |  | ATE102AR | 9SER001VD |  | 60 |  |  |  |  | 3 |  | 2.5 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDA |  |  |  | ATE102AR | 9SER002VD |  | 45 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDA |  |  |  | ATE102AR | 9SER005VD |  | 63 |  |  |  |  | 3 |  | 2.5 |  | B0029 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | EPP |  |  |  | LLB0609 | EPP101AR |  | 95 |  |  |  |  | 2 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | LLB0611 | EPP201AR |  | 242 |  |  |  |  | 2 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | ETY |  |  |  | PN1L311 | ETY043VA |  | 36 |  |  |  |  | 12 |  | 1.5 |  | C0633 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | ETY |  |  |  | PN1L311 | ETY044VA |  | 36 |  |  |  |  | 12 |  | 1.5 |  | C0634 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | ETY |  |  |  | PN1L527 | ETY001MT |  | 134 |  |  |  |  | 1TTB |  | 1 |  | M0001 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 4
1-2 | ETY |  |  |  | PN1L527 | ETY002MT |  | 151 |  |  |  |  | 1TTB |  | 1 |  | M0002 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 4
1-2 | ETY |  |  |  | PN1L527 | ETY003MT |  | 106 |  |  |  |  | 1TTB |  | 1 |  | M0003 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | ETY |  |  |  | PN1L527 | ETY004MT |  | 108 |  |  |  |  | 1TTB |  | 1 |  | M0004 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | ETY |  |  |  | PN1L513 | ETY101MP |  | 28 |  |  |  |  | 1PTB |  | 1 |  | M0300 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ETY |  |  |  | PN1L529 | ETY102MP |  | 34 |  |  |  |  | 1PTB |  | 1 |  | M0302 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ETY |  |  |  | PN1L515 | ETY103MP |  | 33 |  |  |  |  | 1PTB |  | 1 |  | M0304 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 2
1-2 | ETY |  |  |  | PN1L533 | ETY104MP |  | 39 |  |  |  |  | 1PTB |  | 1 |  | M0305 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 2
1-2 | ETY |  |  |  | PN1L529 | ETY202MP |  | 40 |  |  |  |  | 1PTB |  | 1 |  | M0904 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | ETY |  |  |  | PN1L513 | ETY201MP |  | 18 |  |  |  |  | 1PTB |  | 1 |  | M0905 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 2
1-2 | ETY |  |  |  | LKH0403 | ETY001RS |  | 233 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 2
1-2 | ETY |  |  |  | LLI0406 | ETY001ZV |  | 276 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 2
1-2 | ETY |  |  |  | LLJ0305 | ETY002ZV |  | 215 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 2
1-2 | EVC |  |  |  | PN1L528 | EVC011MT |  | 60 |  |  |  |  | 1PTB |  | 1 |  | M0001 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC012MT |  | 69 |  |  |  |  | 1PTB |  | 1 |  | M0002 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC013MT |  | 68 |  |  |  |  | 1PTB |  | 1 |  | M0003 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC014MT |  | 68 |  |  |  |  | 1PTB |  | 1 |  | M0004 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC021MT |  | 64 |  |  |  |  | 1PTB |  | 1 |  | M0005 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC022MT |  | 59 |  |  |  |  | 1PTB |  | 1 |  | M0006 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC023MT |  | 50 |  |  |  |  | 1PTB |  | 1 |  | M0007 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC024MT |  | 50 |  |  |  |  | 1PTB |  | 1 |  | M0008 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC031MT |  | 62 |  |  |  |  | 1PTB |  | 1 |  | M0009 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC032MT |  | 60 |  |  |  |  | 1PTB |  | 1 |  | M0010 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC033MT |  | 61 |  |  |  |  | 1PTB |  | 1 |  | M0011 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L528 | EVC034MT |  | 62 |  |  |  |  | 1PTB |  | 1 |  | M0012 | [16 empty] | Economic | [11 empty] | M | VZBA |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L527 | EVC041MT |  | 73 |  |  |  |  | 1TTB |  | 1 |  | M0013 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVC |  |  |  | PN1L527 | EVC042MT |  | 69 |  |  |  |  | 1TTB |  | 1 |  | M0014 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVC |  |  |  | PN1L527 | EVC043MT |  | 75 |  |  |  |  | 1TTB |  | 1 |  | M0015 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVC |  |  |  | PN1L527 | EVC044MT |  | 53 |  |  |  |  | 1TTB |  | 1 |  | M0016 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVC |  |  |  | PN1L527 | EVC045MT |  | 64 |  |  |  |  | 1TTB |  | 1 |  | M0017 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 3
1-2 | EVC |  |  |  | PN1L527 | EVC046MT |  | 68 |  |  |  |  | 1TTB |  | 1 |  | M0018 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVC |  |  |  | PN1L527 | EVC047MT |  | 68 |  |  |  |  | 1TTB |  | 1 |  | M0019 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC048MT |  | 62 |  |  |  |  | 1TTB |  | 1 |  | M0020 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC049MT |  | 66 |  |  |  |  | 1TTB |  | 1 |  | M0021 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC050MT |  | 70 |  |  |  |  | 1TTB |  | 1 |  | M0022 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC051MT |  | 56 |  |  |  |  | 1TTB |  | 1 |  | M0023 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC052MT |  | 64 |  |  |  |  | 1TTB |  | 1 |  | M0024 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVC |  |  |  | PN1L527 | EVC053MT |  | 65 |  |  |  |  | 1TTB |  | 1 |  | M0025 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVR |  |  |  | PN1L527 | EVR004MT |  | 109 |  |  |  |  | 1TTB |  | 1 |  | M0001 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVR |  |  |  | PN1L527 | EVR005MT |  | 102 |  |  |  |  | 1TTB |  | 1 |  | M0002 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR006MT |  | 64 |  |  |  |  | 1TTB |  | 1 |  | M0003 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR007MT |  | 69 |  |  |  |  | 1TTB |  | 1 |  | M0004 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR008MT |  | 98 |  |  |  |  | 1TTB |  | 1 |  | M0005 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR009MT |  | 59 |  |  |  |  | 1TTB |  | 1 |  | M0006 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR010MT |  | 68 |  |  |  |  | 1TTB |  | 1 |  | M0007 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 6
1-2 | EVR |  |  |  | PN1L527 | EVR011MT |  | 67 |  |  |  |  | 1TTB |  | 1 |  | M0008 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 4
1-2 | EVR |  |  |  | PN1L527 | EVR012MT |  | 71 |  |  |  |  | 1TTB |  | 1 |  | M0009 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 4
1-2 | EVR |  |  |  | PN1L527 | EVR013MT |  | 86 |  |  |  |  | 1TTB |  | 1 |  | M0010 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVR |  |  |  | PN1L527 | EVR014MT |  | 73 |  |  |  |  | 1TTB |  | 1 |  | M0011 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | EVR |  |  |  | PN1L527 | EVR015MT |  | 85 |  |  |  |  | 1TTB |  | 1 |  | M0012 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | GCT |  |  |  | GCT002BC | GCT004EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0034 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT002BC | GCT008EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0036 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT002BC | GCT012EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0038 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT002BC | GCT016EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0040 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT004BC | GCT052EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0042 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT004BC | GCT056EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0044 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT004BC | GCT060EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0046 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT004BC | GCT064EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0048 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT006BC | GCT036EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0050 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT006BC | GCT040EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0052 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT006BC | GCT044EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0054 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT006BC | GCT048EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0056 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT008BC | GCT020EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0058 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT008BC | GCT024EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0060 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT008BC | GCT028EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0062 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT008BC | GCT032EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0064 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT003BC | GCT066EL |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0109 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT001BC | GCT001EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0115 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT001BC | GCT003EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0117 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT001BC | GCT005EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0119 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT001BC | GCT007EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0121 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT005BC | GCT009EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0123 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT005BC | GCT011EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0125 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT005BC | GCT013EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0127 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT005BC | GCT015EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0129 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT009BC | GCT065EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0131 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT007BC | GCT057EL |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0137 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCTO07BC | GCT059EL |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0139 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT007BC | GCT061EL |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0141 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT007BC | GCT063EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0143 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT011BC | GCT049EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0145 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT011BC | GCT051EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0147 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT011BC | GCT053EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0149 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT011BC | GCT055EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0151 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | LLI0407 | GCT130VV |  | 108 |  |  |  |  | 12 |  | 1.5 |  | C0266 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | YES | AR | V1
1-2 | GCT |  |  |  | LLC0405 | GCT129VV |  | 112 |  |  |  |  | 12 |  | 1.5 |  | C0270 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | YES | AR | V1
1-2 | GCT |  |  |  | LLA0510 | GCT128VV |  | 111 |  |  |  |  | 12 |  | 1.5 |  | C0274 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | YES | AR | V1
1-2 | GCT |  |  |  | GCT015BC | GCT002EL |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0277 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT013BC | GCT033EL |  | 233 |  |  |  |  | 3 |  | 1.5 |  | C0283 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT013BC | GCT035EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0285 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT021BC | GCT023EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0286 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT013BC | GCT037EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0287 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT021BC | GCT021EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0288 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT013BC | GCT039EL |  | 25 |  |  |  |  | 3 |  | 1.5 |  | C0289 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT021BC | GCT019EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0290 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT017BC | GCT041EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0291 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT021BC | GCT017EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0292 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT017BC | GCT043EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0293 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT019BC | GCT031EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0294 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT017BC | GCT045EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0295 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT019BC | GCT029EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0296 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT017BC | GCT047EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0297 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT019BC | GCT027EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0298 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT019BC | GCT025EL |  | 15 |  |  |  |  | 3 |  | 1.5 |  | C0299 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | X1
1-2 | GCT |  |  |  | GCT005UB | GCT131VV |  | 67 |  |  |  |  | 12 |  | 1.5 |  | C0319 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | GCT |  |  |  | GCT005UB | GCT132VV |  | 64 |  |  |  |  | 12 |  | 1.5 |  | C0320 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | GCT |  |  |  | KPR003BN | GCT131VV |  | 81 |  |  |  |  | 1PTB |  | 1 |  | M0312 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | GCT |  |  |  | KPR003BN | GCT132VV |  | 69 |  |  |  |  | 1PTB |  | 1 |  | M0313 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | GCT |  |  |  | KPR003BN | GCT133VV |  | 79 |  |  |  |  | 1PTB |  | 1 |  | M0314 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | GCT |  |  |  | GCT005UB | GCT133VV |  | 81 |  |  |  |  | 12 |  | 1.5 |  | C0321 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | V1
1-2 | GCT |  |  |  | LKH0404 | GCT100VV |  | 156 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GCT |  |  |  | LKH0405 | GCT101VV |  | 151 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GCT |  |  |  | LKH0406 | GCT102VV |  | 156 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GCT |  |  |  | LKH0407 | GCT103VV |  | 150 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GCT |  |  |  | LLA0510 | GCT128VV |  | 95 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | V1
1-2 | GCT |  |  |  | LLC0405 | GCT129VV |  | 78 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | V1
1-2 | GCT |  |  |  | LLI0407 | GCT130VV |  | 120 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | V1
1-2 | GEV |  |  |  | GEV002CR | GEV011AR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GEV |  |  |  | GEV002CR | GEV012AR |  | 16 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GEV |  |  |  | GEV002CR | GEV013AR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GEV |  |  |  | LKE0105 | GEV001CR |  | 184 |  |  |  |  | 3 |  | 150 |  | B0021 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEV |  |  |  | LKE0105 | GEV001CR |  | 169 |  |  |  |  | 3 |  | 150 |  | B0022 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEV |  |  |  | LKF0506 | GEV004AR |  | 146 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEV |  |  |  | LKH0411 | GEV002CR |  | 155 |  |  |  |  | 3 |  | 16 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX001AR | GEX002AR |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX001TR | GEX002TR |  | 18 |  |  |  |  | 1 |  | 185 |  | B0604 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX001TR | GEX002TR |  | 18 |  |  |  |  | 1 |  | 185 |  | B0606 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX001TR | GEX003TR |  | 18 |  |  |  |  | 1 |  | 185 |  | B0608 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX002AP | GEX001AR |  | 47 |  |  |  |  | 1 |  | 300 |  | B0601 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX002AP | GEX001AR |  | 43 |  |  |  |  | 4 |  | 300 |  | B0602 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX002TR | GEX003TR |  | 15 |  |  |  |  | 1 |  | 185 |  | B0605 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX002TR | GEX003TR |  | 19 |  |  |  |  | 1 |  | 185 |  | B0607 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX003AP | GEX001AR |  | 42 |  |  |  |  | 1 |  | 6 |  | B0603 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX003TR | GEX001AR |  | 26 |  |  |  |  | 1 |  | 185 |  | B0611 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX020CR | GEX001AR |  | 26 |  |  |  |  | 1 |  | 185 |  | B0609 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX020CR | GEX001AR |  | 26 |  |  |  |  | 1 |  | 185 |  | B0610 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | GEX020CR | GEX001AR |  | 28 |  |  |  |  | 1 |  | 185 |  | B0612 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GEX |  |  |  | LKC0610 | GEX004TR |  | 106 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GFR |  |  |  | LKA0209 | GFR003PO |  | 116 |  |  |  |  | 3 |  | 185 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GFR |  |  |  | LKA0504 | GFR001PO |  | 129 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GFR |  |  |  | LKC0209 | GFR004PO |  | 128 |  |  |  |  | 3 |  | 185 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GFR |  |  |  | LKC0712 | GFR002PO |  | 137 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001AR | GGR020MO |  | 1 |  |  |  |  | 1 |  | 300 |  | B0020 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001AR | GGR020MO |  | 1 |  |  |  |  | 1 |  | 300 |  | B0021 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001AR | GGR020MO |  | 1 |  |  |  |  | 1 |  | 300 |  | B0022 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001AR | GGR059CR |  | 116 |  |  |  |  | 1 |  | 300 |  | B0027 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001GA | GGR059CR |  | 120 |  |  |  |  | 4 |  | 25 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR001GA | GGR059CR |  | 108 |  |  |  |  | 4 |  | 25 |  | B0024 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR002BX | GGR002PO |  | 5 |  |  |  |  | 3 |  | 150 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR010BX | GGR010PO |  | 5 |  |  |  |  | 3 |  | 185 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR011BX | GGR011PO |  | 5 |  |  |  |  | 3 |  | 185 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR059CR | GGR001MO |  | 2 |  |  |  |  | 4 |  | 25 |  | B0025 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | GGR059CR | GGR001MO |  | 2 |  |  |  |  | 4 |  | 25 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | LGB0101 | GGR001TR |  | 137 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | X1
1-2 | GGR |  |  |  | LKA0503 | GGR009ZV |  | 107 |  |  |  |  | 3 |  | 6 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | LKF0511 | GGR204VN |  | 139 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | LKF0512 | GGR012PO |  | 165 |  |  |  |  | 3 |  | 6 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GGR |  |  |  | LKH0409 | GGR022ZV |  | 131 |  |  |  |  | 3 |  | 16 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GHE |  |  |  | LKE0302 | GHE006ZV |  | 129 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GHE |  |  |  | LKE0303 | GHE005PO |  | 136 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GHE |  |  |  | LKH0410 | GHE001PO |  | 85 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GHE |  |  |  | LLI0408 | GHE003PO |  | 141 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GPV |  |  |  | LKC0707 | GPV055VV |  | 136 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GPV |  |  |  | LKC0708 | GPV054VV |  | 149 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GPV |  |  |  | LKC0709 | GPV053VV |  | 149 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GPV |  |  |  | LKC0710 | GPV052VV |  | 149 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GPV |  |  |  | LKC0711 | GPV051VV |  | 144 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA |  | 1 |  |  |  |  | 2 |  | 6 |  | B0023 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | GSE |  |  |  | KRG033AR | GSE023MP |  | 103 |  |  |  |  | 1PTB |  | 1 |  | M0300 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | X1
1-2 | GSE |  |  |  | KRG042AR | GSE024MP |  | 107 |  |  |  |  | 1PTB |  | 1 |  | M0301 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | X1
1-2 | GSE |  |  |  | DNLG151BC | GSE002AR |  | 30 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE003AR | GRE002AR |  | 40 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE003AR | GRE002AR |  | 40 |  |  |  |  | 2 |  | 16 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GRE002AR |  | 21 |  |  |  |  | 2 |  | 16 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GSE003AR |  | 50 |  |  |  |  | 2 |  | 35 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GSE003AR |  | 51 |  |  |  |  | 2 |  | 35 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GSE003AR |  | 40 |  |  |  |  | 2 |  | 35 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GSE003AR |  | 40 |  |  |  |  | 2 |  | 35 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | GSE005AR | GSE003AR |  | 66 |  |  |  |  | 4 |  | 35 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | LKA0501 | GSE003AR |  | 54 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSE |  |  |  | LKA0501 | GSE003AR |  | 54 |  |  |  |  | 3 |  | 16 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0701 | GSS122VV |  | 120 |  |  |  |  | 2.5 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0702 | GSS121VV |  | 173 |  |  |  |  | 2.5 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0703 | GSS006VV |  | 141 |  |  |  |  | 2.5 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0704 | GSS005VV |  | 141 |  |  |  |  | 2.5 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0705 | GSS002VV |  | 121 |  |  |  |  | 2.5 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0706 | GSS001VV |  | 146 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0801 | GSS221VV |  | 112 |  |  |  |  | 2.5 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSS |  |  |  | LKC0802 | GSS222VV |  | 128 |  |  |  |  | 2.5 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GST |  |  |  | LKE0209 | GST001PO |  | 132 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GST |  |  |  | LKF0509 | GST002RS |  | 141 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GST |  |  |  | LKF0510 | GST001RS |  | 145 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GST |  |  |  | LKS0209 | GST002PO |  | 114 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSY |  |  |  | GSY003AR | GSY101JS |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GSY |  |  |  | GSY003AR | GSY201JS |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GSY |  |  |  | GSY003AR | GSY301JS |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | GSY |  |  |  | LKB0203 | GSY001MO |  | 162 |  |  |  |  | 3 |  | 50 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSY |  |  |  | LKB0309 | GSY006ZV |  | 175 |  |  |  |  | 3 |  | 6 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSY |  |  |  | LKB0310 | GSY007ZV |  | 176 |  |  |  |  | 3 |  | 6 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | GSY |  |  |  | LKC0103 | GSY002MO |  | 107 |  |  |  |  | 3 |  | 50 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | JPP |  |  |  | JPP001BX | JPP001PO |  | 25 |  |  |  |  | 3 |  | 185 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | JPP |  |  |  | JPP002BX | JPP002PO |  | 23 |  |  |  |  | 3 |  | 185 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | JPP |  |  |  | LLE0701 | JPP002VE |  | 321 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | KRG |  |  |  | KRG024CR | KRG023AR |  | 6 |  |  |  |  | 3 |  | 2.5 |  | B0900 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | C1
1-2 | KRG |  |  |  | KRG032AR | KRG031AR |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0308 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | C1
1-2 | KRG |  |  |  | KRG032AR | KRG034AR |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0309 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | C1
1-2 | KRG |  |  |  | KRG035CR | KRG034AR |  | 6 |  |  |  |  | 3 |  | 2.5 |  | B0901 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | C1
1-2 | KRG |  |  |  | KRG046CR | KRG042AR |  | 6 |  |  |  |  | 3 |  | 2.5 |  | B0902 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | C1
1-2 | KRT |  |  |  | KRT129CR | KRT055MA |  | 42 |  |  |  |  | 2 |  | 6 |  | C0933 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT129CR | KRT056MA |  | 35 |  |  |  |  | 3 |  | 1.5 |  | C0934 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT129CR | KRT057MA |  | 27 |  |  |  |  | 2 |  | 6 |  | C0935 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT129CR | KRT055MA |  | 42 |  |  |  |  | 3 |  | 1.5 |  | C0936 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT129CR | KRT056MA |  | 35 |  |  |  |  | 2 |  | 6 |  | C0937 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT129CR | KRT057MA |  | 27 |  |  |  |  | 3 |  | 1.5 |  | C0938 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | PN1L528 | KRT022MA |  | 60 |  |  |  |  | 1 |  | 1.83 |  | M0720 | [16 empty] | Significant | [11 empty] | M | PRECICABLE |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | PN1L528 | KRT022MA |  | 60 |  |  |  |  | 1 |  | 1.83 |  | M0721 | [16 empty] | Significant | [11 empty] | M | PRECICABLE |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | PN1L528 | KRT023MA |  | 60 |  |  |  |  | 1 |  | 1.83 |  | M0730 | [16 empty] | Significant | [11 empty] | M | PRECICABLE |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | PN1L528 | KRT023MA |  | 60 |  |  |  |  | 1 |  | 1.83 |  | M0731 | [16 empty] | Significant | [11 empty] | M | PRECICABLE |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | KRT023CR | KRT011MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1031 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | PN1L527 | KRT023CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1032 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | KRT024CR | KRT012MA |  | Site Run |  |  |  |  | 2 and 8 |  | 2,5 and 1,5 |  | M1034 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | PMC003CR | KRT024CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1035 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | KRT |  |  |  | KRT027CR | KRT013MA |  | Site Run |  |  |  |  | 2 and 8 |  | 2,5 and 1,5 |  | M1039 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | KRT |  |  |  | KRT074CR | KRT027CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1040 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | KRT |  |  |  | KRT028CR | KRT014MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1043 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | KRT |  |  |  | KRT014IK | KRT028CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1044 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | KRT |  |  |  | KRT046CR | KRT041MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1065 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | KRT |  |  |  | KRT049CR | KRT050MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1068 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | KRT |  |  |  | KRT050CR | KRT051MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1070 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | KRT |  |  |  | KRT054CR | KRT055MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1078 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT055IK | KRT054CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1079 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | KRT |  |  |  | KRT055CR | KRT056MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1080 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT056IK | KRT055CR |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1081 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | KRT |  |  |  | KRT056CR | KRT057MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1082 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | V1
1-2 | KRT |  |  |  | KRT057IK | KRT056MA |  | Site Run |  |  |  |  | 1PTB |  | 0.5 |  | M1083 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
9 | KRT |  |  |  | 9KRT501AR | KRT001TB |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0798 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | X1
9 | KRT |  |  |  | 9KRT566CR | 9DSNB02CR |  | 66 |  |  |  |  | 2 |  | 2.5 |  | B0023 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | KRT |  |  |  | KRT001TB | KRT002AR |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0799 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | KRT |  |  |  | KRT010CR | KRT028CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1030 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | K1
1-2 | KRT |  |  |  | KRT010CR | KRT054CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1052 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | W1
1-2 | KRT |  |  |  | KRT010CR | KRT055CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1053 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | W1
1-2 | KRT |  |  |  | KRT010CR | KRT056CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1054 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | W1
1-2 | KRT |  |  |  | KRT074CR | KRT027CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1029 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | K1
1-2 | KRT |  |  |  | LLA0501 | KRT001TB |  | 91 |  |  |  |  | 2 |  | 6 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | KRT |  |  |  | LMA027JA | KRT003AR |  | 107 |  |  |  |  | 2 |  | 2.5 |  | B0904 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | KRT |  |  |  | PMC003CT | KRT024CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1026 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | 3
1-2 | KRT |  |  |  | PN1L320 | KRT023CR |  | Site Run |  |  |  |  | 3 |  | 0.6 |  | B1022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | LAA |  |  |  | LAA0231 | LNE002DL |  | 29 |  |  |  |  | 2 |  | 70 |  | B0023 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LAA0231 | LNE002DL |  | 29 |  |  |  |  | 2 |  | 70 |  | B0024 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LAA0232 | LNE003DL |  | 29 |  |  |  |  | 2 |  | 70 |  | B0025 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LAA0232 | LNE003DL |  | 29 |  |  |  |  | 2 |  | 70 |  | B0026 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LAA0242 | LNE001DL |  | 27 |  |  |  |  | 2 |  | 70 |  | B0021 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LAA0242 | LNE001DL |  | 30 |  |  |  |  | 2 |  | 70 |  | B0022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAA |  |  |  | LLE0105 | LCA |  | 69 |  |  |  |  | 3 |  | 150 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LAA |  |  |  | LLE0105 | LAA001RD |  | 70 |  |  |  |  | 3 |  | 150 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LAA |  |  |  | LLI0107 | LAA002RD |  | 33 |  |  |  |  | 3 |  | 150 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LAA |  |  |  | LLI0107 | LAA002RD |  | 32 |  |  |  |  | 3 |  | 150 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LAB |  |  |  | LAB03 | GGR004PO |  | 33 |  |  |  |  | 1 |  | 185 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | AR | L1
1-2 | LAB |  |  |  | LAB03 | GGR004PO |  | 37 |  |  |  |  | 1 |  | 185 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | AR | L1
1-2 | LAB |  |  |  | LAB03 | GGR004PO |  | 37 |  |  |  |  | 2 |  | 6 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | AR | L1
1-2 | LAB |  |  |  | LLI0105 | LAB001RD |  | 87 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | LAC |  |  |  | LAC03 | GHE004PO |  | 44 |  |  |  |  | 2 |  | 35 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAC |  |  |  | LAC03 | GHE004PO |  | 48 |  |  |  |  | 2 |  | 16 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAC |  |  |  | LAC04 | GGR003PO |  | 36 |  |  |  |  | 1 |  | 185 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAC |  |  |  | LAC04 | GGR003PO |  | 36 |  |  |  |  | 1 |  | 185 |  | B0014 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAC |  |  |  | LAC04 | GGR003PO |  | 36 |  |  |  |  | 2 |  | 16 |  | B0015 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LAC |  |  |  | LKH0105 | LAC001RD |  | 46 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | LAC |  |  |  | LKH0105 | LAC001RD |  | 42 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LBA |  |  |  | LLC0407 | LBA002RD |  | 32 |  |  |  |  | 3 |  | 70 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBA |  |  |  | LLE0401 | LBA001RD |  | 70 |  |  |  |  | 3 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LBB |  |  |  | LLB0509 | LBB001RD |  | 40 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBB |  |  |  | LLD0405 | LBB002RD |  | 55 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBC |  |  |  | LLA0509 | LBC001RD |  | 57 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBD |  |  |  | LLB0508 | LBD001RD |  | 44 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBE |  |  |  | LLA0508 | LBE001RD |  | 44 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBF |  |  |  | LLB0507 | LBF001RD |  | 60 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBJ |  |  |  | LLC0409 | LBJ001RD |  | 30 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LBJ |  |  |  | LLI0409 | LBJ002RD |  | 40 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LCA |  |  |  | LLA0506 | LCA001RD |  | 68 |  |  |  |  | 3 |  | 70 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LCA |  |  |  | LLE0403 | LCA002RD |  | 75 |  |  |  |  | 3 |  | 70 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LCB |  |  |  | LLB0505 | LCB001RD |  | 30 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LCB |  |  |  | LLD0406 | LCB002RD |  | 40 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LCC |  |  |  | LLA0505 | LCC001RD |  | 40 |  |  |  |  | 3 |  | 6 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LCC |  |  |  | LLC0410 | LCC002RD |  | 30 |  |  |  |  | 3 |  | 6 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0010 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | GEV001TS | LGA0801 |  | 127 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGA |  |  |  | LGA001TR | LGA001AR |  | 5 |  |  |  |  | 1 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LGA |  |  |  | LGA001TR | LGA001AR |  | 5 |  |  |  |  | 1 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 176 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 177 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 179 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 180 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 181 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGB |  |  |  | 9LGE0201 | 1LGB0401 |  | 180 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 225 |  |  |  |  | 1 |  | 400 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 223 |  |  |  |  | 1 |  | 400 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 224 |  |  |  |  | 1 |  | 400 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 225 |  |  |  |  | 1 |  | 400 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 227 |  |  |  |  | 1 |  | 400 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 225 |  |  |  |  | 1 |  | 400 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 234 |  |  |  |  | 1 |  | 500 |  | A0010 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 234 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGC |  |  |  | 9LGF0301 | 1LGC0601 |  | 233 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | GEV001TS | LGD001TR |  | 11 |  |  |  |  | 1 |  | 400 |  | A0019 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD001TR |  | 10 |  |  |  |  | 1 |  | 400 |  | A0020 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD001TR |  | 10 |  |  |  |  | 1 |  | 400 |  | A0021 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0010 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | GEV001TS | LGD0501 |  | 106 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | X1
1-2 | LGD |  |  |  | LGD001AR | LGATT19 |  | 9 |  |  |  |  | 1 |  | 25 |  | A0023 | [16 empty] | Significant | [11 empty] | A | MTCU |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD001TR | LGD001AR |  | 8 |  |  |  |  | 1 |  | 25 |  | A0022 | [16 empty] | Significant | [11 empty] | A | MTCU |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD001TR | LGD001AR |  | 5 |  |  |  |  | 1 |  | 70 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LGD |  |  |  | LGD001TR | LGD001AR |  | 5 |  |  |  |  | 1 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 45 |  |  |  |  | 1 |  | 400 |  | A0013 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 48 |  |  |  |  | 1 |  | 400 |  | A0014 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 45 |  |  |  |  | 1 |  | 400 |  | A0015 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 42 |  |  |  |  | 1 |  | 400 |  | A0016 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 45 |  |  |  |  | 1 |  | 400 |  | A0017 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 42 |  |  |  |  | 1 |  | 400 |  | A0018 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 47 |  |  |  |  | 1 |  | 400 |  | A0025 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 43 |  |  |  |  | 1 |  | 400 |  | A0026 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | LGD |  |  |  | LGD0401 | LGC0701 |  | 46 |  |  |  |  | 1 |  | 400 |  | A0027 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE001AR | 9LGETT8 |  | 20 |  |  |  |  | 3 |  | 50 |  | A0026 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE001TR | 9LGE001AR |  | 20 |  |  |  |  | 3 |  | 50 |  | A0025 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LHS |  |  |  | 9LHS002AR | 9LHS001GA |  | 33 |  |  |  |  | 3 |  | 35 |  | B0024 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
9 | LHS |  |  |  | 9LHS003AR | 9LHS002AR |  | 1 |  |  |  |  | 2 |  | 1.5 |  | B0117 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | X1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0013 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0014 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0015 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0016 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0017 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 6 |  |  |  |  | 1 |  | 400 |  | A0018 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 7 |  |  |  |  | 1 |  | 400 |  | A0019 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 7 |  |  |  |  | 1 |  | 400 |  | A0020 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGE0501 | 9LGF0501 |  | 7 |  |  |  |  | 1 |  | 400 |  | A0021 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 20 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 20 |  |  |  |  | 1 |  | 500 |  | A0010 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE001TR |  | 23 |  |  |  |  | 1 |  | 400 |  | A0022 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE001TR |  | 23 |  |  |  |  | 1 |  | 400 |  | A0023 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGE |  |  |  | 9LGR001TA | 9LGE001TR |  | 23 |  |  |  |  | 1 |  | 400 |  | A0024 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGF001AR | 9LGFTT9 |  | 20 |  |  |  |  | 3 |  | 50 |  | A0017 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGF001TR | 9LGF001AR |  | 20 |  |  |  |  | 3 |  | 50 |  | A0016 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | RIS |  |  |  | 9LKI0105 | 9RIS001AR |  | 78 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | LNF |  |  |  | 9LKI0305 | 9LNF001TR |  | 22 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF001TR |  | 21 |  |  |  |  | 1 |  | 400 |  | A0013 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF001TR |  | 21 |  |  |  |  | 1 |  | 400 |  | A0014 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF001TR |  | 21 |  |  |  |  | 1 |  | 400 |  | A0015 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 20 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 13 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 16 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 16 |  |  |  |  | 1 |  | 500 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 16 |  |  |  |  | 1 |  | 500 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 14 |  |  |  |  | 1 |  | 500 |  | A0010 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGF |  |  |  | 9LGR002TA | 9LGF0401 |  | 15 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | 2LGC0201 | 9LGI0501 |  | 55 |  |  |  |  | 3 |  | 240 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | 2LGC0201 | 9LGI0501 |  | 71 |  |  |  |  | 3 |  | 240 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | 9LGI0301 | 9LHC0801 |  | 28 |  |  |  |  | 1 |  | 400 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | 9LGI0301 | 9LHC0801 |  | 28 |  |  |  |  | 1 |  | 400 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | 9LGI0301 | 9LHC0801 |  | 28 |  |  |  |  | 1 |  | 400 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | LGC0201 | 9LGI0101 |  | 75 |  |  |  |  | 3 |  | 240 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LGI |  |  |  | LGC0201 | 9LGI0101 |  | 77 |  |  |  |  | 3 |  | 240 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
9 | LHA |  |  |  | 9LHC0201 | 1LHA0701 |  | 69 |  |  |  |  | 1 |  | 400 |  | A0007 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
9 | LHA |  |  |  | 9LHC0201 | 1LHA0701 |  | 73 |  |  |  |  | 1 |  | 400 |  | A0008 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
9 | LHA |  |  |  | 9LHC0201 | 1LHA0701 |  | 69 |  |  |  |  | 1 |  | 400 |  | A0009 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHA |  |  |  | LGB0601 | LHA0101 |  | 25 |  |  |  |  | 1 |  | 400 |  | A0004 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHA |  |  |  | LGB0601 | LHA0101 |  | 23 |  |  |  |  | 1 |  | 400 |  | A0005 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHA |  |  |  | LGB0601 | LHA0101 |  | 25 |  |  |  |  | 1 |  | 400 |  | A0006 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHA |  |  |  | LHP001AR | LHA0401 |  | 46 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHA |  |  |  | LHP001AR | LHA0401 |  | 44 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHA |  |  |  | LHP001AR | LHA0401 |  | 44 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHB |  |  |  | 9LHC0101 | 1LHB0801 |  | 15 |  |  |  |  | 1 |  | 400 |  | A0007 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
9 | LHB |  |  |  | 9LHC0101 | 1LHB0801 |  | 18 |  |  |  |  | 1 |  | 400 |  | A0008 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
9 | LHB |  |  |  | 9LHC0101 | 1LHB0801 |  | 13 |  |  |  |  | 1 |  | 400 |  | A0009 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHB |  |  |  | LGC0401 | LHB0101 |  | 30 |  |  |  |  | 1 |  | 400 |  | A0004 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHB |  |  |  | LGC0401 | LHB0101 |  | 30 |  |  |  |  | 1 |  | 400 |  | A0005 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHB |  |  |  | LGC0401 | LHB0101 |  | 30 |  |  |  |  | 1 |  | 400 |  | A0006 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHB |  |  |  | LHQ001AR | LHB0401 |  | 156 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHB |  |  |  | LHQ001AR | LHB0401 |  | 158 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHB |  |  |  | LHQ001AR | LHB0401 |  | 157 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHC |  |  |  | 9LHS001AR | 9LHC0501 |  | 156 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHC |  |  |  | 9LHS001AR | 9LHC0501 |  | 156 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHC |  |  |  | 9LHS001AR | 9LHC0501 |  | 156 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHP |  |  |  | LHP001GA | LHP001AR |  | 13 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHP |  |  |  | LHP001GA | LHP001AR |  | 13 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHP |  |  |  | LHP001GA | LHP001AR |  | 14 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
1-2 | LHP |  |  |  | LHP002AR | LHP001GA |  | 15 |  |  |  |  | 2 |  | 16 |  | B0021 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | LHP |  |  |  | LHP002AR | LHP001GA |  | 1 |  |  |  |  | 2 |  | 16 |  | B0022 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | LHP |  |  |  | LHP002AR | LHP001GA |  | 23 |  |  |  |  | 2 |  | 6 |  | B0023 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | LHP |  |  |  | LHP002AR | LHP001GA |  | 21 |  |  |  |  | 3 |  | 35 |  | B0024 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
1-2 | LHP |  |  |  | LHP003AR | LHP002AR |  | 1 |  |  |  |  | 2 |  | 1.5 |  | B0117 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | X1
1-2 | LHP |  |  |  | LLG0101 | LHP001PO |  | 41 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0103 | LHP004MO |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0105 | LHP002ZV |  | 39 |  |  |  |  | 3 |  | 70 |  | B0013 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0107 | LHP001ZV |  | 43 |  |  |  |  | 3 |  | 70 |  | B0012 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0201 | LHP002PO |  | 43 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0202 | LHP003PO |  | 21 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0203 | LHP005PO |  | 14 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0204 | LHP001RE |  | 21 |  |  |  |  | 3 |  | 16 |  | B0009 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0204 | LHP004RE |  | 21 |  |  |  |  | 3 |  | 16 |  | B0025 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0205 | LHP002RE |  | 35 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0206 | LHP003RE |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0207 | LHP001CO |  | 13 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0208 | LHP002CO |  | 12 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0209 | LHP003ZV |  | 32 |  |  |  |  | 3 |  | 16 |  | B0014 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0210 | LHP004ZV |  | 35 |  |  |  |  | 3 |  | 16 |  | B0015 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0211 | LHP005ZV |  | 39 |  |  |  |  | 3 |  | 16 |  | B0016 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHP |  |  |  | LLG0212 | LHP006ZV |  | 43 |  |  |  |  | 3 |  | 16 |  | B0017 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ001GA | LHQ001AR |  | 14 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ001GA | LHQ001AR |  | 14 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ001GA | LHQ001AR |  | 14 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ002AR | LHQ001GA |  | 20 |  |  |  |  | 2 |  | 16 |  | B0021 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ002AR | LHQ001GA |  | 1 |  |  |  |  | 2 |  | 16 |  | B0022 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ002AR | LHQ001GA |  | 1 |  |  |  |  | 2 |  | 6 |  | B0023 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ002AR | LHQ001GA |  | 28 |  |  |  |  | 3 |  | 35 |  | B0024 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LHQ003AR | LHQ002AR |  | 1 |  |  |  |  | 2 |  | 1.5 |  | B0117 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 220 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0101 | LHQ001PO |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0103 | LHQ004MO |  | 26 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0105 | LHQ002ZV |  | 43 |  |  |  |  | 3 |  | 70 |  | B0013 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0107 | LHQ001ZV |  | 39 |  |  |  |  | 3 |  | 70 |  | B0012 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0201 | LHQ002PO |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0202 | LHQ003PO |  | 44 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0203 | LHQ005PO |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0204 | LHQ001RE |  | 18 |  |  |  |  | 3 |  | 16 |  | B0009 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0204 | LHQ004RE |  | 9 |  |  |  |  | 3 |  | 16 |  | B0025 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0205 | LHQ002RE |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0206 | LHQ003RE |  | 17 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0207 | LHQ001CO |  | 14 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0208 | LHQ002CO |  | 13 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0209 | LHQ003ZV |  | 32 |  |  |  |  | 3 |  | 16 |  | B0014 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0210 | LHQ004ZV |  | 35 |  |  |  |  | 3 |  | 16 |  | B0015 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0211 | LHQ005ZV |  | 42 |  |  |  |  | 3 |  | 16 |  | B0016 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LHQ |  |  |  | LLW0212 | LHQ006ZV |  | 44 |  |  |  |  | 3 |  | 16 |  | B0017 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LHS001GA | 9LHS001AR |  | 11 |  |  |  |  | 1 |  | 400 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHS |  |  |  | 9LHS001GA | 9LHS001AR |  | 11 |  |  |  |  | 1 |  | 400 |  | A0002 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | LHS |  |  |  | 9LHS001GA | 9LHS001AR |  | 11 |  |  |  |  | 1 |  | 400 |  | A0003 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | X1
9 | REA |  |  |  | 9LKI0309 | 9REA002AG |  | 101 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
9 | RRI |  |  |  | 9LKI0403 | 9RRI044VN |  | 77 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | RRI |  |  |  | 9LKI0404 | 9RRI045VN |  | 100 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | RRI |  |  |  | 9LKI0405 | 9RRI322VN |  | 87 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | RRI |  |  |  | 9LKI0406 | 9RRI323VN |  | 116 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TES |  |  |  | 9LKI0509 | 9TES001AG |  | 82 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
0 | LZD |  |  |  | 9LKK0301 | 0LZD001RD |  | 90 |  |  |  |  | 3 |  | 6 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
0 | LZD |  |  |  | 9LKK0401 | 0LZD002RD |  | 79 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | SED |  |  |  | 9LKK0405 | 9SED008VD |  | 308 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | LZB |  |  |  | 9LKK0407 | 0LZB001RD |  | 87 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | LHS |  |  |  | 9LLV0206 | 9LHS004MO |  | 61 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | SEP |  |  |  | 9LKK0509 | 9SEP613VE |  | 316 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LHS |  |  |  | 9LLV0208 | 9LHS001PO |  | 40 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0209 | 9LHS002PO |  | 43 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0210 | 9LHS003PO |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0211 | 9LHS005PO |  | 23 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | SEP |  |  |  | 9LKK0510 | 9SEP611VE |  | 319 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SEP |  |  |  | 9LKK0511 | 9SEP607VE |  | 319 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SEP |  |  |  | 9LKK0512 | 9SEP606VE |  | 326 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0205 | 9SDX001CO |  | 83 |  |  |  |  | 3 |  | 50 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0207 | 9SDX002CO |  | 76 |  |  |  |  | 3 |  | 50 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0209 | 9SDX003CO |  | 78 |  |  |  |  | 3 |  | 50 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0303 | 9SDX154AG |  | 101 |  |  |  |  | 3 |  | 2.5 |  | B0060 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0304 | 9SDX153AG |  | 103 |  |  |  |  | 3 |  | 2.5 |  | B0059 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | LKA |  |  |  | LGA0303 | LKA001TR |  | 16 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKB |  |  |  | LGD0203 | LKB001TR |  | 49 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKC |  |  |  | LGD0202 | LKC001TR |  | 28 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKD |  |  |  | LGB0203 | LKD001TR |  | 24 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKE |  |  |  | LGB0202 | LKE001TR |  | 36 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKF |  |  |  | LGC0303 | LKF001TR |  | 27 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKG |  |  |  | LGC0803 | LKG001TR |  | 312 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKH |  |  |  | LGC0802 | LKH001TR |  | 41 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
9 | LKI |  |  |  | 9LGI0203 | 9LKI001TR |  | 99 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
9 | LKI |  |  |  | 9LKI002CR | 9RCP001PO |  | 1 |  |  |  |  | 2.5 |  | 1.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | LKJ |  |  |  | LGC0301 | LKJ001TR |  | 129 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
9 | LKK |  |  |  | 9LGI0201 | 9LKK001TR |  | 14 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
1-2 | LKL |  |  |  | LKD0103 | LKL001TB |  | 237 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | LKL |  |  |  | LKD0103 | LKL001TB |  | 227 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
9 | LKM |  |  |  | 9LGI0402 | 9LKM001TR |  | 342 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | AR | L1
6 | LKN |  |  |  | 6LKN010CR | 6LKN001CO |  | 1 |  |  |  |  | 3 |  | 4 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
6 | LKN |  |  |  | 6LKN011CR | 6LKN002CO |  | 9 |  |  |  |  | 3 |  | 4 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LKN |  |  |  | 9LGI0202 | 9LKN001TR |  | 253 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | NSA | L1
9 | LKP |  |  |  | 9LGI0401 | 9LKP001TR |  | 482 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | NSA | L1
1-2 | LKS |  |  |  | LGC0302 | LKS001TR |  | 46 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | NSA | L1
9 | LKX |  |  |  | 9LKP0309 | 9LKX001TB |  | 107 |  |  |  |  | 3 |  | 150 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LKX |  |  |  | 9LKP0309 | 9LKX001TB |  | 116 |  |  |  |  | 3 |  | 150 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LKX |  |  |  | 9LKX0101 | 9LKX001PR |  | 65 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
9 | LKX |  |  |  | 9LKX0212 | 9LKX002CR |  | 30 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LKZ |  |  |  | 9LGI0601 | 9LKZ001TR |  | 88 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 380 Vac | NO | NSA | L1
9 | LKZ |  |  |  | 9LKZ001TB | 9LXZ001RD |  | 90 |  |  |  |  | 3 |  | 16 |  | B0900 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | LLA |  |  |  | LHA0603 | LLA001TR |  | 13 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLB |  |  |  | LHB0603 | LLB001TR |  | 25 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLC |  |  |  | LHA0602 | LLC001TR |  | 26 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLD |  |  |  | LHB0602 | LLD001TR |  | 19 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLE |  |  |  | LHA0503 | LLE001TR |  | 47 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLG |  |  |  | LLI0103 | LLG001TB |  | 34 |  |  |  |  | 3 |  | 150 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LLG |  |  |  | LLI0103 | LLG001TB |  | 34 |  |  |  |  | 3 |  | 150 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LLI |  |  |  | LHA0502 | LLI001TR |  | 18 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
1-2 | LLJ |  |  |  | LHB0703 | LLJ001TR |  | 31 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB |  | 274 |  |  |  |  | 1 |  | 300 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB |  | 278 |  |  |  |  | 1 |  | 300 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | LLL |  |  |  | 0LLK0222 | 0LLL001TB |  | 269 |  |  |  |  | 1 |  | 300 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LLM |  |  |  | 9LLM001CR | 9LLM001TR |  | 13 |  |  |  |  | 3 |  | 185 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LLV |  |  |  | 9LLZ0103 | 9LLV001TB |  | 165 |  |  |  |  | 3 |  | 150 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LLV |  |  |  | 9LLZ0103 | 9LLV001TB |  | 190 |  |  |  |  | 3 |  | 150 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LLZ |  |  |  | 9LHC0602 | 9LLZ001TR |  | 14 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Critical | [11 empty] | A | MTAL |  | 6.6 kV | NO | CSR | L1
9 | LLZ |  |  |  | 9LKK0103 | 9LLZ001TB |  | 20 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LLZ |  |  |  | 9LKK0103 | 9LLZ001TB |  | 20 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LMA |  |  |  | LMA0254 | KIR001AR |  | 78 |  |  |  |  | 2 |  | 16 |  | B0018 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL001AR |  | 22 |  |  |  |  | 2 |  | 2.5 |  | B0101 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL002AR |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0102 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL003AR |  | 13 |  |  |  |  | 2 |  | 2.5 |  | B0103 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL004AR |  | 19 |  |  |  |  | 2 |  | 2.5 |  | B0104 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL005AR |  | 14 |  |  |  |  | 2 |  | 2.5 |  | B0105 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA100CR | RGL006AR |  | 58 |  |  |  |  | 2 |  | 2.5 |  | B0106 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI001MO |  | 61 |  |  |  |  | 2 |  | 2.5 |  | B0121 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI002MO |  | 53 |  |  |  |  | 2 |  | 2.5 |  | B0122 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI003MO |  | 58 |  |  |  |  | 2 |  | 2.5 |  | B0123 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI004MO |  | 39 |  |  |  |  | 2 |  | 2.5 |  | B0124 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI005MO |  | 39 |  |  |  |  | 2 |  | 2.5 |  | B0125 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA120CR | CFI006MO |  | 45 |  |  |  |  | 2 |  | 2.5 |  | B0126 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA130CR | CFI001CR |  | 30 |  |  |  |  | 2 |  | 2.5 |  | B0131 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA130CR | CFI002CR |  | 35 |  |  |  |  | 2 |  | 2.5 |  | B0132 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA130CR | CFI003CR |  | 35 |  |  |  |  | 2 |  | 2.5 |  | B0133 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA130CR | CFI004CR |  | 57 |  |  |  |  | 2 |  | 2.5 |  | B0134 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA140CR | CSI004VC |  | 51 |  |  |  |  | 2 |  | 2.5 |  | B0141 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA140CR | CSI005VC |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0142 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA160CR | KRT001AR |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0161 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA160CR | KRT002AR |  | 25 |  |  |  |  | 2 |  | 2.5 |  | B0162 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
6 | LMA |  |  |  | LMA160CR | 9KRT501AR |  | 28 |  |  |  |  | 2 |  | 2.5 |  | B0163 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV001AR |  | 28 |  |  |  |  | 2 |  | 2.5 |  | B0181 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV002AR |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0182 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV003AR |  | 27 |  |  |  |  | 2 |  | 2.5 |  | B0183 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV011AR |  | 27 |  |  |  |  | 2 |  | 2.5 |  | B0184 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV012AR |  | 15 |  |  |  |  | 2 |  | 2.5 |  | B0185 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV013AR |  | 26 |  |  |  |  | 2 |  | 2.5 |  | B0186 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LMA |  |  |  | LMA180CR | GEV004AR |  | 58 |  |  |  |  | 2 |  | 2.5 |  | B0187 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
1-2 | LNA |  |  |  | LLC0412 | LNA001TR |  | 26 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LNB |  |  |  | LLD0408 | LNB001TR |  | 58 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LNC |  |  |  | LLC0512 | LNC001TR |  | 52 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LND |  |  |  | LLD0409 | LND001TR |  | 56 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LNE |  |  |  | B0708 | RPN005AR |  | 160 |  |  |  |  | 2 |  | 6 |  | B0085 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | X1
1-2 | LNE |  |  |  | GSE001AR | GSE002AR |  | 8 |  |  |  |  | 2 |  | 2.5 |  | B0081 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | X1
1-2 | LNE |  |  |  | K0102 | RPN005AR |  | 1 |  |  |  |  | 2 |  | 6 |  | B0083 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | X1
1-2 | LNE |  |  |  | LLI0310 | LNE001DL |  | 45 |  |  |  |  | 2 |  | 6 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | LNE |  |  |  | LNE001DL | LNE002DL |  | 7 |  |  |  |  | 2 |  | 6 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE002DL | LNE003DL |  | 7 |  |  |  |  | 2 |  | 6 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0213 | KRT001AR |  | 104 |  |  |  |  | 2 |  | 6 |  | B0039 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0214 | KRT002AR |  | 102 |  |  |  |  | 2 |  | 16 |  | B0040 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0223 | GPA004AR |  | 102 |  |  |  |  | 2 |  | 6 |  | B0035 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0234 | GPA003AR |  | 92 |  |  |  |  | 2 |  | 6 |  | B0032 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0312 | KKO601AR |  | 120 |  |  |  |  | 2 |  | 16 |  | B0062 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0313 | KKO801AR |  | 111 |  |  |  |  | 2 |  | 16 |  | B0063 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0322 | RAM001TB |  | 78 |  |  |  |  | 2 |  | 6 |  | B0058 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0331 | RCP001RG |  | 37 |  |  |  |  | 2 |  | 16 |  | B0053 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0332 | RCP002RG |  | 37 |  |  |  |  | 2 |  | 16 |  | B0054 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0333 | RIC001AR |  | 147 |  |  |  |  | 2 |  | 16 |  | B0055 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0341 | RGL009AR |  | 91 |  |  |  |  | 2 |  | 6 |  | B0049 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0342 | RGL009AR |  | 90 |  |  |  |  | 2 |  | 6 |  | B0050 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0343 | RGL009AR |  | 97 |  |  |  |  | 2 |  | 6 |  | B0051 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0344 | GEX001AR |  | 164 |  |  |  |  | 2 |  | 2.5 |  | B0076 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0351 | RGL010AR |  | 90 |  |  |  |  | 2 |  | 6 |  | B0045 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0453 | ASG055CR |  | 99 |  |  |  |  | 2 |  | 2.5 |  | B0071 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE0463 | GSE001AR |  | 91 |  |  |  |  | 2 |  | 16 |  | B0067 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE100CR | PTR100EN |  | 1 |  |  |  |  | 2 |  | 2.5 |  | B0105 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE180CR | GPB002AR |  | 45 |  |  |  |  | 2 |  | 6 |  | B0183 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN010MG |  | 10 |  |  |  |  | 2 |  | 2.5 |  | B0261 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN041MG |  | 3 |  |  |  |  | 2 |  | 2.5 |  | B0262 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN042MG |  | 3 |  |  |  |  | 2 |  | 2.5 |  | B0263 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN043MG |  | 4 |  |  |  |  | 2 |  | 2.5 |  | B0264 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN044MG |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0265 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN071MG |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0266 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN072MG |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0267 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN073MG |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0268 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN081MG |  | 14 |  |  |  |  | 2 |  | 2.5 |  | B0269 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN082MG |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0270 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN083MG |  | 9 |  |  |  |  | 2 |  | 2.5 |  | B0271 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE260CR | REN010MG |  | 9 |  |  |  |  | 2 |  | 2.5 |  | B0272 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE320CR | VVP010MP |  | 15 |  |  |  |  | 2 |  | 2.5 |  | B0321 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE320CR | VVP011MP |  | 15 |  |  |  |  | 2 |  | 2.5 |  | B0322 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE320CR | VVP012MP |  | 40 |  |  |  |  | 2 |  | 2.5 |  | B0323 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE320CR | ARE002YP |  | 30 |  |  |  |  | 2 |  | 2.5 |  | B0324 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE330CR | ARE005YD |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0331 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE330CR | ARE006YD |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0332 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE330CR | ARE007YD |  | 5 |  |  |  |  | 2 |  | 2.5 |  | B0333 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE400CR | CRF001SN |  | 21 |  |  |  |  | 2 |  | 2.5 |  | B0401 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE400CR | CRF001SP |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0402 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE410CR | CRF005SN |  | 18 |  |  |  |  | 2 |  | 2.5 |  | B0411 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE410CR | CRF003SP |  | 10 |  |  |  |  | 2 |  | 2.5 |  | B0412 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE420CR | CRF009SN |  | 39 |  |  |  |  | 2 |  | 2.5 |  | B0421 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
1-2 | LNE |  |  |  | LNE420CR | CRF005SP |  | 15 |  |  |  |  | 2 |  | 2.5 |  | B0422 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 230 Vdc | NO | SR | L1
9 | SDX |  |  |  | 9LKN0410 | 9SDX151AG |  | 73 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0411 | 9SDX152AG |  | 79 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | LZB |  |  |  | 0LZB001RD | 0LZB001TB |  | 20 |  |  |  |  | 2 |  | 35 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
0 | LZB |  |  |  | 0LZB001TB | 0LZC001TB |  | 20 |  |  |  |  | 1 |  | 70 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
9 | SER |  |  |  | 9LKN0605 | 9SER001VD |  | 53 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | LZC |  |  |  | 0LZB001TB | 0LZC001TB |  | 112 |  |  |  |  | 2 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
0 | LZC |  |  |  | 0LZD001TB | 0LZC001TB |  | 124 |  |  |  |  | 2 |  | 2.5 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
0 | LZC |  |  |  | 0LZD002TB | 0LZC001TB |  | 121 |  |  |  |  | 2 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
9 | SER |  |  |  | 9LKN0606 | 9SER002VD |  | 41 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SER |  |  |  | 9LKN0607 | 9SER005VD |  | 56 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | ATE102AR | 9SER006VD |  | 48 |  |  |  |  | 3 |  | 2.5 |  | B0030 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
0 | LZZ |  |  |  | LKS0105 | 0LZZ001TR |  | 211 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | PMC |  |  |  | PMC005CR | PMC001MP |  | Site Run | [8 empty] | C0903 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC003MO |  | Site Run | [8 empty] | C0905 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC002MO |  | Site Run | [8 empty] | C0906 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC001CR |  | Site Run | [8 empty] | C0907 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC001CR |  | Site Run | [8 empty] | C0908 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC001CR |  | Site Run | [8 empty] | C0909 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC004MO |  | Site Run | [8 empty] | C0910 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC010CR |  | Site Run | [8 empty] | C0911 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC001CR |  | Site Run | [8 empty] | C0914 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC003MO |  | Site Run | [8 empty] | C0915 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC002MO |  | Site Run | [8 empty] | C0916 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC007CR |  | Site Run | [8 empty] | C0917 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC012AR | PMC005SM |  | Site Run | [8 empty] | C0918 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC008CR | PMC011SM |  | Site Run | [8 empty] | C0919 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC011CR | PMC004SM |  | Site Run | [8 empty] | C0920 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC006SM |  | Site Run | [8 empty] | C0921 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC014SM |  | Site Run | [8 empty] | C0922 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC015SM |  | Site Run | [8 empty] | C0923 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC016SM |  | Site Run | [8 empty] | C0924 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC017SM |  | Site Run | [8 empty] | C0925 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC020SM |  | Site Run | [8 empty] | C0926 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC004MO |  | Site Run | [8 empty] | C0927 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC014CR |  | Site Run | [8 empty] | C0929 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC013AR | PMC018SM |  | Site Run | [8 empty] | C0930 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC001SM |  | Site Run | [8 empty] | C0931 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC002SM |  | Site Run | [8 empty] | C0932 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC003SM |  | Site Run | [8 empty] | C0933 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC019SM |  | Site Run | [8 empty] | C0934 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC006EL |  | Site Run | [8 empty] | C0935 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | GRIPPERLIMITSWITCHES |  | Site Run | [8 empty] | C0936 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC006CR | PMC010CR |  | Site Run | [8 empty] | C0937 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC001CR |  | Site Run | [8 empty] | C0939 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC001CR |  | Site Run | [8 empty] | C0940 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC006CR |  | Site Run | [8 empty] | C0941 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP6 | PMC005CR |  | Site Run | [8 empty] | M0900 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP7 | PMC003MM |  | Site Run | [8 empty] | M0901 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP10 | PMC004MM |  | Site Run | [8 empty] | M0902 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP8 | PMC005MM |  | Site Run | [8 empty] | M0903 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP11 | PMC006MM |  | Site Run | [8 empty] | M0904 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP9 | PMC001MM |  | Site Run | [8 empty] | M0905 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP12 | PMC002MM |  | Site Run | [8 empty] | M0906 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP1 | PMC001CR |  | Site Run | [8 empty] | M0907 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP2 | PMC005CR |  | Site Run | [8 empty] | M0908 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP3 | PMC005CR |  | Site Run | [8 empty] | M0909 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP4 | PMC005CR |  | Site Run | [8 empty] | M0910 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP5 | PMC005CR |  | Site Run | [8 empty] | M0911 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP40 | PMC005CR |  | Site Run | [8 empty] | M0912 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP14 | PMC101TV |  | Site Run | [8 empty] | M0913 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP19 | PMC101TV |  | Site Run | [8 empty] | M0916 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | BRIDGEFESTOON | CONTROLCONSOLEP17 |  | Site Run | [8 empty] | M0917 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | BRIDGEFESTOON | CONTROLCONSOLEP18 |  | Site Run | [8 empty] | M0918 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | BRIDGEFESTOON | CONTROLCONSOLEP22 |  | Site Run | [8 empty] | M0919 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP16 | PMC100TV |  | Site Run | [8 empty] | M0920 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLEP15 | PMC042PJ |  | Site Run | [8 empty] | M0921 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC006CR |  | Site Run | [8 empty] | M0922 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 3
1-2 | PMC |  |  |  | CGE | PMC001TB |  | 92 |  |  |  |  | 3 |  | 185 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | PMC |  |  |  | CONTROLCONSOLE P13 | PMC001CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0904 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | CONTROLCONSOLE P26 | PMC030PJ |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0903 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | LKL0107 | PMC002TB |  | 48 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | PMC |  |  |  | LKL0107 | PMC002TB |  | 52 |  |  |  |  | 3 |  | 185 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | PMC |  |  |  | PENETRATION | PMC003CR |  | Site Run |  |  |  |  | 3 |  | 6 |  | B0035 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PENETRATION | PMC003CR |  | Site Run |  |  |  |  | 3 |  | 6 |  | B0055 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC005CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0907 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC001CR | PMC004CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0911 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC003CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC003CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0906 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC006JS |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0909 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC002CR | PMC003CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0910 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC003CR | PMC006JS |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0905 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC004CR | PMC006ES |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0900 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC004CR | PMC007ES |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0901 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC004CR | PMC008ES |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0902 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PMC005CR | PMC006CR |  | Site Run |  |  |  |  | 3 |  | 2.5 |  | B0908 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 3
1-2 | PMC |  |  |  | PN1L317 | PMC001TB |  | Site Run |  |  |  |  | 3 |  | 185 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 3
1-2 | PTR |  |  |  | KRG024AR | PTR100MN |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0100 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG013AR | PTR101MN |  | 350 |  |  |  |  | 1TTB |  | 1 |  | M0101 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG024AR | PTR100MT |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0102 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG013AR | PTR101MT |  | 350 |  |  |  |  | 1TTB |  | 1 |  | M0103 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG024AR | PTR102MT |  | 350 |  |  |  |  | 1TTB |  | 1 |  | M0104 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG013AR | PTR103MT |  | 350 |  |  |  |  | 1TTB |  | 1 |  | M0105 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | K1
1-2 | PTR |  |  |  | KRG024AR | PTR100MD |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0106 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | PTR |  |  |  | KRG013AR | PTR101MD |  | 350 |  |  |  |  | 1PTB |  | 1 |  | M0107 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | W1
1-2 | PTR |  |  |  | KRG023AR | PTR018MN |  | 62 |  |  |  |  | 1PTB |  | 1 |  | M0615 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | X1
1-2 | PTR |  |  |  | KRG034AR | PTR019MN |  | 63 |  |  |  |  | 1PTB |  | 1 |  | M0618 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | X1
1-2 | PTR |  |  |  | KRG041AR | PTR020MN |  | 63 |  |  |  |  | 1PTB |  | 1 |  | M0622 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | X1
1-2 | PTR |  |  |  | LKL0203 | PTR005PO |  | 81 |  |  |  |  | 3 |  | 50 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | PTR |  |  |  | LKL0204 | PTR003PO |  | 44 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | PTR |  |  |  | LLI001TB | PTR137VB |  | 270 |  |  |  |  | 3 |  | 2.5 |  | B0101 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | PTR |  |  |  | PTR001BX | PTR001PO |  | 42 |  |  |  |  | 3 |  | 150 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | PTR |  |  |  | PTR002BX | PTR002PO |  | 42 |  |  |  |  | 3 |  | 150 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | K1
1-2 | RAM |  |  |  | LKA0201 | RAM002MO |  | 44 |  |  |  |  | 3 |  | 150 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | LKA0201 | RAM002MO |  | 44 |  |  |  |  | 3 |  | 150 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | LKA0201 | RAM001TB |  | 101 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | LKC0205 | RAM001MO |  | 52 |  |  |  |  | 3 |  | 150 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | LKC0205 | RAM001MO |  | 54 |  |  |  |  | 3 |  | 150 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | LKC0205 | RAM001TB |  | 145 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM001AP |  | 16 |  |  |  |  | 4 |  | 150 |  | B0311 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM001AP |  | 16 |  |  |  |  | 4 |  | 150 |  | B0312 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM001AP |  | 16 |  |  |  |  | 4 |  | 150 |  | B0313 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM002AP |  | 17 |  |  |  |  | 4 |  | 150 |  | B0328 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM002AP |  | 17 |  |  |  |  | 4 |  | 150 |  | B0329 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM002TB | RAM002AP |  | 17 |  |  |  |  | 4 |  | 150 |  | B0330 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM001AP |  | 15 |  |  |  |  | 2 |  | 16 |  | B0300 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM001AP |  | 15 |  |  |  |  | 2 |  | 16 |  | B0301 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0303 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0304 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0305 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0306 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0307 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0308 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0309 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM401BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 2.5 |  | B0310 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM501BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0319 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM501BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0338 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0320 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0321 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0322 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0323 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0324 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0325 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 6 |  | B0326 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002TB |  | 7 |  |  |  |  | 2 |  | 2.5 |  | B0327 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002AP |  | 16 |  |  |  |  | 2 |  | 16 |  | B0331 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RAM601BN | RAM002AP |  | 16 |  |  |  |  | 2 |  | 16 |  | B0332 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RGL001AR | RAM002TB |  | 8 |  |  |  |  | 2 |  | 2.5 |  | B0314 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RGL003AR | RAM002TB |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0315 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RGL004AR | RAM002TB |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0316 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RGL005AR | RAM002TB |  | 9 |  |  |  |  | 2 |  | 2.5 |  | B0317 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | 1
1-2 | RAM |  |  |  | RGL006AR | RAM002TB |  | 10 |  |  |  |  | 2 |  | 2.5 |  | B0318 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RCP |  |  |  | PN1L345 | RCP007VP |  | 50 |  |  |  |  | 12 |  | 1.5 |  | C0008 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 4
1-2 | RCP |  |  |  | PN1L345 | RCP215VP |  | 45 |  |  |  |  | 12 |  | 1.5 |  | C0014 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RCP |  |  |  | PN1L309 | RCP212VP |  | 100 |  |  |  |  | 12 |  | 1.5 |  | C0037 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RCP |  |  |  | PN1L337 | RCP005VP |  | 42 |  |  |  |  | 12 |  | 1.5 |  | C0391 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L337 | RCP006VP |  | 41 |  |  |  |  | 12 |  | 1.5 |  | C0394 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L337 | RCP212VP |  | 56 |  |  |  |  | 12 |  | 1.5 |  | C0401 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RCP |  |  |  | RCP004CR | RCP001VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0403 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | 3
1-2 | RCP |  |  |  | RCP004CR | RCP002VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0404 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | 3
1-2 | RCP |  |  |  | PN1L345 | RCP215VP |  | 34 |  |  |  |  | 12 |  | 1.5 |  | C0520 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RCP |  |  |  | PN1L345 | RCP007VP |  | 30 |  |  |  |  | 12 |  | 1.5 |  | C0602 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L526 | RCP114MT |  | 30 |  |  |  |  | 1TTB |  | 1 |  | M0001 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP116MT |  | 97 |  |  |  |  | 1TTB |  | 1 |  | M0002 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP118MT |  | 97 |  |  |  |  | 1TTB |  | 1 |  | M0003 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP214MT |  | 29 |  |  |  |  | 1TTB |  | 1 |  | M0004 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP216MT |  | 27 |  |  |  |  | 1TTB |  | 1 |  | M0005 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP218MT |  | 27 |  |  |  |  | 1TTB |  | 1 |  | M0006 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP314MT |  | 135 |  |  |  |  | 1TTB |  | 1 |  | M0007 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP316MT |  | 133 |  |  |  |  | 1TTB |  | 1 |  | M0008 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L526 | RCP318MT |  | 131 |  |  |  |  | 1TTB |  | 1 |  | M0009 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP030MT |  | 43 |  |  |  |  | 1TTB |  | 1 |  | M0300 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP033MT |  | 37 |  |  |  |  | 1TTB |  | 1 |  | M0302 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP031MT |  | 43 |  |  |  |  | 1TTB |  | 1 |  | M0304 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP034MT |  | 37 |  |  |  |  | 1TTB |  | 1 |  | M0306 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP005MP |  | 17 |  |  |  |  | 1PTB |  | 1 |  | M0308 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L513 | RCP011MN |  | 17 |  |  |  |  | 1PTB |  | 1 |  | M0310 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L513 | RCP039MP |  | 48 |  |  |  |  | 1PTB |  | 1 |  | M0312 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L513 | RCP025MD |  | 35 |  |  |  |  | 1TTB |  | 1 |  | M0314 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L513 | RCP040MD |  | 48 |  |  |  |  | 1TTB |  | 1 |  | M0316 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L513 | RCP052MD |  | 65 |  |  |  |  | 1PTB |  | 1 |  | M0318 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L529 | RCP045MT |  | 26 |  |  |  |  | 1QTB |  | 1 |  | M0320 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP048MT |  | 21 |  |  |  |  | 1QTB |  | 1 |  | M0322 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP046MT |  | 26 |  |  |  |  | 1QTB |  | 1 |  | M0324 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP049MT |  | 21 |  |  |  |  | 1QTB |  | 1 |  | M0326 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP006MP |  | 29 |  |  |  |  | 1PTB |  | 1 |  | M0328 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L529 | RCP008MN |  | 29 |  |  |  |  | 1PTB |  | 1 |  | M0330 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L529 | RCP026MD |  | 52 |  |  |  |  | 1TTB |  | 1 |  | M0332 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L529 | RCP041MD |  | 26 |  |  |  |  | 1TTB |  | 1 |  | M0334 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L529 | RCP053MD |  | 65 |  |  |  |  | 1PTB |  | 1 |  | M0336 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L515 | RCP060MT |  | 75 |  |  |  |  | 1QTB |  | 1 |  | M0338 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP057MT |  | 76 |  |  |  |  | 1QTB |  | 1 |  | M0340 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP058MT |  | 76 |  |  |  |  | 1QTB |  | 1 |  | M0342 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP061MT |  | 75 |  |  |  |  | 1QTB |  | 1 |  | M0344 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP013MP |  | 14 |  |  |  |  | 1PTB |  | 1 |  | M0346 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L515 | RCP007MN |  | 14 |  |  |  |  | 1PTB |  | 1 |  | M0348 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L515 | RCP027MD |  | 45 |  |  |  |  | 1TTB |  | 1 |  | M0350 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L515 | RCP042MD |  | 38 |  |  |  |  | 1TTB |  | 1 |  | M0352 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L515 | RCP054MD |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0354 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 2
1-2 | RCP |  |  |  | PN1L533 | RCP037MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0356 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 2
1-2 | RCP |  |  |  | PN1L518 | RCP001VP |  | 17 |  |  |  |  | 1PTB |  | 1 |  | M0456 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | RCP |  |  |  | PN1L518 | RCP002VP |  | 19 |  |  |  |  | 1PTB |  | 1 |  | M0458 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 3
1-2 | RCP |  |  |  | PN1L517 | RCP010MT |  | 27 |  |  |  |  | 1TTB |  | 1 |  | M0553 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L517 | RCP018MT |  | 32 |  |  |  |  | 1TTB |  | 1 |  | M0557 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L517 | RCP019MT |  | 28 |  |  |  |  | 1TTB |  | 1 |  | M0559 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L517 | RCP020MT |  | 26 |  |  |  |  | 1TTB |  | 1 |  | M0561 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L517 | RCP021MT |  | 31 |  |  |  |  | 1TTB |  | 1 |  | M0563 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L517 | RCP035MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0571 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L517 | RCP032MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0573 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP055MT |  | 64 |  |  |  |  | 1TTB |  | 1 |  | M0586 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L513 | RCP028MT |  | 50 |  |  |  |  | 1PTB |  | 1 |  | M0588 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L529 | RCP043MT |  | 24 |  |  |  |  | 1TTB |  | 1 |  | M0590 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L518 | RCP050MT |  | 20 |  |  |  |  | 1QTB |  | 1 |  | M0592 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L518 | RCP047MT |  | 20 |  |  |  |  | 1QTB |  | 1 |  | M0594 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L522 | RCP062MT |  | 20 |  |  |  |  | 1QTB |  | 1 |  | M0618 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L522 | RCP059MT |  | 20 |  |  |  |  | 1QTB |  | 1 |  | M0620 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP140MC |  | 36 |  |  |  |  | 6PTB |  | 0.5 |  | M0634 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L513 | RCP141MC |  | 36 |  |  |  |  | 6PTB |  | 0.5 |  | M0636 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP240MC |  | 19 |  |  |  |  | 6PTB |  | 0.5 |  | M0638 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L529 | RCP241MC |  | 19 |  |  |  |  | 6PTB |  | 0.5 |  | M0640 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP340MC |  | 74 |  |  |  |  | 6PTB |  | 0.5 |  | M0642 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP341MC |  | 74 |  |  |  |  | 6PTB |  | 0.5 |  | M0644 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 6
1-2 | RCP |  |  |  | PN1L515 | RCP151MM |  | Site Run |  |  |  |  | 1TTB |  | 1 |  | M0981 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L529 | RCP152MM |  | Site Run |  |  |  |  | 1TTB |  | 1 |  | M0982 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | PN1L515 | RCP153MM |  | Site Run |  |  |  |  | 1TTB |  | 1 |  | M0985 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 4
1-2 | RCP |  |  |  | ABC | RCP001PO |  | 41 |  |  |  |  | 1 |  | 500 |  | A0011 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP001PO |  | 48 |  |  |  |  | 1 |  | 500 |  | A0012 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP001PO |  | 43 |  |  |  |  | 1 |  | 500 |  | A0013 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP002PO |  | 41 |  |  |  |  | 1 |  | 500 |  | A0014 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP002PO |  | 41 |  |  |  |  | 1 |  | 500 |  | A0015 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP002PO |  | 41 |  |  |  |  | 1 |  | 500 |  | A0016 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP003PO |  | 82 |  |  |  |  | 1 |  | 500 |  | A0017 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP003PO |  | 80 |  |  |  |  | 1 |  | 500 |  | A0018 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | ABC | RCP003PO |  | 75 |  |  |  |  | 1 |  | 500 |  | A0019 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | B0103 | RCP011PO |  | 50 |  |  |  |  | 3 |  | 6 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | B0103 | RCP021PO |  | 70 |  |  |  |  | 3 |  | 6 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | B0103 | RCP031PO |  | 84 |  |  |  |  | 3 |  | 6 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | ATE |  |  |  | ATE202AR | ATE500MG |  | 43 |  |  |  |  | 3 |  | 2.5 |  | B0052 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE102AR | ATE621MG |  | 60 |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | ATE |  |  |  | ATE101AR | ATE801MG |  | 94 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | X1
1-2 | DEG |  |  |  | PN1L310 | DEG044VD |  | 78 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | YES | AR | 3
1-2 | DVC |  |  |  | DVC013CR | DVC003RS |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVC |  |  |  | DVC013CR | DVC004RS |  | 25 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | RCP |  |  |  | LGA1101 | ABC |  | 46 |  |  |  |  | 1 |  | 500 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | 3
1-2 | RCP |  |  |  | LGA1101 | ABC |  | 48 |  |  |  |  | 1 |  | 500 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGA1101 | ABC |  | 46 |  |  |  |  | 1 |  | 500 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0701 | ABC |  | 56 |  |  |  |  | 1 |  | 500 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0701 | ABC |  | 57 |  |  |  |  | 1 |  | 500 |  | A0005 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0701 | ABC |  | 56 |  |  |  |  | 1 |  | 500 |  | A0006 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0801 | ABC |  | 66 |  |  |  |  | 1 |  | 500 |  | A0007 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0801 | ABC |  | 61 |  |  |  |  | 1 |  | 500 |  | A0008 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LGD0801 | ABC |  | 61 |  |  |  |  | 1 |  | 500 |  | A0009 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCP |  |  |  | LKA0103 | RCP003RS |  | 48 |  |  |  |  | 3 |  | 185 |  | B0024 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKA0103 | RCP003RS |  | 49 |  |  |  |  | 3 |  | 185 |  | B0025 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKB0205 | RCP002RS |  | 21 |  |  |  |  | 3 |  | 185 |  | B0022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKB0205 | RCP002RS |  | 21 |  |  |  |  | 3 |  | 185 |  | B0023 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKB0207 | RCP004RS |  | 17 |  |  |  |  | 3 |  | 185 |  | B0026 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKB0207 | RCP004RS |  | 17 |  |  |  |  | 3 |  | 185 |  | B0027 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKC0101 | RCP001RS |  | 66 |  |  |  |  | 3 |  | 185 |  | B0020 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LKC0101 | RCP001RS |  | 63 |  |  |  |  | 3 |  | 185 |  | B0021 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLC0105 | RCP205RS |  | 15 |  |  |  |  | 3 |  | 150 |  | B0033 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLC0105 | RCP205RS |  | 15 |  |  |  |  | 3 |  | 150 |  | B0035 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLC0107 | RCP105RS |  | 11 |  |  |  |  | 3 |  | 150 |  | B0029 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLC0107 | RCP105RS |  | 15 |  |  |  |  | 3 |  | 150 |  | B0031 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLD0103 | RCP206RS |  | 51 |  |  |  |  | 3 |  | 150 |  | B0032 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLD0103 | RCP206RS |  | 51 |  |  |  |  | 3 |  | 150 |  | B0034 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLD0105 | RCP106RS |  | 49 |  |  |  |  | 3 |  | 150 |  | B0028 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | LLD0105 | RCP106RS |  | 52 |  |  |  |  | 3 |  | 150 |  | B0030 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | DVC |  |  |  | DVC004CR | DVC008RS |  | 52 |  |  |  |  | 3 |  | 2.5 |  | B0022 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0377 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0378 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0379 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0380 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0381 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0382 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L314 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0482 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0383 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0384 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0385 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0386 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0387 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 24 |  |  |  |  | 1 |  | 70 |  | B0388 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0483 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0484 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0485 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0486 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0487 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L315 | RCP050CR |  | 20 |  |  |  |  | 2 |  | 16 |  | B0488 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | DVC |  |  |  | DVC011CR | DVC009RS |  | 31 |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | C1
1-2 | DVL |  |  |  | DVL002CS | DVL002EV |  | 10 |  |  |  |  | 2 |  | 2.5 |  | B0901 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | DVN |  |  |  | DVN001BX | DVN001ZV |  | 6 |  |  |  |  | 3 |  | 150 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | DVN |  |  |  | DVN004BX | DVN004ZV |  | 9 |  |  |  |  | 3 |  | 185 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | EPP |  |  |  | EPP101AR | EPP114VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0328 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP114VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0329 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP115VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0330 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP115VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0331 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP116VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0332 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP116VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0333 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP120VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0334 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP101AR | EPP120VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0335 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP214VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0320 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP214VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0321 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP215VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0322 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP215VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0323 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP216VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0324 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP216VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0325 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP220VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0326 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | EPP |  |  |  | EPP201AR | EPP220VA |  | 20 |  |  |  |  | 2 |  | 2.5 |  | B0327 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | RCP003RS | RCP001RG |  | 9 |  |  |  |  | 2 |  | 2.5 |  | B0480 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0331 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0332 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0333 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0334 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0335 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0336 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0401 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0402 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0403 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0404 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0405 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP001RG | RCP003RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0406 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 19 |  |  |  |  | 1 |  | 70 |  | B0352 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 19 |  |  |  |  | 1 |  | 70 |  | B0353 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 19 |  |  |  |  | 1 |  | 70 |  | B0354 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 19 |  |  |  |  | 1 |  | 70 |  | B0355 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP004RS | RCP002RG |  | 11 |  |  |  |  | 2 |  | 2.5 |  | B0481 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0407 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 20 |  |  |  |  | 1 |  | 70 |  | B0408 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 18 |  |  |  |  | 1 |  | 70 |  | B0409 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 18 |  |  |  |  | 1 |  | 70 |  | B0410 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 18 |  |  |  |  | 1 |  | 70 |  | B0411 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP002RG | RCP004RS |  | 18 |  |  |  |  | 1 |  | 70 |  | B0412 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | J2527 | RCP005VP |  | 73 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | J2830 | RCP006VP |  | 69 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | E1315 | RCP007VP |  | 50 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | E0103 | RCP008RS |  | 51 |  |  |  |  | 3 |  | 6 |  | B0014 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | E0103 | RCP009RS |  | 67 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | E0103 | RCP010RS |  | 76 |  |  |  |  | 3 |  | 6 |  | B0016 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 26 |  |  |  |  | 1 |  | 70 |  | B0461 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 26 |  |  |  |  | 1 |  | 70 |  | B0462 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 26 |  |  |  |  | 1 |  | 70 |  | B0463 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 21 |  |  |  |  | 1 |  | 70 |  | B0464 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 21 |  |  |  |  | 1 |  | 70 |  | B0465 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L347 | RCP060CR |  | 21 |  |  |  |  | 1 |  | 70 |  | B0466 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0455 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0456 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0457 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0458 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCV |  |  |  | PN1L309 | RCV088VP |  | 56 |  |  |  |  | 12 |  | 1.5 |  | C0033 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L309 | RCV050VP |  | 99 |  |  |  |  | 12 |  | 1.5 |  | C0051 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV002VP |  | 52 |  |  |  |  | 12 |  | 1.5 |  | C0303 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV003VP |  | 61 |  |  |  |  | 12 |  | 1.5 |  | C0308 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV227VP |  | 61 |  |  |  |  | 12 |  | 1.5 |  | C0312 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV082VP |  | 64 |  |  |  |  | 12 |  | 1.5 |  | C0334 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV257VP |  | 72 |  |  |  |  | 12 |  | 1.5 |  | C0350 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV007VP |  | 64 |  |  |  |  | 12 |  | 1.5 |  | C0357 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV008VP |  | 64 |  |  |  |  | 12 |  | 1.5 |  | C0364 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L337 | RCV009VP |  | 61 |  |  |  |  | 12 |  | 1.5 |  | C0384 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L339 | RCV310VP |  | 65 |  |  |  |  | 12 |  | 1.5 |  | C0386 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L339 | RCV002VP |  | 53 |  |  |  |  | 12 |  | 1.5 |  | C0409 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | RCV005CR | RCV003VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0440 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | RCV005CR | RCV227VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0441 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | RCV005CR | RCV008VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0442 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | RCV005CR | RCV007VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0446 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | RCV005CR | RCV009VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0447 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L339 | RCV082VP |  | 65 |  |  |  |  | 12 |  | 1.5 |  | C0448 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L339 | RCV310VP |  | 61 |  |  |  |  | 12 |  | 1.5 |  | C0474 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L345 | RCV250VP |  | 33 |  |  |  |  | 12 |  | 1.5 |  | C0498 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | NO | SR | 5
1-2 | RCV |  |  |  | PN1L518 | RCV038MD |  | 72 |  |  |  |  | 1PTB |  | 1 |  | M0305 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | RCV |  |  |  | PN1L518 | RCV001MT |  | 74 |  |  |  |  | 1TTB |  | 1 |  | M0339 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 4
1-2 | RCV |  |  |  | PN1L518 | RCV019MT |  | 55 |  |  |  |  | 1TTB |  | 1 |  | M0341 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 4
1-2 | RCV |  |  |  | PN1L517 | RCV048MP |  | 69 |  |  |  |  | 1PTB |  | 1 |  | M0365 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | RCV |  |  |  | PN1L517 | RCV049MT |  | 68 |  |  |  |  | 1TTB |  | 1 |  | M0376 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | RCV |  |  |  | LHA0202 | RCV001PO |  | 102 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCV |  |  |  | LHA0302 | RCV003PO |  | 108 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCV |  |  |  | LHB0302 | RCV002PO |  | 75 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RCV |  |  |  | LKC0309 | RCV076VP |  | 147 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LKC0507 | RCV078VP |  | 161 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LKC0508 | RCV077VP |  | 159 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0501 | RCV085VP |  | 132 |  |  |  |  | 3 |  | 2.5 |  | B0021 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0502 | RCV083VP |  | 125 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0503 | RCV060VP |  | 148 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0504 | RCV053VP |  | 140 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0506 | RCV033VP |  | 171 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0507 | RCV006PO |  | 144 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0508 | RCV004PO |  | 134 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLC0602 | RCV223VP |  | 143 |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0412 | RCV005PO |  | 89 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0504 | RCV222VP |  | 80 |  |  |  |  | 3 |  | 2.5 |  | B0022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0505 | RCV089VP |  | 70 |  |  |  |  | 3 |  | 2.5 |  | B0020 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0506 | RCV086VP |  | 88 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0507 | RCV084VP |  | 92 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0510 | RCV054VP |  | 79 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0511 | RCV048VP |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCV |  |  |  | LLD0512 | RCV034VP |  | 104 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0459 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L348 | RCP060CR |  | 27 |  |  |  |  | 1 |  | 70 |  | B0460 | [16 empty] | Critical | [11 empty] | B | ALU CFG |  | 380 Vac | YES | CSR | 3
9 | SER |  |  |  | 9LKN0608 | 9SER006VD |  | 42 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | RCP |  |  |  | RCP002RG | RCP073RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0489 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | PN1L310 | RCP212VP |  | 101 |  |  |  |  | 3 |  | 6 |  | B0047 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 2
1-2 | RCP |  |  |  | PN1L344 | RCP215VP |  | 43 |  |  |  |  | 3 |  | 6 |  | B0046 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 2
1-2 | RCP |  |  |  | RCP050CR | RCP511RS |  | 19 |  |  |  |  | 2 |  | 16 |  | B0389 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP512RS |  | 19 |  |  |  |  | 2 |  | 16 |  | B0390 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | REA |  |  |  | LLD0502 | REA210VB |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | REA |  |  |  | LLI0101 | REA001PO |  | 247 |  |  |  |  | 3 |  | 70 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | REA |  |  |  | LLJ0103 | REA002PO |  | 231 |  |  |  |  | 3 |  | 70 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | REA |  |  |  | REA001BX | REA003PO |  | 5 |  |  |  |  | 3 |  | 16 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | REA |  |  |  | REA002BX | REA004PO |  | 5 |  |  |  |  | 3 |  | 16 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | REN |  |  |  | PN1L307 | REN101VP |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0303 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN102VP |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0304 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN121VP |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0305 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN122VP |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0311 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN123VB |  | 66 |  |  |  |  | 12 |  | 1.5 |  | C0312 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN124VP |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0313 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN161VB |  | 37 |  |  |  |  | 12 |  | 1.5 |  | C0316 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN162VB |  | 51 |  |  |  |  | 12 |  | 1.5 |  | C0317 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN163VB |  | 63 |  |  |  |  | 12 |  | 1.5 |  | C0318 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN231VY |  | 37 |  |  |  |  | 12 |  | 1.5 |  | C0320 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | REN |  |  |  | PN1L307 | REN235VY |  | 37 |  |  |  |  | 12 |  | 1.5 |  | C0323 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0322 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0325 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0328 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0331 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0334 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0337 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0340 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0343 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0346 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0349 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0352 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0355 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0358 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0361 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0364 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 144 |  |  |  |  | 6 |  | 1.5 |  | M0367 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 27 |  |  |  |  | 6 |  | 1.5 |  | M0372 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0382 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0385 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0388 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0391 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0394 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 45 |  |  |  |  | 6 |  | 1.5 |  | M0397 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 48 |  |  |  |  | 6 |  | 1.5 |  | M0400 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 48 |  |  |  |  | 6 |  | 1.5 |  | M0403 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L523 | RGL009AR |  | 47 |  |  |  |  | 6 |  | 1.5 |  | M0406 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 47 |  |  |  |  | 6 |  | 1.5 |  | M0409 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 47 |  |  |  |  | 6 |  | 1.5 |  | M0412 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0415 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0418 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0421 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0424 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0427 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0442 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0445 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0448 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0451 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0454 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0457 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0460 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0463 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0466 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0469 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0472 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0475 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0478 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0481 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0484 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | PN1L524 | RGL009AR |  | 40 |  |  |  |  | 6 |  | 1.5 |  | M0487 | [16 empty] | Economic | [11 empty] | M | PVC DPTB |  | 30 Vdc | NO | AR | 1
1-2 | RGL |  |  |  | RGL001PJ | RGL001BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0300 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL002AR | RGL012CR |  | 13 |  |  |  |  | 2 |  | 16 |  | B0339 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL012CR |  | 13 |  |  |  |  | 2 |  | 16 |  | B0340 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL012CR |  | 13 |  |  |  |  | 2 |  | 2.5 |  | B0341 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL001AR |  | 3 |  |  |  |  | 2 |  | 2.5 |  | B0342 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0343 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0345 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0347 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0349 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0395 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0397 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0399 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 20 |  |  |  |  | 2 |  | 10 |  | B0449 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0498 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002AR | RGL003AR |  | 7 |  |  |  |  | 2 |  | 6 |  | B0500 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL002PJ | RGL002BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0303 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL003PJ | RGL003BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0306 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0344 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0346 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0348 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0386 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0387 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0389 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0391 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0393 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0396 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0398 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 20 |  |  |  |  | 2 |  | 10 |  | B0448 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0489 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0490 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0492 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0494 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0496 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0499 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL003AR |  | 6 |  |  |  |  | 2 |  | 6 |  | B0501 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0504 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004AR | RGL006AR |  | 3 |  |  |  |  | 2 |  | 6 |  | B0506 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL004PJ | RGL004BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0309 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL002AR |  | 6 |  |  |  |  | 2 |  | 150 |  | B0336 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL002AR |  | 6 |  |  |  |  | 2 |  | 150 |  | B0337 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL002AR |  | 6 |  |  |  |  | 2 |  | 150 |  | B0338 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0388 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0390 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0392 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0394 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0491 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0493 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0495 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0497 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0505 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005AR | RGL006AR |  | 5 |  |  |  |  | 2 |  | 6 |  | B0507 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RGL |  |  |  | RGL005PJ | RGL005BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0362 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL006PJ | RGL006BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0365 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL007PJ | RGL007BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0368 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL008PJ | RGL008BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0371 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL009PJ | RGL009BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0424 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL010PJ | RGL010BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0427 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL011PJ | RGL011BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0430 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL012PJ | RGL012BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0433 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL013PJ | RGL013BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0436 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL014PJ | RGL014BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0439 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL015PJ | RGL015BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0442 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL016PJ | RGL016BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0445 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL017PJ | RGL017BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0312 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL018PJ | RGL018BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0315 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL019PJ | RGL019BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0318 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL020PJ | RGL020BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0321 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL021PJ | RGL021BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0350 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL022PJ | RGL022BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0353 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL023PJ | RGL023BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0356 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL024PJ | RGL024BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0359 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL025PJ | RGL025BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0412 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL026PJ | RGL026BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0415 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL027PJ | RGL027BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0418 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL028PJ | RGL028BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0421 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL029PJ | RGL029BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0462 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL030PJ | RGL030BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0465 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL031PJ | RGL031BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0468 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL032PJ | RGL032BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0471 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL033PJ | RGL033BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0324 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL034PJ | RGL034BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0327 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL035PJ | RGL035BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0330 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL036PJ | RGL036BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0333 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL037PJ | RGL037BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0374 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL038PJ | RGL038BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0377 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL039PJ | RGL039BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0380 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL040PJ | RGL040BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0383 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL041PJ | RGL041BK |  | 20 |  |  |  |  | 2 |  | 6 |  | B0400 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL042PJ | RGL042BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0403 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL043PJ | RGL043BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0406 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL044PJ | RGL044BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0409 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL045PJ | RGL045BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0474 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL046PJ | RGL046BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0477 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL047PJ | RGL047BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0480 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RGL |  |  |  | RGL048PJ | RGL048BK |  | 20 |  |  |  |  | 2 |  | 10 |  | B0483 | [16 empty] | Economic | [11 empty] | B | QDIA |  | 380 Vac | NO | AR | 3
1-2 | RIC |  |  |  | RICA001PJ | RIC001MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0540 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA004PJ | RIC004MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0541 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA006PJ | RIC006MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0542 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA009PJ | RIC009MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0543 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA010PJ | RIC010MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0544 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA013PJ | RIC013MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0545 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA015PJ | RIC015MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0546 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA017PJ | RIC017MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0547 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA018PJ | RIC018MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0548 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA019PJ | RIC019MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0549 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA021PJ | RIC021MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0550 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA023PJ | RIC023MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0551 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA024PJ | RIC024MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0552 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA026PJ | RIC026MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0553 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA029PJ | RIC029MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0554 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA031PJ | RIC031MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0555 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA033PJ | RIC033MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0556 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA037PJ | RIC037MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0557 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA038PJ | RIC038MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0558 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA040PJ | RIC040MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0559 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA042PJ | RIC042MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0560 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA044PJ | RIC044MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0561 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA046PJ | RIC046MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0562 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA047PJ | RIC047MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0563 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA050PJ | RIC050MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0564 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB002PJ | RIC002MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0565 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB003PJ | RIC003MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0566 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB005PJ | RIC005MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0567 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB007PJ | RIC007MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0568 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB008PJ | RIC008MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0569 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB011PJ | RIC011MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0570 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB012PJ | RIC012MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0571 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB014PJ | RIC014MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0572 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB016PJ | RIC016MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0573 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB020PJ | RIC020MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0574 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB022PJ | RIC022MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0575 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB025PJ | RIC025MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0576 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB027PJ | RIC027MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0577 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB028PJ | RIC028MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0578 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB030PJ | RIC030MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0579 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB032PJ | RIC032MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0580 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB034PJ | RIC034MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0581 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB035PJ | RIC035MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0582 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB036PJ | RIC036MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0583 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB039PJ | RIC039MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0584 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB041PJ | RIC041MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0585 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB043PJ | RIC043MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0586 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB045PJ | RIC045MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0587 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB048PJ | RIC048MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0588 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB049PJ | RIC049MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0589 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB051PJ | RIC051MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0590 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA001PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0591 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA004PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0592 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA006PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0593 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA009PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0594 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA010PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0595 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA013PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0596 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA015PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0597 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA017PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0598 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA018PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0599 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA019PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0600 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA021PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0601 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA023PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0602 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA024PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0603 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA026PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0604 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA029PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0605 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA031PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0606 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA033PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0607 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA037PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0608 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA038PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0609 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA040PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0610 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA042PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0611 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA044PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0612 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA046PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0613 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA047PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0614 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICA050PJ | PN1L521 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0615 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB002PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0616 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB003PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0617 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB005PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0618 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB007PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0619 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB008PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0620 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB011PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0621 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB012PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0622 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB014PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0623 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB016PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0624 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB020PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0625 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB022PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0626 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB025PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0627 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB027PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0628 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB028PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0629 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB030PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0630 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB032PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0631 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB034PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0632 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB035PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0633 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB036PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0634 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB039PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0635 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB041PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0636 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB043PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0637 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB045PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0638 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB048PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0639 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB049PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0640 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RICB051PJ | PN1L520 |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0641 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | RIC001BS | RIC039MT |  | 20 |  |  |  |  | 1PTB |  | 0.5 |  | C0684 | [16 empty] | Significant | [11 empty] | C | PRECIBLE Z |  | 48 Vdc | YES | SR | 1
1-2 | RIC |  |  |  | PN1L519 | RIC100UC |  | 30 |  |  |  |  | 1K |  | 59.7 |  | M0336 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L519 | RIC200UC |  | 30 |  |  |  |  | 1K |  | 59.7 |  | M0338 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L519 | RIC300UC |  | 30 |  |  |  |  | 1K |  | 59.7 |  | M0340 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L519 | RIC400UC |  | 29 |  |  |  |  | 1K |  | 59.7 |  | M0342 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L519 | RIC500UC |  | 30 |  |  |  |  | 1K |  | 59.7 |  | M0344 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L521 | RIC100UC |  | 31 |  |  |  |  | 37 |  | 0.5 |  | M0346 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L521 | RIC200UC |  | 31 |  |  |  |  | 37 |  | 0.5 |  | M0348 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L521 | RIC300UC |  | 31 |  |  |  |  | 37 |  | 0.5 |  | M0350 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L521 | RIC400UC |  | 30 |  |  |  |  | 37 |  | 0.5 |  | M0352 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | PN1L521 | RIC500UC |  | 31 |  |  |  |  | 37 |  | 0.5 |  | M0354 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 1
1-2 | RIC |  |  |  | B0406 | RIC002AR |  | 72 |  |  |  |  | 3 |  | 6 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 1
1-2 | CFI |  |  |  | 9LKX002CR | CFI111VC |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0061 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | RCP |  |  |  | RCP050CR | RCP513RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0391 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP521RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0392 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP522RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0393 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RIS |  |  |  | LHA0301 | RIS001PO |  | 220 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RIS |  |  |  | LHB0301 | RIS002PO |  | 138 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RIS |  |  |  | LLC0604 | RIS021VP |  | 124 |  |  |  |  | 3 |  | 2.5 |  | B0021 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0603 | RIS085VB |  | 147 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0606 | RIS013VP |  | 146 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0607 | RIS033VP |  | 120 |  |  |  |  | 3 |  | 2.5 |  | B0024 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0608 | RIS035VP |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0609 | RIS052VP |  | 140 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0610 | RIS062VP |  | 138 |  |  |  |  | 3 |  | 6 |  | B0030 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0611 | RIS064VP |  | 147 |  |  |  |  | 3 |  | 6 |  | B0032 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0612 | RIS078VP |  | 146 |  |  |  |  | 3 |  | 2.5 |  | B0034 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0711 | RIS145VP |  | 162 |  |  |  |  | 3 |  | 2.5 |  | B0022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLD0712 | RIS144VP |  | 159 |  |  |  |  | 3 |  | 2.5 |  | B0020 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0405 | RIS021PO |  | 87 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0408 | RIS075VB |  | 186 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0503 | RIS133VP |  | 196 |  |  |  |  | 3 |  | 2.5 |  | B0037 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0504 | RIS132VP |  | 197 |  |  |  |  | 3 |  | 2.5 |  | B0035 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0505 | RIS077VP |  | 201 |  |  |  |  | 3 |  | 2.5 |  | B0033 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0506 | RIS063VP |  | 175 |  |  |  |  | 3 |  | 6 |  | B0031 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0507 | RIS061VP |  | 183 |  |  |  |  | 3 |  | 6 |  | B0029 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0508 | RIS051VP |  | 201 |  |  |  |  | 3 |  | 2.5 |  | B0027 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0509 | RIS034VP |  | 153 |  |  |  |  | 3 |  | 2.5 |  | B0025 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0510 | RIS032VP |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0023 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0511 | RIS020VP |  | 144 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RIS |  |  |  | LLE0512 | RIS012VP |  | 208 |  |  |  |  | 3 |  | 6 |  | B0017 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RPB |  |  |  | RPB001TB | RGL002AR |  | 20 |  |  |  |  | 4 |  | 150 |  | B0400 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | RPB |  |  |  | RPB001TB | RGL002AR |  | 20 |  |  |  |  | 4 |  | 150 |  | B0401 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | RPB |  |  |  | RPB001TB | RGL002AR |  | 20 |  |  |  |  | 4 |  | 150 |  | B0402 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | RPE |  |  |  | PN1L337 | RPE002VY |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0302 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RPE |  |  |  | PN1L337 | RPE017VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0325 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RPE |  |  |  | PN1L337 | RPE027VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0326 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RPE |  |  |  | PN1L337 | RPE055VE |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0327 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RPE |  |  |  | RPE002CR | RPE056VE |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0454 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | W1
1-2 | RPE |  |  |  | PN1L522 | RPE002MN |  | 30 |  |  |  |  | 1PTB |  | 1 |  | M0300 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | RPE |  |  |  | PN1L522 | RPE003MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0302 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | RPE |  |  |  | PN1L522 | RPE008MN |  | 94 |  |  |  |  | 1PTB |  | 1 |  | M0304 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | RPE |  |  |  | PN1L522 | RPE015MN |  | 94 |  |  |  |  | 1PTB |  | 1 |  | M0306 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | RPE |  |  |  | PN1L522 | RPE011MT |  | 31 |  |  |  |  | 1TTB |  | 1 |  | M0313 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | AR | 2
1-2 | RPE |  |  |  | A0103 | RPE001PO |  | 49 |  |  |  |  | 3 |  | 16 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | RPE |  |  |  | A0103 | RPE002PO |  | 49 |  |  |  |  | 3 |  | 16 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | RPE |  |  |  | E0709 | RPE014PO |  | 56 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | RPE |  |  |  | LKH0504 | RPE029PO |  | 74 |  |  |  |  | 3 |  | 16 |  | B0026 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RPN |  |  |  | PN1L514 | RPN014MA |  | 65 |  |  |  |  | 1K |  | 59.7 |  | M0501 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN013MA |  | 65 |  |  |  |  | 1K |  | 59.7 |  | M0502 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN013MA |  | 65 |  |  |  |  | 1K |  | 59.7 |  | M0503 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN013MA |  | 65 |  |  |  |  | 1K |  | 59.7 |  | M0504 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN010MA |  | 71 |  |  |  |  | 1K |  | 59.7 |  | M0505 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN010MA |  | 71 |  |  |  |  | 1K |  | 59.7 |  | M0506 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN010MA |  | 71 |  |  |  |  | 1K |  | 59.7 |  | M0507 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN013MA |  | 65 |  |  |  |  | 1K |  | 59.7 |  | M0508 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L514 | RPN010MA |  | 71 |  |  |  |  | 1K |  | 59.7 |  | M0509 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN024MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0510 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN023MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0511 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN023MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0512 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN023MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0513 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN020MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0514 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN020MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0515 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN020MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0516 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN023MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0517 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L530 | RPN020MA |  | 46 |  |  |  |  | 1K |  | 59.7 |  | M0518 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN034MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0519 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN030MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0520 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN030MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0521 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN030MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0522 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN033MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0523 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN033MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0524 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN033MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0525 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L516 | RPN030MA |  | 49 |  |  |  |  | 1K |  | 59.7 |  | M0526 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN040MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0527 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN040MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0528 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN040MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0529 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN043MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0530 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN043MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0531 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN043MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0532 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RPN |  |  |  | PN1L534 | RPN040MA |  | 35 |  |  |  |  | 1K |  | 59.7 |  | M0533 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | NO | CSR | 1
1-2 | RRA |  |  |  | PN1L309 | RRA001VP |  | 109 |  |  |  |  | 12 |  | 1.5 |  | C0005 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L345 | RRA021VP |  | 38 |  |  |  |  | 12 |  | 1.5 |  | C0006 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L309 | RRA014VP |  | 51 |  |  |  |  | 12 |  | 1.5 |  | C0011 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L345 | RRA015VP |  | 115 |  |  |  |  | 12 |  | 1.5 |  | C0012 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L339 | RRA001VP |  | 74 |  |  |  |  | 12 |  | 1.5 |  | C0313 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | RRA020CR | RRA012VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0315 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L339 | RRA014VP |  | 65 |  |  |  |  | 12 |  | 1.5 |  | C0317 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | RRA020CR | RRA013VP |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0319 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L307 | RRA020CR |  | 71 |  |  |  |  | 12 |  | 1.5 |  | C0362 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L345 | RRA021VP |  | 33 |  |  |  |  | 12 |  | 1.5 |  | C0460 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L345 | RRA015VP |  | 105 |  |  |  |  | 12 |  | 1.5 |  | C0464 | [16 empty] | Significant | [11 empty] | C | PVC |  | 48 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA010MT |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0001 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA022MT |  | 76 |  |  |  |  | 1PTB |  | 1 |  | M0002 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA024MT |  | 75 |  |  |  |  | 1PTB |  | 1 |  | M0003 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA012MT |  | 75 |  |  |  |  | 1PTB |  | 1 |  | M0004 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA014MT |  | 70 |  |  |  |  | 1PTB |  | 1 |  | M0005 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA026MT |  | 76 |  |  |  |  | 1PTB |  | 1 |  | M0006 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA011MT |  | 79 |  |  |  |  | 1TTB |  | 1 |  | M0007 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA023MT |  | 79 |  |  |  |  | 1PTB |  | 1 |  | M0008 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA025MT |  | 78 |  |  |  |  | 1PTB |  | 1 |  | M0009 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA013MT |  | 74 |  |  |  |  | 1PTB |  | 1 |  | M0010 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA015MT |  | 75 |  |  |  |  | 1PTB |  | 1 |  | M0011 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L528 | RRA027MT |  | 73 |  |  |  |  | 1PTB |  | 1 |  | M0012 | [16 empty] | Significant | [11 empty] | M | VZBA |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L522 | RRA004MP |  | 74 |  |  |  |  | 1TTB |  | 1 |  | M0300 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | NO | SR | 2
1-2 | RRA |  |  |  | PN1L522 | RRA006MD |  | 79 |  |  |  |  | 1PTB |  | 1 |  | M0303 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L522 | RRA005MT |  | 61 |  |  |  |  | 1TTB |  | 1 |  | M0309 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L518 | RRA007MT |  | 86 |  |  |  |  | 1TTB |  | 1 |  | M0311 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | 1
1-2 | RRA |  |  |  | PN1L522 | RRA013VP |  | 80 |  |  |  |  | 1PTB |  | 1 |  | M0319 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | PN1L522 | RRA012VP |  | 80 |  |  |  |  | 1PTB |  | 1 |  | M0320 | [16 empty] | Significant | [11 empty] | M | PVC |  | 30 Vdc | YES | SR | 2
1-2 | RRA |  |  |  | LHA0501 | PN1L305 |  | 33 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRA |  |  |  | LHB0601 | PN1L349 |  | 41 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRA |  |  |  | PN1L305 | RRA001MO |  | 79 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Significant | [11 empty] | A | ALU CGF |  | 6.6 kV | YES | SR | 2
1-2 | RCP |  |  |  | RCP050CR | RCP523RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0394 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP531RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0395 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP532RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0396 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP533RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0397 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RRA |  |  |  | PN1L349 | RRA002MO |  | 106 |  |  |  |  | 3 |  | 50 |  | A0004 | [16 empty] | Significant | [11 empty] | A | ALU CGF |  | 6.6 kV | YES | SR | 2
1-2 | RRB |  |  |  | LLC0607 | RRB001TB |  | 150 |  |  |  |  | 3 |  | 35 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RRB |  |  |  | LLC0610 | RRB003TB |  | 236 |  |  |  |  | 3 |  | 50 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RRB |  |  |  | LLC0610 | RRB003TB |  | 217 |  |  |  |  | 3 |  | 50 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RRB |  |  |  | LLD0703 | RRB004TB |  | 144 |  |  |  |  | 3 |  | 35 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RRB |  |  |  | LLD0707 | RRB002TB |  | 53 |  |  |  |  | 3 |  | 35 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | RRB |  |  |  | RRB109AR | RRB001TB |  | 94 |  |  |  |  | 2 |  | 16 |  | B0311 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | N1
1-2 | RRB |  |  |  | RRB109AR | RRB001TB |  | 94 |  |  |  |  | 2 |  | 2.5 |  | B0406 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | N1
1-2 | RRB |  |  |  | RRB209AR | RRB002TB |  | 53 |  |  |  |  | 2 |  | 2.5 |  | B0493 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | N1
1-2 | RRB |  |  |  | RRB209AR | RRB002TB |  | 53 |  |  |  |  | 2 |  | 16 |  | B0511 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | AR | N1
1-2 | RRI |  |  |  | PN1L312 | RRI189VN |  | 71 |  |  |  |  | 12 |  | 1.5 |  | C0061 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI318VN |  | 64 |  |  |  |  | 12 |  | 1.5 |  | C0067 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI319VN |  | 67 |  |  |  |  | 12 |  | 1.5 |  | C0073 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI280VN |  | 65 |  |  |  |  | 12 |  | 1.5 |  | C0079 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI281VN |  | 61 |  |  |  |  | 12 |  | 1.5 |  | C0085 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI282VN |  | 70 |  |  |  |  | 12 |  | 1.5 |  | C0091 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L343 | RRI020VN |  | 114 |  |  |  |  | 12 |  | 1.5 |  | C0102 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | RRI |  |  |  | PN1L312 | RRI019VN |  | 71 |  |  |  |  | 12 |  | 1.5 |  | C0105 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | 2
1-2 | CFI |  |  |  | 9LKX002CR | CFI112VC |  | 52 |  |  |  |  | 3 |  | 2.5 |  | B0062 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | 9LKX002CR | CFI113VC |  | 46 |  |  |  |  | 3 |  | 2.5 |  | B0063 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | 9LKX002CR | CFI111VC |  | 61 |  |  |  |  | 3 |  | 2.5 |  | B0064 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | CFI |  |  |  | 9LKX002CR | CFI112VC |  | 75 |  |  |  |  | 3 |  | 2.5 |  | B0065 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | RRI |  |  |  | LHA0903 | RRI001PO |  | 150 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRI |  |  |  | LHA1003 | RRI003PO |  | 152 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRI |  |  |  | LHB0903 | RRI002PO |  | 108 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRI |  |  |  | LHB1003 | RRI004PO |  | 108 |  |  |  |  | 3 |  | 50 |  | A0004 | [16 empty] | Significant | [11 empty] | A | MTAL |  | 6.6 kV | NO | SR | L1
1-2 | RRI |  |  |  | LLD0706 | RRI551VN |  | 129 |  |  |  |  | 3 |  | 2.5 |  | B0032 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLE0501 | RRI041VN |  | 190 |  |  |  |  | 3 |  | 2.5 |  | B0025 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLE0601 | RRI058VN |  | 162 |  |  |  |  | 3 |  | 2.5 |  | B0027 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLE0602 | RRI146VN |  | 190 |  |  |  |  | 3 |  | 2.5 |  | B0029 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLE0609 | RRI465VN |  | 95 |  |  |  |  | 3 |  | 2.5 |  | B0035 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLE0610 | RRI466VN |  | 102 |  |  |  |  | 3 |  | 2.5 |  | B0037 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0301 | RRI170VN |  | 176 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0302 | RRI059VN |  | 152 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0303 | RRI040VN |  | 158 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0401 | RRI177VN |  | 177 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0402 | RRI210VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0403 | RRI211VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0404 | RRI212VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0405 | RRI283VN |  | 175 |  |  |  |  | 3 |  | 2.5 |  | B0020 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0406 | RRI284VN |  | 175 |  |  |  |  | 3 |  | 2.5 |  | B0022 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0407 | RRI285VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0024 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0408 | RRI300VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0409 | RRI304VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0028 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RRI |  |  |  | LLJ0410 | RRI313VN |  | 173 |  |  |  |  | 3 |  | 2.5 |  | B0030 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | RCP |  |  |  | RCP050CR | RCP541RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0398 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP542RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0399 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP050CR | RCP543RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0400 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP611RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0467 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP612RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0468 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP613RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0469 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP621RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0470 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP622RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0471 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP623RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0472 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP631RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0473 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP632RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0474 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCP |  |  |  | RCP060CR | RCP633RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0475 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | SAP |  |  |  | LGC0801 | SAP001CO |  | 128 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | AR | L1
1-2 | SAP |  |  |  | LKF0508 | SAP201VA |  | 53 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SAP |  |  |  | LLI0201 | SAP101CO |  | 39 |  |  |  |  | 3 |  | 185 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SAP |  |  |  | LLJ0201 | SAP102CO |  | 101 |  |  |  |  | 3 |  | 185 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SAR |  |  |  | LLB0503 | SAR432VA |  | 146 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
9 | SDA |  |  |  | 9LKN0103 | 9SDA004PO |  | 79 |  |  |  |  | 3 |  | 16 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | 9LKN0105 | 9SDA005PO |  | 79 |  |  |  |  | 3 |  | 16 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | 9LKN0107 | 9SDA006PO |  | 80 |  |  |  |  | 3 |  | 16 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | 9LKN0407 | 9SDA003PO |  | 77 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | 9LKN0408 | 9SDA002PO |  | 78 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDA |  |  |  | 9LKN0409 | 9SDA001PO |  | 77 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | RCP |  |  |  | RCP060CR | RCP641RS |  | 20 |  |  |  |  | 2 |  | 16 |  | B0476 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 3
1-2 | RCV |  |  |  | PN1L310 | RCV050VP |  | 95 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 5
1-2 | RCV |  |  |  | PN1L310 | RCV088VP |  | 54 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | YES | CSR | 5
1-2 | RIS |  |  |  | C0103 | RIS001VP |  | 60 |  |  |  |  | 3 |  | 16 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
1-2 | RIS |  |  |  | C0406 | RIS002VP |  | 70 |  |  |  |  | 3 |  | 16 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
1-2 | RIS |  |  |  | G0103 | RIS003VP |  | 103 |  |  |  |  | 3 |  | 16 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
1-2 | RRA |  |  |  | PN1L310 | RRA001VP |  | 106 |  |  |  |  | 3 |  | 6 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
9 | SDX |  |  |  | 2ATE101AR | 9SDX013PO |  | 97 |  |  |  |  | 3 |  | 2.5 |  | B0045 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 2ATE101AR | 9SDX014PO |  | 19 |  |  |  |  | 3 |  | 2.5 |  | B0052 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | CFI |  |  |  | 9LKX002CR | CFI113VC |  | 61 |  |  |  |  | 3 |  | 2.5 |  | B0066 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SEC |  |  |  | 9LKX002CR | 1SEC201VE |  | 168 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | 9LKX002CR | 1SEC201VE |  | 138 |  |  |  |  | 3 |  | 2.5 |  | B0018 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | YES | NSA | X2
9 | GRV |  |  |  | 9LKZ0201 | 9GRV001RE |  | 269 |  |  |  |  | 3 |  | 70 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | LHS |  |  |  | 9LLM001TR | 9LHS007ZV |  | 189 |  |  |  |  | 3 |  | 2.5 |  | B0026 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | X1
9 | SDX |  |  |  | 9LKN0305 | 9SDX030PO |  | 104 |  |  |  |  | 3 |  | 2.5 |  | B0058 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0306 | 9SDX029PO |  | 103 |  |  |  |  | 3 |  | 2.5 |  | B0057 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0307 | 9SDX028PO |  | 101 |  |  |  |  | 3 |  | 2.5 |  | B0056 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0308 | 9SDX027PO |  | 92 |  |  |  |  | 3 |  | 2.5 |  | B0055 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0309 | 9SDX025PO |  | 72 |  |  |  |  | 3 |  | 2.5 |  | B0033 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0310 | 9SDX026PO |  | 84 |  |  |  |  | 3 |  | 2.5 |  | B0034 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LHS |  |  |  | 9LLV0105 | 9LHS002ZV |  | 46 |  |  |  |  | 3 |  | 70 |  | B0013 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0107 | 9LHS001ZV |  | 50 |  |  |  |  | 3 |  | 70 |  | B0012 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | SDX |  |  |  | 9LKN0412 | 9SDX021PO |  | 62 |  |  |  |  | 3 |  | 2.5 |  | B0024 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0502 | 9SDX009PO |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0503 | 9SDX008PO |  | 75 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0504 | 9SDX007PO |  | 76 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0505 | 9SDX006PO |  | 77 |  |  |  |  | 3 |  | 2.5 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0506 | 9SDX005PO |  | 81 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0507 | 9SDX004PO |  | 82 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0508 | 9SDX003PO |  | 85 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0509 | 9SDX002PO |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0510 | 9SDX001PO |  | 96 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0602 | 9SDX022PO |  | 51 |  |  |  |  | 3 |  | 2.5 |  | B0025 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0701 | 9SDX020PO |  | 80 |  |  |  |  | 3 |  | 50 |  | B0023 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0703 | 9SDX019PO |  | 91 |  |  |  |  | 3 |  | 50 |  | B0022 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0705 | 9SDX018PO |  | 67 |  |  |  |  | 3 |  | 50 |  | B0021 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9LKN0707 | 9SDX017PO |  | 72 |  |  |  |  | 3 |  | 50 |  | B0020 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SDX |  |  |  | 9SDA201AR | 9SDX024PO |  | 31 |  |  |  |  | 3 |  | 2.5 |  | B0049 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
9 | SDX |  |  |  | 9SDA201AR | 9SDX023PO |  | 111 |  |  |  |  | 3 |  | 2.5 |  | B0050 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | RRA |  |  |  | PN1L310 | RRA014VP |  | 57 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRA |  |  |  | PN1L344 | RRA015VP |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRA |  |  |  | PN1L344 | RRA021VP |  | 71 |  |  |  |  | 3 |  | 6 |  | B0014 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI019VN |  | 72 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L344 | RRI020VN |  | 107 |  |  |  |  | 3 |  | 2.5 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI189VN |  | 71 |  |  |  |  | 3 |  | 2.5 |  | B0013 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI280VN |  | 63 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI281VN |  | 64 |  |  |  |  | 3 |  | 2.5 |  | B0017 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI282VN |  | 70 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI318VN |  | 64 |  |  |  |  | 3 |  | 2.5 |  | B0031 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1-2 | RRI |  |  |  | PN1L310 | RRI319VN |  | 64 |  |  |  |  | 3 |  | 2.5 |  | B0033 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | YES | SR | 2
1 | SEC |  |  |  | 9LKX002CR | 1SEC012AR |  | 112 |  |  |  |  | 12 |  | 1.5 |  | C0075 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 33 |  |  |  |  | 7 |  | 1.5 |  | C0615 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 33 |  |  |  |  | 7 |  | 1.5 |  | C0616 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 35 |  |  |  |  | 19 |  | 1.5 |  | C0618 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC003CR | SEC012AR |  | 18 |  |  |  |  | 12 |  | 1.5 |  | C0622 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC003CR | SEC012AR |  | 18 |  |  |  |  | 12 |  | 1.5 |  | C0623 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC012AR |  | 29 |  |  |  |  | 37 |  | 1.5 |  | C0625 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC003CR | SEC012AR |  | 18 |  |  |  |  | 3 |  | 1.5 |  | C0629 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC003CR | SEC012AR |  | 18 |  |  |  |  | 3 |  | 1.5 |  | C0630 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC012AR |  | 16 |  |  |  |  | 2 |  | 1.5 |  | C0635 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC012AR |  | 16 |  |  |  |  | 2 |  | 1.5 |  | C0636 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC012AR |  | 30 |  |  |  |  | 2 |  | 1.5 |  | C0637 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC003CR | SEC012AR |  | 18 |  |  |  |  | 3 |  | 1.5 |  | C0639 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 48 |  |  |  |  | 2 |  | 1.5 |  | C0651 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 49 |  |  |  |  | 2 |  | 1.5 |  | C0652 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 41 |  |  |  |  | 2 |  | 1.5 |  | C0655 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC001CR | SEC012AR |  | 35 |  |  |  |  | 2 |  | 1.5 |  | C0656 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 51 |  |  |  |  | 19 |  | 1.5 |  | C0714 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 63 |  |  |  |  | 7 |  | 1.5 |  | C0715 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 63 |  |  |  |  | 7 |  | 1.5 |  | C0716 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC004CR | SEC012AR |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0721 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC004CR | SEC012AR |  | 19 |  |  |  |  | 12 |  | 1.5 |  | C0722 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC012AR |  | 20 |  |  |  |  | 37 |  | 1.5 |  | C0725 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC004CR | SEC012AR |  | 19 |  |  |  |  | 3 |  | 1.5 |  | C0729 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC004CR | SEC012AR |  | 20 |  |  |  |  | 3 |  | 1.5 |  | C0730 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC012AR |  | 31 |  |  |  |  | 2 |  | 1.5 |  | C0735 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC012AR |  | 17 |  |  |  |  | 2 |  | 1.5 |  | C0736 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC012AR |  | 26 |  |  |  |  | 2 |  | 1.5 |  | C0737 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC004CR | SEC012AR |  | 19 |  |  |  |  | 3 |  | 1.5 |  | C0739 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 42 |  |  |  |  | 2 |  | 1.5 |  | C0755 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC002CR | SEC012AR |  | 38 |  |  |  |  | 2 |  | 1.5 |  | C0756 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 90 |  |  |  |  | 37 |  | 1.5 |  | C0905 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC031UB |  | 92 |  |  |  |  | 2 |  | 1.5 |  | C0907 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC001AR |  | 100 |  |  |  |  | 2 |  | 1.5 |  | C0908 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC005AR |  | 99 |  |  |  |  | 2 |  | 1.5 |  | C0909 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC900CR |  | 95 |  |  |  |  | 19 |  | 1.5 |  | C0911 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X3
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 90 |  |  |  |  | 37 |  | 1.5 |  | C0955 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X4
1-2 | SEC |  |  |  | SEC012AR | SEC002AR |  | 150 |  |  |  |  | 2 |  | 1.5 |  | C0957 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X5
1-2 | SEC |  |  |  | SEC012AR | SEC004AR |  | 91 |  |  |  |  | 2 |  | 1.5 |  | C0958 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X6
1-2 | SEC |  |  |  | SEC012AR | SEC006AR |  | 99 |  |  |  |  | 2 |  | 1.5 |  | C0959 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X7
1-2 | SEC |  |  |  | SEC012AR | SEC905CR |  | 95 |  |  |  |  | 19 |  | 1.5 |  | C0961 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | NSA | X8
1-2 | SEC |  |  |  | SEC019CR | SEC001MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0600 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC002MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0601 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC013MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0602 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC014MT |  | 20 |  |  |  |  | 1TTB |  | 1 |  | M0603 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC025MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0604 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC026MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0605 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC029MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0606 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC030MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0607 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC031MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0608 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC032MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0609 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC035MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0610 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC036MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0611 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC037MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0612 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC038MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0613 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC019CR | SEC043MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0614 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC020CR | SEC044MT |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0615 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC015CR | SEC001MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0616 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC015CR | SEC002MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0619 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AM | SEC001MD |  | 70 |  |  |  |  | 2 |  | COAXIAL |  | M0620 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | I1
1-2 | SEC |  |  |  | SEC012AM | SEC002MD |  | 70 |  |  |  |  | 2 |  | COAXIAL |  | M0621 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | N1
1-2 | SEC |  |  |  | SEC011AM | SEC001MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0622 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | I1
1-2 | SEC |  |  |  | SEC012AM | SEC002MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0623 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | N1
1-2 | SEC |  |  |  | SEC011AM | SEC001MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0624 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | I1
1-2 | SEC |  |  |  | SEC012AM | SEC002MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0625 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | N1
1-2 | SEC |  |  |  | SEC011AM | SEC001MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0626 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | I1
1-2 | SEC |  |  |  | SEC012AM | SEC002MD |  | Site Run |  |  |  |  | 2 |  | COAXIAL |  | M0627 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | N1
1-2 | SEC |  |  |  | KRG012CR | SEC011AR |  | Site Run |  |  |  |  | 1PTB |  | 1 |  | M0901 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | I1
1-2 | SEC |  |  |  | KRG012CR | SEC012AM |  | Site Run |  |  |  |  | 1PTB |  | 1 |  | M0902 | [16 empty] | Economic | [11 empty] | M | PVC |  | 30 Vdc | NO | NSA | N1
9 | LHS |  |  |  | 9LLV0204 | 9LHS001CO |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0205 | 9LHS002CO |  | 20 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | SEC |  |  |  | LHA0902 | SEC001PO |  | 284 |  |  |  |  | 3 |  | 50 |  | A0001 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | NSA | L1
1-2 | SEC |  |  |  | LHA1002 | SEC003PO |  | 279 |  |  |  |  | 3 |  | 50 |  | A0003 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | NSA | L1
1-2 | SEC |  |  |  | LHB0902 | SEC002PO |  | 254 |  |  |  |  | 3 |  | 50 |  | A0002 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | NSA | L1
1-2 | SEC |  |  |  | LHB1002 | SEC004PO |  | 248 |  |  |  |  | 3 |  | 50 |  | A0004 | [16 empty] | Economic | [11 empty] | A | MTAL |  | 6.6 kV | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0404 | SEC010FI |  | 279 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0405 | SEC012FI |  | 270 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0501 | SEC002MO |  | 279 |  |  |  |  | 3 |  | 6 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0502 | SEC012AR |  | 287 |  |  |  |  | 3 |  | 6 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0601 | SEC004MO |  | 279 |  |  |  |  | 3 |  | 16 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0602 | SEC006PO |  | 221 |  |  |  |  | 3 |  | 35 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0603 | SEC008PO |  | 232 |  |  |  |  | 3 |  | 35 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLB0604 | SEC002RS |  | 284 |  |  |  |  | 3 |  | 2.5 |  | B0016 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | LLE0301 | SEC011FI |  | 275 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0302 | SEC009FI |  | 274 |  |  |  |  | 3 |  | 2.5 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0611 | SEC011AR |  | 295 |  |  |  |  | 3 |  | 6 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0612 | SEC001MO |  | 284 |  |  |  |  | 3 |  | 6 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0709 | SEC001RS |  | 294 |  |  |  |  | 3 |  | 2.5 |  | B0015 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | LLE0710 | SEC007PO |  | 248 |  |  |  |  | 3 |  | 35 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0711 | SEC005PO |  | 237 |  |  |  |  | 3 |  | 35 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LLE0712 | SEC003MO |  | 286 |  |  |  |  | 3 |  | 16 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SEC |  |  |  | LMJ102CR | SEC011AM |  | 5 |  |  |  |  | 4 |  | 2.5 |  | B0105 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | I1
1-2 | SEC |  |  |  | LMK102CR | SEC012AM |  | 5 |  |  |  |  | 4 |  | 2.5 |  | B0104 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | N1
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0600 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0601 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0602 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0603 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0604 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 29 |  |  |  |  | 3 |  | 2.5 |  | B0605 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0900 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0901 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0902 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0903 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0904 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC011AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0905 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0700 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0701 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0702 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0703 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0704 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 27 |  |  |  |  | 3 |  | 2.5 |  | B0705 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC007CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0950 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0951 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0952 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0953 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 91 |  |  |  |  | 3 |  | 2.5 |  | B0954 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
1-2 | SEC |  |  |  | SEC012AR | SEC008CR |  | 90 |  |  |  |  | 3 |  | 2.5 |  | B0955 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 220 Vac | NO | NSA | X2
9 | SED |  |  |  | 9LKK0101 | 9SED001PO |  | 320 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SED |  |  |  | 9LKK0207 | 9SED002PO |  | 314 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LHS |  |  |  | 9LLV0207 | 9LHS001RS |  | 50 |  |  |  |  | 3 |  | 2.5 |  | B0019 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | RRM |  |  |  | DKH | RRM001ZV |  | 46 |  |  |  |  | 3 |  | 185 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RRM |  |  |  | DFH | RRM002ZV |  | 74 |  |  |  |  | 3 |  | 185 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | RRM |  |  |  | DHF | RRM003ZV |  | 60 |  |  |  |  | 3 |  | 185 |  | B0013 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
0 | SEK |  |  |  | 9LKX0103 | 0SEK002PO |  | 212 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | SEK |  |  |  | 9LKX0103 | 0SEK002PO |  | 214 |  |  |  |  | 3 |  | 50 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | SEK |  |  |  | 9LKX0105 | 0SEK001PO |  | 185 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
0 | SEK |  |  |  | 9LKX0105 | 0SEK001PO |  | 215 |  |  |  |  | 3 |  | 50 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LHS |  |  |  | 9LLV0212 | 9LHS001RE |  | 40 |  |  |  |  | 3 |  | 16 |  | B0009 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0212 | 9LHS004RE |  | 16 |  |  |  |  | 3 |  | 16 |  | B0025 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0305 | 9LHS006ZV |  | 45 |  |  |  |  | 3 |  | 16 |  | B0017 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0306 | 9LHS005ZV |  | 41 |  |  |  |  | 3 |  | 16 |  | B0016 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | SER |  |  |  | 9LKN0101 | 9SER001PO |  | 61 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SER |  |  |  | 9LKN0201 | 9SER002PO |  | 59 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | SER |  |  |  | 9LKN0203 | 9SER003PO |  | 57 |  |  |  |  | 3 |  | 50 |  | B0003 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
9 | LHS |  |  |  | 9LLV0307 | 9LHS004ZV |  | 40 |  |  |  |  | 3 |  | 16 |  | B0015 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0308 | 9LHS003ZV |  | 38 |  |  |  |  | 3 |  | 16 |  | B0014 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0311 | 9LHS003RE |  | 15 |  |  |  |  | 3 |  | 2.5 |  | B0011 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
9 | LHS |  |  |  | 9LLV0312 | 9LHS002RE |  | 38 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Critical | [11 empty] | B | A (PVC) |  | 380 Vac | NO | CSR | L1
1-2 | SRI |  |  |  | SRI001BX | SRI001PO |  | 12 |  |  |  |  | 3 |  | 185 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | SRI |  |  |  | SRI002BX | SRI002PO |  | 14 |  |  |  |  | 3 |  | 185 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | SRI |  |  |  | SRI003BX | SRI003PO |  | 11 |  |  |  |  | 3 |  | 185 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL |  | 23 |  |  |  |  | 1 |  | 185 |  | B0503 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL |  | 23 |  |  |  |  | 1 |  | 185 |  | B0515 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSA303BN | 6SSC001DL |  | 23 |  |  |  |  | 1 |  | 185 |  | B0518 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0535 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL |  | 14 |  |  |  |  | 1 |  | 185 |  | B0536 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL |  | 10 |  |  |  |  | 1 |  | 185 |  | B0543 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC001TR | 6SSC001DL |  | 10 |  |  |  |  | 1 |  | 185 |  | B0544 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC700CR | 6SSC001DL |  | 26 |  |  |  |  | 1 |  | 185 |  | B0506 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSC |  |  |  | 6SSC700CR | 6SSC001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0517 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0503 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0513 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSB303BN | 6SSD001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0525 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL |  | 14 |  |  |  |  | 1 |  | 185 |  | B0535 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL |  | 14 |  |  |  |  | 1 |  | 185 |  | B0536 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL |  | 10 |  |  |  |  | 1 |  | 185 |  | B0543 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD001TR | 6SSD001DL |  | 10 |  |  |  |  | 1 |  | 185 |  | B0544 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD700CR | 6SSD001DL |  | 16 |  |  |  |  | 1 |  | 185 |  | B0506 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
6 | SSD |  |  |  | 6SSD700CR | 6SSD001DL |  | 15 |  |  |  |  | 1 |  | 185 |  | B0515 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | X1
1-2 | RRM |  |  |  | ADG | RRM004ZV |  | 77 |  |  |  |  | 3 |  | 185 |  | B0014 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | 1
1-2 | STR |  |  |  | LKA0101 | STR001PO |  | 63 |  |  |  |  | 3 |  | 50 |  | B0001 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | STR |  |  |  | LKB0209 | STR002PO |  | 100 |  |  |  |  | 3 |  | 50 |  | B0002 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | NSA | L1
1-2 | SXS |  |  |  | LKE0101 | SXS005PO |  | 157 |  |  |  |  | 3 |  | 50 |  | B0007 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SXS |  |  |  | LKE0205 | SXS004PO |  | 152 |  |  |  |  | 3 |  | 185 |  | B0006 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SXS |  |  |  | LKE0403 | SXS006PO |  | 162 |  |  |  |  | 3 |  | 16 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | L1
1-2 | SXS |  |  |  | SXS501AR | SXS501PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0601 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SXS |  |  |  | SXS501AR | SXS503PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0602 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SXS |  |  |  | SXS502AR | SXS502PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0701 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SXS |  |  |  | SXS502AR | SXS504PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0702 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SXS |  |  |  | SXS503AR | SXS505PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0603 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | SXS |  |  |  | SXS504AR | SXS506PO |  | 20 |  |  |  |  | 3 |  | 6 |  | B0703 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
1-2 | TEG |  |  |  | LKJ0405 | TEG001RS |  | 99 |  |  |  |  | 3 |  | 16 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | TEG |  |  |  | LKJ0406 | TEG001CO |  | 84 |  |  |  |  | 3 |  | 16 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | TEG |  |  |  | LKJ0407 | TEG001ZV |  | 92 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0103 | 9TEP007PO |  | 55 |  |  |  |  | 3 |  | 50 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0407 | 9TEP005PO |  | 59 |  |  |  |  | 3 |  | 2.5 |  | B0001 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0408 | 9TEP006PO |  | 59 |  |  |  |  | 3 |  | 2.5 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0409 | 9TEP008PO |  | 82 |  |  |  |  | 3 |  | 6 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0410 | 9TEP011PO |  | 69 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0411 | 9TEP010PO |  | 78 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0412 | 9TEP009PO |  | 66 |  |  |  |  | 3 |  | 6 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0510 | 9TEP014PO |  | 70 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0511 | 9TEP013PO |  | 80 |  |  |  |  | 3 |  | 16 |  | B0009 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEP |  |  |  | 9LKI0512 | 9TEP012PO |  | 80 |  |  |  |  | 3 |  | 16 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
1-2 | TEP |  |  |  | LKJ0408 | TEP003PO |  | 68 |  |  |  |  | 3 |  | 70 |  | B0002 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
1-2 | TEP |  |  |  | TEP001BX | TEP001PO |  | 72 |  |  |  |  | 3 |  | 16 |  | B0003 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
9 | TES |  |  |  | 9LKI0501 | 9TES004MO |  | 191 |  |  |  |  | 3 |  | 35 |  | B0010 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | LNF |  |  |  | 9LNF0352 | 9KRT501AR |  | 22 |  |  |  |  | 2 |  | 6 |  | B0019 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 220 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0703 | 9TEU014PO |  | 225 |  |  |  |  | 3 |  | 35 |  | B0012 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0707 | 9TEU008PO |  | 117 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0708 | 9TEU004PO |  | 55 |  |  |  |  | 3 |  | 2.5 |  | B0007 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0709 | 9TEU003PO |  | 72 |  |  |  |  | 3 |  | 2.5 |  | B0006 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0710 | 9TEU002PO |  | 55 |  |  |  |  | 3 |  | 2.5 |  | B0005 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | L1
9 | TEU |  |  |  | 9LKI0711 | 9TEU001PO |  | 56 |  |  |  |  | 3 |  | 2.5 |  | B0004 | [16 empty] | Significant | [11 empty] | B | A (PVC) |  | 380 Vac | NO | SR | N1
1-2 | VVP |  |  |  | VVP001CR | VVP170VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0306 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP001CR | VVP171VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0307 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP001CR | VVP172VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0308 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP006UB | VVP002CR |  | 81 |  |  |  |  | 12 |  | 1.5 |  | C0310 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP002CR | VVP160VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0311 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP002CR | VVP161VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0312 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP004CR | VVP270VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0320 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP004CR | VVP271VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0321 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP004CR | VVP272VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0322 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP005CR | VVP260VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0325 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP005CR | VVP261VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0326 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP007CR | VVP370VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0341 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP007CR | VVP371VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0342 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP007CR | VVP372VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0343 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP008CR | VVP360VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0346 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP008CR | VVP361VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0347 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP014UB | VVP127VV |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0355 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | W1
1-2 | VVP |  |  |  | VVP014UB | VVP128VV |  | 80 |  |  |  |  | 12 |  | 1.5 |  | C0357 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | W1
1-2 | VVP |  |  |  | VVP015UB | VVP129VV |  | 77 |  |  |  |  | 12 |  | 1.5 |  | C0359 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | W1
1-2 | VVP |  |  |  | VVP003CR | VVP180VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0556 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP003CR | VVP181VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0557 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP003CR | VVP182VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0558 | [16 empty] | Economic | [11 empty] | C | PVC |  | 48 Vdc | NO | AR | V1
1-2 | VVP |  |  |  | VVP006CR | VVP280VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0562 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP006CR | VVP281VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0563 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP006CR | VVP282VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0564 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP009CR | VVP380VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0568 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP009CR | VVP381VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0569 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | VVP009CR | VVP382VA |  | 20 |  |  |  |  | 12 |  | 1.5 |  | C0570 | [16 empty] | Critical | [11 empty] | C | PVC |  | 48 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG023AR | VVP007MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0300 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG023AR | VVP008MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0301 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG023AR | VVP009MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0302 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | PN1L515 | VVP004MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0303 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | VVP |  |  |  | PN1L515 | VVP005MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0305 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | VVP |  |  |  | PN1L515 | VVP006MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0307 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | VVP |  |  |  | KRG034AR | VVP010MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0309 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG034AR | VVP011MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0310 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG034AR | VVP012MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0311 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG041AR | VVP013MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0312 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG041AR | VVP014MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0313 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | KRG041AR | VVP015MP |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0314 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | V1
1-2 | VVP |  |  |  | PN1L533 | VVP001MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0315 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | VVP |  |  |  | PN1L533 | VVP002MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0317 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
1-2 | VVP |  |  |  | PN1L533 | VVP003MD |  | 20 |  |  |  |  | 1PTB |  | 1 |  | M0319 | [16 empty] | Critical | [11 empty] | M | PVC |  | 30 Vdc | YES | CSR | 3
9 | XCA |  |  |  | 9XCA004AR | 9XPA001PO |  | 48 |  |  |  |  | 3 |  | 2.5 |  | B0008 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | XCA |  |  |  | 9XCA004AR | 9XPA002PO |  | 47 |  |  |  |  | 3 |  | 2.5 |  | B0009 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | XCA |  |  |  | 9XCA004AR | 9XPA003PO |  | 50 |  |  |  |  | 3 |  | 2.5 |  | B0010 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | XCA |  |  |  | 9XCA004AR | 9XCA010PO |  | 39 |  |  |  |  | 2 |  | 2.5 |  | B0011 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1
9 | XCA |  |  |  | 9XCA004AR | 9XCA010PO |  | 1 |  |  |  |  | 2 |  | 2.5 |  | B0012 | [16 empty] | Economic | [11 empty] | B | A (PVC) |  | 380 Vac | NO | AR | X1

## Others, inc Fibre (hidden)
UNIT | SYSTEM | ER CLASS | CATEG | RGNB | EQUIPMENT_FROM | EQUIPMENT_TO | WAY_PU | LNGTH_CA | LNGTH_ES | LNGTH_PU | CBSC | CBTYP | Cores | Dimensions (mm2) | Cable Size & Core | CBTYP | Cable_No | Cable_Route | Salto_Scope_IN_OUT | CAMP IN-SCOPE | Note | KEY1 | NO. | TYPE OF TEST (OUTAGE) / FDR TEST | FREQ. | START DATE | TYPE OF TEST (ONLINE) | FREQ. | START DATE | V&T INSPECTIONS | FREQ | START DATE (Outage) | Align V&T inspections with VLF-TD to save time and resources | Critical/Signficant/ Economic | GENERAL DESCRIPTION | ER CLASS. | GENERAL DESCRIPTION | ER CLASS. | Not No. VFL | Not No. PD | Not No. Visual | GEOMK_FR | GEOMK_TO | MDMK | POLAR | CABLE TYPE | CABLE OUTER SHEET | CABLE INSULATION | CABLE VOLTAGE | EQ | IMPORTANCE CLASSIFICATION | ENVIRONMENTAL ZONE
0 | DNB |  |  |  | 0DNBA90CR | 0DNB002AN | [8 empty] | 4 X 4mm2 PVC |  | 0BN90905 |  | Out
0 | BZ1 |  |  |  | 0JDT007AR | EKHAYAEXISTINGISOLATOR |  |  |  | 2 |  |  |  |  | 3 X 1.5mm | NA | 0BZ110BZ1 | IND | In
0 | BZ2 |  |  |  | 0JDT010AR | 0JDT9100JSBULKSTORES |  |  |  | 3 |  |  |  |  | 3 X 1.5mm | NA | 0BZ220BZ2 | IND | In
0 | BZ3 |  |  |  | 0JDT9100AN | 0JDT9100JSBULKSTORES |  |  |  | 3 |  |  |  |  | 3 X 1.5mm | NA | 0BZ330BZ3 | IND | In
0 | BZ4 |  |  |  | 0JDT005AR | MSB |  |  |  | 2 |  |  |  |  | Twin & E 2.5mm | NA | 0BZ440BZ4 | IND - IND | In
0 | BZ5 |  |  |  | 0JDT7000AN | MSBSUBBOARD |  |  |  | 7 |  |  |  |  | Twin & E 2.5mm | NA | 0BZ550BZ5 | IND - | In
0 | BZ6 |  |  |  | 0JDT7001AN | 0JDT7000AN |  |  |  | 3 |  |  |  |  | Twin & E 2.5mme | NA | 0BZ660BZ6 | IND | In
0 | BZ7 |  |  |  | DOSIMETRYKITCHEN | DOSIMETRYLABMSB1STFLOOR |  |  |  | 35 |  |  |  |  | 3 X 2.5mm | A | 0BZ770BZ7 | IND - IND | Out
0 | BZ8 |  |  |  | 0JDT050CR | 0JDT1000ARHVCONTROLROOM |  |  |  | 35 |  |  |  |  | 3 x 4mm | NA | 0BZ880BZ8 | IND | Out
9 | BZ9 |  |  |  | 9JDT050CR | 9JDT1000AR |  |  |  | 35 |  |  |  |  | 3 X 4MM | NA | 0BZ990BZ9 | IND - IND | Out
0 | DNB |  |  |  | 0DNBA90CR | 0DNB001AN | [8 empty] | 4 X 4mm2 PVC |  | 0DN 90904 |  | Out
0 | DNB |  |  |  | 0DNB001AN | 0DNBA91CR | [8 empty] | 2 X 6mm2 PVC |  | 0DNB00906 |  | Out
0 | DNB |  |  |  | 0DNB002AN | 0DNBA91CR | [8 empty] | 2 X 6mm2 PVC |  | 0DNB00907 |  | Out
1 | DNP |  |  |  | 1DNP002CR | 1DNP003CR | [8 empty] | 3 x 16 mm2 SWA |  | 1DNP90900 |  | Out
1 | JDT |  |  |  | 1JDT509DT | 1JDT510DT | [8 empty] | 1P x 1mm2 |  | 1JDT00511 |  | In
1 | RCP |  |  |  | 1KIT002CQ-L509 | 1KIT103AR-L609 | [8 empty] | 64 x 0,22 mm2 |  | 1RCPK0118 |  | Out
1 | RCP |  |  |  | 1KIT003CQ-L609 | 1KIT105AR-L649 | [8 empty] | 64 x 0,22 mm2 |  | 1RCPK0381 |  | Out
1 | RPR |  |  |  | 1RPR901AR | 220VPLUG | [8 empty] | 0,5mm2 |  | 1RPRT0B01 |  | Out
1 | RPR |  |  |  | 1RPR901AR | CABLEREEL | [10 empty] | 1RPRT0C01 |  | Out
1 | RPR |  |  |  | CABLEREEL | 1RPR901AR | [10 empty] | 1RPRT0C02 |  | Out
1 | SEC |  |  |  | 1SEC201MT | 1KRG328CQ-SEC201CT | [8 empty] | 1TTB 1mm2 non armoured |  | 1SEC20201 |  | In
2 | ARE |  |  |  | 2KRG122AR | 2ARE005UB |  |  |  | 60 |  |  |  |  | 2 X 1,5 | NA | 2ARE00056 | 2L5 5482C-B, 5571A, 5471A, 5JT1B-A, 6001A-C, 6021A-E | In
2 | DMR |  |  |  | 2DMR001NP | 2DMR001UV | [8 empty] | 2c x 0,5mm2 |  | 2DMR90900 |  | Out
2 | DMR |  |  |  | 2DMR001PR-TB5 | 2DMR001NP | [8 empty] | 2c x 1,0mm2 |  | 2DMR90901 |  | Out
2 | LCA |  |  |  | 2LCA001BN | U2TRNBKIT | [8 empty] | 2 x 1.5mm2 Non - Armoured |  | 2LCA10195 |  | In
2 | LCC |  |  |  | 2KSAR00AR | T12.1 | [8 empty] | 12 x 1.5 mm2 Non-armoured |  | 2LCC90925 |  | In
2 | PTR |  |  |  | 2PTR004BX | 2PTR002BX |  |  |  | 180 |  |  |  |  | 3 x 185 | A | 2PTR00004 | IND,2L3042B,2L3K21A,2L2K21A,2L1K21A,2L1022B–A,2L1G02A,2L0G02A,2L0552A,2N0552A,2N1552C–B,2N1232A,2N1592A,2N1522A,2N1572A,2K0511A–H,2K0521A,2K2C51A,IND | In
2 | RCP |  |  |  | 2KIT002CQ-L549 | 2KIT103AR-L649 | [8 empty] | 64 x 0,22 mm2 |  | 2RCPK0118 |  | Out
2 | RCP |  |  |  | 2KIT003CQ-L609 | 2KIT105AR-L649 | [8 empty] | 64 x 0,22 mm2 |  | 2RCPK0381 |  | Out
2 | RPR |  |  |  | 2RPR901AR | 220VPLUG | [8 empty] | 0,5mm2 |  | 2RPRT0B01 |  | Out
2 | RPR |  |  |  | 2RPR901AR | CABLEREEL | [10 empty] | 2RPRT0C01 |  | Out
2 | RPR |  |  |  | CABLEREEL | 2RPR901AR | [10 empty] | 2RPRT0C02 |  | Out
2 | SIR | [15 empty] | 2SIR0SIR |  | Out
6 | DTL |  |  |  | 6LRAK02JS | 6LRAC01JS | [8 empty] | 11KV,25mm2,3C+ COPPER EARTH, PILC |  | 6LRAK0900 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0900 |  | Out
6 | DTL |  |  |  | 6LRAH01TB | 6LRAH01AR | [8 empty] | 4c x 70mm2 |  | 6LRAO0900 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0901 |  | Out
6 | DTL |  |  |  | 6LRAH01TB | 6LRAH02AR | [8 empty] | 4c x 70mm2 |  | 6LRAO0901 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0902 |  | Out
6 | DTL |  |  |  | 6LRAH01TB | 6LRAH03AR | [8 empty] | 4c x 70mm2 |  | 6LRAO0902 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0903 |  | Out
6 | DTL |  |  |  | 6LRAH01TB | 6LRAH04AR | [8 empty] | 4c x 70mm2 |  | 6LRAO0903 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0904 |  | Out
6 | DTL |  |  |  | 6LRAH04TB | 6LRAH05AR | [8 empty] | 3c x 10mm2 |  | 6LRAO0904 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0905 |  | Out
6 | DTL |  |  |  | 6LRAH04TB | 6LRAH06AR | [8 empty] | 3c x 10mm2 |  | 6LRAO0905 |  | Out
6 | DTL |  |  |  | TRANSF.DO2 | 9SRO001TB | [8 empty] | 1pr x 500mm2 (PILC) |  | 6LRAO0906 |  | Out
6 | DTL |  |  |  | 6LRAH04TB | 6LRAH07AR | [8 empty] | 3c x 10mm2 |  | 6LRAO0906 |  | Out
6 | DTL |  |  |  | 6LRAH04TB | 6LRAH08AR | [8 empty] | 3c x 10mm2 |  | 6LRAO0907 |  | Out
6 | DTL |  |  |  | 6LRAH01AR | 6LRAH016CR | [8 empty] | 4c x 70mm2 PVC SWA |  | 6LRAO0915 |  | Out
6 | DTL |  |  |  | 6LRAH01AR | 6HAG001AR | [8 empty] | 4c x 150mm2 PVC SWA |  | 6LRAO0916 |  | Out
6 | DTL |  |  |  | 6HAG001AR | 6HAGA01CR | [8 empty] | 4c x 70mm2 PVC SWA |  | 6LRAO0917 |  | Out
6 | DTL |  |  |  | 6HAG001AR | 6HAGB02CR | [8 empty] | 4c x 70mm2 PVC SWA |  | 6LRAO0918 |  | Out
6 | DTL |  |  |  | 6HAG001AR | 6HAGC03CR | [8 empty] | 4c x 70mm2 PVC SWA |  | 6LRAO0919 |  | Out
6 | DTL |  |  |  | 6HAG001AR | 6HAGD04CR | [8 empty] | 4c x 70mm2 PVC SWA |  | 6LRAO0920 |  | Out
6 | GPA |  |  |  | 6SSP500AR | 6SSP504AR | [8 empty] | CCTV camera |  | 6SSP000TV |  | Out
6 | GPA |  |  |  | 6SSP500AR | 6SSP505AR | [8 empty] | CCTV camera |  | 6SSP001TV |  | Out
6 | GEX |  |  |  | 6SSP523AR | 6SSP524AR | [8 empty] | CCTV camera |  | 6SSP002TV |  | Out
6 | GPA |  |  |  | 6SSP500AR | 6SSP505AR | [8 empty] | CCTV camera |  | 6SSP002TV |  | Out
6 | GEX |  |  |  | 6SSP519AR | 6SSP521AR | [8 empty] | CCTV camera |  | 6SSP003TV |  | Out
6 | GPA |  |  |  | 6SSP500AR | 6SSP505AR | [8 empty] | CCTV camera |  | 6SSP003TV |  | Out
6 | GPA |  |  |  | 6SSP500AR | 6SSP505AR | [8 empty] | CCTV camera |  | 6SSP004TV |  | Out
6 | GEX |  |  |  | 6SSD060BX | 6SSP523AR | [8 empty] | CCTV camera |  | 6SSP005TV |  | Out
6 | GEX |  |  |  | 6SSP519AR | 6SSP521AR | [8 empty] | CCTV camera |  | 6SSP006TV |  | Out
6 | GEX |  |  |  | 6SSP500AR | 6SSP501AR | [8 empty] | CCTV camera |  | 6SSP007TV |  | Out
6 | GEX |  |  |  | 6SSP500AR | 6SSP502AR | [8 empty] | CCTV camera |  | 6SSP008TV |  | Out
6 | GGR |  |  |  | 6SSP500AR | 6SSP503AR | [8 empty] | CCTV camera |  | 6SSP009TV |  | Out
6 | SST |  |  |  | 6SST073CR | 6SST073CR |  |  |  | 5 |  |  |  |  | 2 x FIBRE |  | 6SSTT0SST | IND - IND | Out
9 | JDT |  |  |  | 1LKA607JA | 9DAI005CR | [8 empty] | 3 Core x 4mm2 Armoured |  | 9DAI90900 |  | Out
9 | LNF |  |  |  | 9LNF530CR | 9JDT325CR |  |  |  | 20 |  |  |  |  | 3 X 2,5 | A | 9LNF90903 | N245IND 2241A 2C03A, 3C03A, 3102A N370 9N33182B IND | In
9 | LNF |  |  |  | 9LNF530CR5 | 9JDT326CR |  |  |  | 35 |  |  |  |  | 3 X 2,5 | A | 9LNF90904 | N245IND 2241A 2C03A, 3C03A, 4C03A | In
9 | LNF |  |  |  | 9LNF530CR5 | 9JDT324CR |  |  |  | 52 |  |  |  |  | 3 X 2,5 | A | 9LNF90905 | N245IND 2241A 2C03A, 3C03A, 3102A,N370,9N33182B N379 9N33182B, N317 9N33A52A 9N33311A, N327 9N33311A, N381, 9N33302B, N381 9N33151A IND | In
9 | LNF |  |  |  | 9LNF035JA | 9LNF530CR |  |  |  | 7 |  |  |  |  | 3 X 2,5 | A | 9LNF90906 | N245IND IND 9N22241A IND | In
9 | KRG |  |  |  | 9PMC330AR | 9PMC331PJ | [8 empty] | 4 x 0.75mm2 Power Cable |  | 9PMC30324 |  | Out
9 | KRT |  |  |  | 9TES053CR | 9TES204EF | [8 empty] | 3x1.5mm2 (LIME INLET CLOSE SOLENOID) |  | 9TES10026 |  | In
9 | 907 |  |  |  | 9DMN900MO | 9DMN900AR |  |  |  | 6 |  |  |  |  | 3X6 |  | B90770907 | IND | In
9 | 907 |  |  |  | 9DMN9028M | 9DMN902CR |  |  |  | 1 | [6 empty] | C90770907 | IND | In
9 | 908 |  |  |  | 9DMN902CR | 9DMN900AR |  |  |  | 17 |  |  |  |  | 12X1,5 |  | C90880908 | IND | In
9 | 909 |  |  |  | 9DMN901SN | 9DMN900AR |  |  |  | 4 |  |  |  |  | 2P |  | C90990909 | IND | In
9 | 909 |  |  |  | 9DMN903SN | 9DMN900AR |  |  |  | 6 |  |  |  |  | 2P |  | C90990909 | IND | In
9 | 910 |  |  |  | 9DMN9048M | 9DMN904SM |  |  |  | 3 | [6 empty] | C91000910 | IND | In
9 | 911 |  |  |  | 9DMN901EA | 9DMN900AR |  |  |  | 5 |  |  |  |  | 2P |  | C91110911 | IND | In
9 | 912 |  |  |  | 9DMN904EA | 9DMN900AR |  |  |  | 8 |  |  |  |  | 2P |  | C91220912 | IND | In
1 | 114 |  |  |  | 1KIT002CQ | 1KIT103AR |  |  |  | 15 |  |  |  |  | 64 X 0,5 | NA | E11440114 | 1L5554F - E - D | In
| 011 |  |  |  | SPLICEBOXINSEC | AR4 |  |  |  | 160 |  |  |  |  | 4 FIBRE | A | F0110F01 | IND - IND | Out
| 022 |  |  |  | SPLICEBOXINSEC | AR5 |  |  |  | 135 |  |  |  |  | 4 FIBRE | A | F0220F02 | IND - IND | Out
| 033 |  |  |  | SPLICEBOXINSEC | AR6 |  |  |  | 71 |  |  |  |  | 4 FIBRE | A | F0330F03 | IND - IND | Out
| 044 |  |  |  | SPLICEBOXINSEC | AR7 |  |  |  | 80 |  |  |  |  | 4 FIBRE | A | F0440F04 | IND - IND | Out
| 055 |  |  |  | CASELECTRONICROOMNO.1 | SPILCEBOXINSEC |  |  |  | 675 |  |  |  |  | 24 FIBRE | A | F0550F05 | IND - C-0G1233A - C-0G1213C,D - C-1M1163B - C-1M1016C,B,A - C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P - IND - M1L173D - M-9L1703C - M-9L1731A - M-9L1354A - M-2L1231A | Out
| 066 |  |  |  | SPLICEBOXINMABROOF | AROFPTZ7EXCISTING |  |  |  | 200 |  |  |  |  | 4 FIBRE | A | F0660F06 | IND - IND | Out
| 077 |  |  |  | SPLICEBOXINMABROOF | AROFPTZ8BOXES |  |  |  | 200 |  |  |  |  | 4 FIBRE | A | F0770F07 | IND - IND | Out
| 088 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXINMAB |  |  |  | 480 |  |  |  |  | 12 FIBRE | A | F0880F08 | IND - IND | Out
| 099 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXINACP2 |  |  |  | 500 |  |  |  |  | 24 FIBRE | A | F0990F09 | IND - IND | Out
| 100 |  |  |  | SPLICEBOXINACP2 | AR18INVIB |  |  |  | 120 |  |  |  |  | 6 FIBRE | A | F1000F10 | IND - IND | Out
| 111 |  |  |  | SPLICEBOXINMAB | SPLICEBOXMETALTOWER |  |  |  | 600 |  |  |  |  | 6 FIBRE |  | F1110F11 | IND - IND | Out
| 122 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXACP1TOWER |  |  |  | 1130 |  |  |  |  | 12 FIBRE |  | F1220F12 | IND - IND | Out
| 133 |  |  |  | SPLICEBOXACP1TOWER | AR |  |  |  | 500 |  |  |  |  | 4 FIBRE |  | F1330F13 | IND - IND | Out
| 144 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXINSAS |  |  |  | 420 |  |  |  |  | 24 FIBRE | A | F1440F14 | IND - C-0G1233A - C-0G1213C,D - C-1M1163B - C1M1A05 - C1M1016C,B,A - C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P - C-1L11J2A - C-1L21J2A - C-1L31J2A - C-1L41J4A - C-1L52J2A - C-1L6061C,J,K,N,P - C-1L6311C,D,E - IND - IND | Out
| 155 |  |  |  | SPLICEBOXINSAS | AR |  |  |  | 320 |  |  |  |  | 4 FIBRE |  | F1550F15 | IND - IND | Out
| 166 |  |  |  | SPLICEBOXINSAS | AR |  |  |  | 320 |  |  |  |  | 4 FIBRE |  | F1660F16 | IND - IND | Out
| 177 |  |  |  | SPLICEBOXINSAS | AR |  |  |  | 230 |  |  |  |  | 4 FIBRE |  | F1770F17 | IND - IND | Out
| 188 |  |  |  | SPLICEBOXINSAS | AR |  |  |  | 230 |  |  |  |  | 4 FIBRE |  | F1880F18 | IND - IND | Out
| 199 |  |  |  | SPLICEBOXINSAS | AR21STEAMBUNKER |  |  |  | 160 |  |  |  |  | 4 FIBRE | A | F1990F19 | IND - IND | Out
| 200 |  |  |  | SPLICEBOXINSAS | AR20 |  |  |  | 60 |  |  |  |  | 4 FIBRE | A | F2000F20 | IND - IND | Out
| 211 |  |  |  | SPLICEBOXINSAS | AR15SKICABIN |  |  |  | 190 |  |  |  |  | 4 FIBRE | A | F2110F21 | IND - IND | Out
| 222 |  |  |  | SPLICEBOXINSAS | AR16 |  |  |  | 190 |  |  |  |  | 4 FIBRE | A | F2220F22 | IND - IND | Out
| 233 |  |  |  | SPLICEBOXINSAS | AR9 |  |  |  | 280 |  |  |  |  | 4 FIBRE | A | F2330F23 | IND - IND | Out
| 244 |  |  |  | SPLICEBOXINSAS | AR10 |  |  |  | 280 |  |  |  |  | 4 FIBRE | A | F2440F24 | IND - IND | Out
6 | 255 |  |  |  | SPLICEBOXON7M | 6SSP090AR |  |  |  | 65 |  |  |  |  | 4 FIBRE | A | F2550F25 | IND - C-1L41J4A - C-1L52J2A - C1L6062C,H,G,F - C-1L6064E - M9L6501A,B,C - IND | Out
6 | 266 |  |  |  | SPLICEBOXON7M | 6SSP089AR |  |  |  | 40 |  |  |  |  | 4 FIBRE | A | F2660F26 | IND - C-1L41J4A - C-1L52J2A - C-1L5002H,G,F,E,D,C,B,A - IND - IND | Out
6 | 288 |  |  |  | SPLICEBOXON7M | 6SSP088AR |  |  |  | 20 |  |  |  |  | 12 FIBRE | A | F2880F28 | IND - IND | Out
| 299 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXON7MLEVEL |  |  |  | 450 |  |  |  |  | 24 FIBRE | A | F2990F29 | IND - C-0G1233A - C-0G1213C,D - C-1M1163B - C-1M1A05 - C1M1016C,B,A - C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P - C-1L11J2A - C-1L21J2A - C-1L31J2A - C-1L41J4A - IND | Out
| 300 |  |  |  | CASELECTRONICROOMNO.1 | SPLICEBOXINL208 |  |  |  | 400 |  |  |  |  | 24 FIBRE | A | F3000F30 | IND - C0 - 0G1233A - C-0G1213C,D - C-1M1163B - C1M1A05 - C1M1016C,B,A - C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P | Out
| 311 |  |  |  | SPLICEBOXINL208 | AR11L208 |  |  |  | 30 |  |  |  |  | 4 FIBRE | A | F3110F31 | IND - IND | Out
| 322 |  |  |  | SPLICEBOXINL208 | AR12 |  |  |  | 91 |  |  |  |  | 4 FIBRE | A | F3220F32 | IND - IND | Out
6 | 333 |  |  |  | SPLICEBOXINL208 | 6SSP071AR |  |  |  | 260 |  |  |  |  | 6 | A | F3330F33 | IND - IND - M2W6661A-A-M216572C-M2L6543A,B,C,D,E,F,G-C1L6491B-M1L6573L-K-M1L6501A-C1L6063E-C,-C1L51J4A-C1L41J4A-C1L31J4A-C1L21J3A | Out
6 | 333 |  |  |  | SPLICEBOXINL208 | 6SSP071AR |  |  |  | 260 |  |  |  |  | 6 FIBRE | A | F3330F33 | IND - IND - M2W661A,A - M216572C - M2L6543A,B,C,D,E,F,G - C1L6491B - M1L6573L-K - M1L6501A - C1L6063E ,C - C1L51J4A - C1L41J4A - C1L31J4A - C1L21J3A | Out
6 | 344 |  |  |  | SPLICEBOXINL208 | 6SSP072AR |  |  |  | 150 |  |  |  |  | 4 FIBRE | A | F3440F34 | IND - C-1L1023P,O,N,M,L,K,J,H,G,F - C-1L1004D,C | Out
| 355 |  |  |  | SPLICEBOXINL208 | SPLICEBOXINSEISMICB. |  |  |  | 200 |  |  |  |  | 12 FIBRE | A | F3550F35 | IND - M-1L173D - M9L1703 - C-M-9L1731A - M-9L1354A - M-2L1231A - C-2L1253D,E,F,G,H - C-2L1371A - M-2L1151A - M-2L1141A,B - IND | Out
| 366 |  |  |  | SPLICEBOXINL208 | AR13 |  |  |  | 90 |  |  |  |  | 4 FIBRE | A | F3660F36 | M-1L1111D - IND - IND | Out
| 377 |  |  |  | SPLICEBOXINL208 | AR14 |  |  |  | 120 |  |  |  |  | 4 FIBRE | A | F3770F37 | M - IND - M-1L173C - M9L1703C - M9L1731A - M9L1354A - M2L1231A - IND - IND | Out
| 388 |  |  |  | CASELECTRONICROOMNO.1 | AR |  |  |  | 1100 |  |  |  |  | 4 FIBRE |  | F3880F38 | IND - IND | Out
| 399 |  |  |  | SPLICEBOXINSEIMICB. | AR1 |  |  |  | 10 |  |  |  |  | 4 FIBRE | A | F3990F39 | IND - IND | Out
| 400 |  |  |  | SPLICEBOXINSEISMICB. | AR24 |  |  |  | 70 |  |  |  |  | 4 FIBRE | A | F4000F40 | IND - IND | Out
| 411 |  |  |  | SPLICEBOXINSEISMICB. | AR25 |  |  |  | 90 |  |  |  |  | 4 FIBRE | A | F4110F41 | IND - IND | Out
| 422 |  |  |  | SPLICEBOXINSEISMICB. | AR26 |  |  |  | 100 |  |  |  |  | 4 FIBRE | A | F4220F42 | IND - IND | Out
| 433 |  |  |  | SPLICEBOXINL208 | AR22 |  |  |  | 170 |  |  |  |  | 4 FIBRE | A | F4330F43 | M1L1111D,C,B,A - C1L1023E,D,C,B - IND - IND | Out
| 444 |  |  |  | SPLICEBOXINL208 | NEWAR |  |  |  | 160 |  |  |  |  | 4 FIBRE | A | F4440F44 | M1L1111D-C,B,A - C1L1023E,D,C,B - IND - IND | Out
| 455 |  |  |  | FN5 | SPLICEBOXINSEC |  |  |  | 380 |  |  |  |  | 4 FIBRE | A | F4550F45 | IND - IND - C2C0014O,A - C1C0015C-A - C2C444A-A | Out
| 466 |  |  |  | FN4 | SPLICEBOXINSEC |  |  |  | 425 |  |  |  |  | 4 FIBRE | A | F4660F46 | IND - IND | Out
| 477 |  |  |  | FN4 | FN3 |  |  |  | 300 |  |  |  |  | 4 FIBRE | A | F4770F47 | IND - IND | Out
| 488 |  |  |  | SPLICEBOXACP2&VIB | FN2 |  |  |  | 80 |  |  |  |  | 4 FIBRE | A | F4880F48 | IND - IND | Out
| 499 |  |  |  | FN2 | FN1 |  |  |  | 70 |  |  |  |  | 4 FIBRE | A | F4990F49 | IND - IND | Out
| 501 |  |  |  | CAS | ACP2LS |  |  |  | 516 |  |  |  |  | 24 CORE |  | F50110501 | IND - IND | Out
| 502 |  |  |  | CAS | EKHAYA |  |  |  | 803 |  |  |  |  | 12 CORE |  | F50220502 | IND - IND | Out
| 503 |  |  |  | CAS | SAS |  |  |  | 420 |  |  |  |  | 8 CORE |  | F50330503 | IND, -C-0G1233A, C-0G1213C,D, C-1M1163B, C1M1A05, C1M1A05, C,M1016C,B,A -C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P - C-1L11J2A - C-1L2132A - C-1L31JA - C-1L41J4A - C-1L52J2A - C-1L6061C,J,K,N,P - C-1L6311C,D,E - IND - IND | Out
| 504 |  |  |  | CAS | L208 |  |  |  | 400 |  |  |  |  | 24 CORE |  | F50440504 | IND - C-0G1233A - C-0G1213C,D - C-1M1163B - C1M1A05 - C1M1016C,B,A - C-1M1H16A - C-1L1023F,G,H,J,K,L,M,N,O,P | Out
| 505 |  |  |  | ACP2 | MABWEST |  |  |  | 320 |  |  |  |  | 12 CORE |  | F50550505 | IND - IND | Out
| 506 |  |  |  | MABWEST | MABEAST |  |  |  | 90 |  |  |  |  | 12 CORE |  | F50660506 | IND - IND | Out
| 507 |  |  |  | MABWEST | GS&A |  |  |  | 180 |  |  |  |  | 12 CORE |  | F50770507 | IND - IND | Out
| 508 |  |  |  | EKHAYA | ELECTRONICHUT |  |  |  | 410 |  |  |  |  | 12 CORE |  | F50880508 | IND - IND | Out
| 509 |  |  |  | CAS | LLW |  |  |  | 450 |  |  |  |  | 6 CORE |  | F50990509 | IND - IND | Out
| 510 |  |  |  | CAS | PETERSPENCER |  |  |  | 400 |  |  |  |  | 6 CORE |  | F51000510 | IND - IND | Out
| 511 |  |  |  | CAS | ISI-WEST |  |  |  | 150 |  |  |  |  | 6 CORE |  | F51110511 | IND - IND | Out
| 512 |  |  |  | CAS | ISI-EAST |  |  |  | 250 |  |  |  |  | 6 CORE |  | F51220512 | IND - IND | Out
| 513 |  |  |  | MMS | FIRESTATION |  |  |  | 300 |  |  |  |  | 6 CORE |  | F51330513 | IND - IND | Out
| 514 |  |  |  | CAS | MMS |  |  |  | 300 |  |  |  |  | 12 CORE |  | F51440514 | IND - IND | Out
| 521 |  |  |  | CHEMLAB | MAB |  |  |  | 350 |  |  |  |  | 6 CORE |  | F52110521 | IND - IND | Out
| 903 |  |  |  | L208 | SAS |  |  |  | 100 |  |  |  |  | 8 CORE |  | F90330903 | IND - C-1L11J2A - C-1L21J2A - C-1L31JA - C-1L41J4A - C-1L52J2A - C-1L6061C,J,K,N,P - C-1L6311C,D,E, IND - IND | Out
| 904 |  |  |  | ACP2 | ACP1VISITORSREC |  |  |  | 630 |  |  |  |  | 12 CORE |  | F90440904 | IND - IND | Out
| ++0 |  |  |  | 6SSK044AR | NEWBOOYH |  |  |  | 10 |  |  |  |  | 4 FIBRE | A | H++0H+ |  | Out
0 | 823 |  |  |  | 2KIT304AR | 0ESC003AR |  |  |  | 95 |  |  |  |  | 3PR +7CORE | NA | K82330823 | IND - M 5JB8A -6JB8A - 6551T-D - M67JA - 6501A - 6572A - IND M1L6561C - M9L6561B 2L6501R-J - 6721A - IND | In
1 | INK |  |  |  | 1KRG152AR | 1KRG151AR |  |  |  | 8 |  |  |  |  | 1PTB |  | LINKK0INK | IND | In
2 | INK |  |  |  | 2KRG152AR | 2KRG151AR |  |  |  | 8 |  |  |  |  | 1PTB |  | LINKK0INK | IND | In
1 | O90 |  |  |  | 001MD | 1ATE012 |  |  |  | 48 |  |  |  |  | 1P |  | MO9070907 | IND | Out
1 | O90 |  |  |  | 101MD | 1ATE012 |  |  |  | 44 |  |  |  |  | 1P |  | MO9080908 | IND | Out
1 | O90 |  |  |  | 201MD | 1ATE012 |  |  |  | 40 |  |  |  |  | 1P |  | MO9090909 | IND | Out
1 | O91 |  |  |  | 301MD | 1ATE012 |  |  |  | 34 |  |  |  |  | 1P |  | MO9100910 | IND | Out
1 | O91 |  |  |  | 401MD | 1ATE012 |  |  |  | 30 |  |  |  |  | 1P |  | MO9110911 | IND | Out
1 | O91 |  |  |  | 031MD | 1ATE012 |  |  |  | 37 |  |  |  |  | 1P X 1 |  | MO9120912 | IND | Out
1 | O91 |  |  |  | 151MD | 1ATE012 |  |  |  | 33 |  |  |  |  | 1P X 1 |  | MO9130913 | IND | Out
1 | O91 |  |  |  | 251MD | 1ATE012 |  |  |  | 28 |  |  |  |  | 1P X 1 |  | MO9140914 | IND | Out
1 | O91 |  |  |  | 351MD | 1ATE012 |  |  |  | 23 |  |  |  |  | 1P X 1 |  | MO9150915 | IND | Out
1 | O91 |  |  |  | 451MD | 1ATE012 |  |  |  | 18 |  |  |  |  | 1P X 1 |  | MO9160916 | IND | Out
| BAA |  |  |  | MAB | Framex |  |  |  | 780 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND. | Out
| BAA |  |  |  | DTV15,5m | NAB(RPOO) |  |  |  | 150 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND, 2L20J2A, 2L10J2A, 2L1231A, 9L1354A-B, 9L1731F, 9L1703C, IND, 1L1111D, 1JX2A, 2JX2A, 3JX2A, 4JX2A, 5JX2A, 6JX2A, 1L6492B-T, IND. | Out
1 | BAA |  |  |  | MAB | 15,5m |  |  |  | 470 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND, 1L6492B-T, 6JX2A, 5JX2A, 4JX2A, 3JX2A, 2JX2A, 1JX2A, 1L1111D, IND, 1L1703A-B, 9L1703C, 9L1731A, 9L1351A, 1M1121A-C, IND. | Out
| BAA |  |  |  | Framex | TSB(Hub2) |  |  |  | 265 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND. | Out
| BAA |  |  |  | Framex | TSB(Hub1) |  |  |  | 165 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND. | Out
| BAA |  |  |  | Framex | MWS/Civils |  |  |  | 105 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND. | Out
| BAA |  |  |  | Framex | MWS/WeldingWorkshop |  |  |  | 200 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND. | Out
| BAA |  |  |  | MAB | WeatherStation |  |  |  | 1289 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | KTC |  |  |  | 1590 |  |  |  |  | 24 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | ACP1 |  |  |  | 677 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | Simulator |  |  |  | 2116 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | DTV15,5m | PTWOffice |  |  |  | 100 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND, RISER, IND, 1L6751C-A, IND, 1L6553M-T, IND. | Out
| BAA |  |  |  | MSB | DemonPlant |  |  |  | 230 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | Conservation | Auditorium |  |  |  | 180 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | Bulkstores | ESL |  |  |  | 335 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | ACP1 | VisitorsCentre |  |  |  | 626 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | RadioStation |  |  |  | 1177 |  |  |  |  | 24 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | Edusec |  |  |  | 2116 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | Bulkstores |  |  |  | 1971 |  |  |  |  | 48 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | MAB | ACP2 |  |  |  | 308 |  |  |  |  | 24 core fibre | NA | TBAA0TBA | IND | Out
| BAA |  |  |  | ACP1 | Transport |  |  |  | 120 |  |  |  |  | 8 core fibre | NA | TBAA0TBA | IND | Out
2 | 101 |  |  |  | 2RGL104AR | 2RGL102AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10110101 | IND - IND | Out
1 | 102 |  |  |  | 1RGL106AR | 1RGL104AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10220102 | IND - IND | Out
2 | 102 |  |  |  | 2RGL106AR | 2RGL104AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10220102 | IND - IND | Out
1 | 103 |  |  |  | 1RGL103AR | 1RGL101AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10330103 | IND - IND | Out
2 | 103 |  |  |  | 2RGL103AR | 2RGL101AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10330103 | IND - IND | Out
1 | 104 |  |  |  | 1RGL105AR | 1RGL103AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10440104 | IND - IND | Out
1 | 104 |  |  |  | 1RGL105AR | 1RGL103AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10440104 | IND - IND | Out
2 | 104 |  |  |  | 2RGL105AR | 2RGL103AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10440104 | IND - IND | Out
1 | 105 |  |  |  | 1RGL108AR | 1RGL110AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10550105 | IND - IND | Out
2 | 105 |  |  |  | 2RGL108AR | 2RGL110AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10550105 | IND - IND | Out
1 | 106 |  |  |  | 1RGL110AR | 1RGL112AR |  |  |  | 4 |  |  |  |  | 2 X 2.5 | A | W10660106 | IND - IND | Out
2 | 106 |  |  |  | 2RGL110AR | 2RGL112AR |  |  |  | 4 |  |  |  |  | 2 X 2.5 | A | W10660106 | IND - IND | Out
1 | 107 |  |  |  | 1RGL107AR | 1RGL109AR |  |  |  | 3 |  |  |  |  | 2 x 2.5 | A | W10770107 | IND - IND | Out
2 | 107 |  |  |  | 2RGL107AR | 2RGL109AR |  |  |  | 3 |  |  |  |  | 2 x 2.5 | A | W10770107 | IND - IND | Out
1 | 108 |  |  |  | 1RGL109AR | 1RGL111AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10880108 | IND - IND | Out
2 | 108 |  |  |  | 2RGL109AR | 2RGL111AR |  |  |  | 4 |  |  |  |  | 2 x 2.5 | A | W10880108 | IND - IND | Out
2 | 109 |  |  |  | 2RGL101AR | 2RGL102AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W10990109 | IND - IND | Out
1 | 110 |  |  |  | 1RGL102AR | 1RGL104AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11000110 | IND - IND | Out
2 | 110 |  |  |  | 2RGL102AR | 2RGL104AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11000110 | IND - IND | Out
1 | 111 |  |  |  | 1RGL103AR | 1RGL101AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11110111 | IND - IND | Out
2 | 111 |  |  |  | 2RGL103AR | 2RGL101AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11110111 | IND - IND | Out
2 | 111 |  |  |  | 2RGL103AR | 2RGL101AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11110111 | IND - IND | Out
1 | 112 |  |  |  | 1RGL104AR | 1RGL106AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11220112 | IND - IND | Out
2 | 112 |  |  |  | 2RGL104AR | 2RGL106AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11220112 | IND - IND | Out
1 | 113 |  |  |  | 1RGL106AR | 1RGL105AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11330113 | IND - IND | Out
2 | 113 |  |  |  | 2RGL106AR | 2RGL105AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11330113 | IND - IND | Out
1 | 114 |  |  |  | 1RGL107AR | 1RGL108AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11440114 | IND - IND | Out
2 | 114 |  |  |  | 2RGL107AR | 2RGL108AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11440114 | IND - IND | Out
1 | 115 |  |  |  | 1RGL108AR | 1RGL110AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11550115 | IND - IND | Out
2 | 115 |  |  |  | 2RGL108AR | 2RGL110AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11550115 | IND - IND | Out
1 | 116 |  |  |  | 1RGL109AR | 1RGL107AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11660116 | IND - IND | Out
2 | 116 |  |  |  | 2RGL109AR | 2RGL107AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11660116 | IND - IND | Out
1 | 117 |  |  |  | 1RGL111AR | 1RGL109AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11770117 | IND - IND | Out
2 | 117 |  |  |  | 2RGL111AR | 2RGL109AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11770117 | IND - IND | Out
1 | 118 |  |  |  | 1RGL112AR | 1RGL111AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11880118 | IND - IND | Out
2 | 118 |  |  |  | 2RGL112AR | 2RGL111AR |  |  |  | 4 |  |  |  |  | 7 x 1.5 | NA | W11880118 | IND - IND | Out
1 | JDT |  |  |  | 1JDT001AR | 6JDT001CR | [8 empty] | 4 core FO 50/125µm Multimode |  | 1JDTF0001 |  | IN
2 | JDT |  |  |  | 2JDT001AR | 6JDT001CR | [8 empty] | 4 core FO 50/125µm Multimode |  | 2JDTF0001 |  | IN

## ROOM MASTER (hidden)
ROOM NUMBER | DESCRIPTION | SYSTEM | ENVIRONMENTAL ZONE
R010 | ACCESS GALLERY FOR ASPIRATION PIPING SUMPS | DVK | K1
R050 | ACCESS GALLERY FOR ASPIRATION PIPING SUMPS | DVK | K1
R110 | ANNULUS LOOP 1 | EVR | R2
R111 | SAFETY INJECTION ACCUMULATOR RIS LOOP 1 | EVR | R2
R112 | VENTILATION ROOM LOOP 1 (EVR FAN NO 1) | EVR | R2
R113 | COMMON AREA LOOP 1 | EVR | R2
R120 | ANNULUS LOOP 2 | EVR | R2
R121 | SAFETY INJECTION ACCUMULATOR RIS LOOP 2 | EVR | R2
R122 | VENTILATION ROOM LOOP 1 (EVR FAN NO 2) | EVR | R2
R123 | COMMON AREA LOOP 2 | EVR | R1
R130 | ANNULUS LOOP 3 | EVR | R2
R131 | SAFETY INJECTION ACCUMULATOR RIS LOOP 3 | EVR | R2
R132 | VENTILATION ROOM LOOP 1 (EVR FAN NO 3) | EVR | R2
R133 | COMMON AREA LOOP 3 | EVR | R2
R140 | ROOM UNDER REACTOR VESSEL | EVR | R1
R141 | IN-CORE INSTRUMENTATION ROOM | EVR | R1
R144 | RRA HEAT EXCHANGER ROOM | EVR | R2
R145 | RCV VALVES ROOM | EVR | R5
R146 | REGENERATIVE HEAT EXCHANGER RCV | EVR | R5
R147 | EVC VENTILATION ROOM (REACTOR PIT) | ETY | R2
R148 | PRIMARY WASTE TANK ROOM (RPE) | EVR | R2
R149 | PRIMARY WASTE TANK ROOM (RPE) | EVR | R2
R150 | ANNULUS LOOP 1 | EVR | R2
R151 | SAFETY INJECTION ACCUMULATOR RIS LOOP 1 | EVR | R2
R152 | VENTILATION ROOM LOOP 1 (EVR FAN NO 1) | EVR | R2
R153 | COMMON AREA LOOP 1 | EVR | R2
R160 | ANNULUS LOOP 2 | EVR | R2
R161 | SAFETY INJECTION ACCUMULATOR RIS LOOP 2 | EVR | R2
R162 | VENTILATION ROOM LOOP 1 (EVR FAN NO 2) | EVR | R2
R163 | DAMPER ISOLATING R163 | EVR | R1
R170 | ANNULUS LOOP 3 | EVR | R2
R171 | SAFETY INJECTION ACCUMULATOR RIS LOOP 3 | EVR | R2
R172 | VENTILATION ROOM LOOP 1 (EVR FAN NO 3) | EVR | R2
R173 | COMMON AREA LOOP 3 | EVR | R2
R180 | ROOM UNDER REACTOR VESSEL | EVR | R1
R181 | IN-CORE INSTRUMENTATION ROOM | EVR | R1
R183 | 02RPE LINE NUMBER 326TY | EVR | R2
R184 | RRA HEAT EXCHANGER ROOM | EVR | R2
R185 | RCV VALVES ROOM | EVR | R5
R186 | REGENERATIVE HEAT EXCHANGER RCV | EVR | R5
R187 | EVC VENTILATION ROOM (REACTOR PIT) | ETY | R2
R188 | PRIMARY WASTE TANK ROOM (RPE) | EVR | R2
R189 | PRIMARY WASTE TANK ROOM (RPE) | EVR | R2
R210 | ANNULUS LOOP 1 | EVR | R2
R211 | SAFETY INJECTION ACCUMULATOR RIS LOOP 1 | EVR | R2
R212 | HANDLING FLOOR | EVR | R2
R213 | COMMON AREA LOOP 1 | EVR | R2
R217 | VALVE - HOT LEG INJECTION LINE DRAIN. | EVR | R2
R220 | ANNULUS LOOP 2 | EVR | R2
R221 | SAFETY INJECTION ACCUMULATOR RIS LOOP 2 | EVR | R2
R222 | HANDLING FLOOR | EVR | R2
R223 | COMMON AREA LOOP 2 | EVR | R2
R230 | ANNULUS LOOP 3 | EVR | R2
R231 | SAFETY INJECTION ACCUMULATOR RIS LOOP 3 | EVR | R2
R232 | HANDLING FLOOR | EVR | R2
R233 | COMMON AREA LOOP 3 | EVR | R2
R240 | ROOM UNDER REACTOR VESSEL | EVR | R1
R241 | HANDLING HATCH AND ACCESS TO R 141 | EVR | R2
R242 | IODINE FILTER ROOM NO 1 (EVF) | EVR | R2
R243 | IODINE FILTER ROOM NO 2 (EVF) | EVR | R2
R244 | RRA HEAT EXCHANGERS | EVR | R2
R245 | RRA PUMP NO 1 | EVR | R2
R246 | RRA PUMP NO 2 | EVR | R2
R247 | HANDLING FLOOR TO EMERGENCY EXIT | EVR | R2
R248 | PRESSURIZER RELIEF TANK (RCP) | EVR | R2
R250 | ANNULUS LOOP 1 | EVR | R2
R251 | SAFETY INJECTION ACCUMULATOR RIS LOOP 1 | EVR | R2
R252 | HANDLING FLOOR | EVR | R2
R253 | COMMON AREA LOOP 1 | EVR | R2
R254 | VALVE ISOLATION EVF 002VA | EVR | R2
R257 | VALVE - BIT TANK 004BA OUTLET TEST. | EVR | R2
R260 | ANNULUS LOOP 2 | EVR | R2
R261 | SAFETY INJECTION ACCUMULATOR RIS LOOP 2 | EVR | R2
R262 | HANDLING FLOOR | EVR | R2
R263 | COMMON AREA LOOP 2 | EVR | R2
R268 | DAMPERS BALANCING R288 | EVR | R2
R270 | ANNULUS LOOP 3 | EVR | R2
R271 | SAFETY INJECTION ACCUMULATOR RIS LOOP 3 | EVR | R2
R272 | HANDLING FLOOR | EVR | R2
R273 | COMMON AREA LOOP 3 | EVR | R2
R280 | ROOM UNDER REACTOR VESSEL | EVR | R1
R281 | HANDLING HATCH AND ACCESS TO R 141 | EVR | R2
R282 | IODINE FILTER ROOM NO 1 (EVF) | EVR | R2
R283 | IODINE FILTER ROOM NO 2 (EVF) | EVR | R2
R284 | RRA HEAT EXCHANGERS | EVR | R2
R285 | RRA PUMP NO 1 | EVR | R2
R286 | RRA PUMP NO 2 | EVR | R2
R287 | HANDLING FLOOR TO EMERGENCY EXIT | EVR | R2
R288 | PRESSURIZER RELIEF TANK (RCP) | EVR | R2
R310 | ANNULUS LOOP 1 | EVR | R2
R311 | REACTOR COOLANT PUMP LOOP 1 (RCP) | EVR | R6
R312 | STEAM GENERATOR LOOP 1 (RCP) | EVR | R6
R313 | COMMON AREA LOOP 1 | EVR | R2
R315 | MANUAL ACTUATOR | EVR | R2
R320 | ANNULUS LOOP 2 | EVR | R2
R321 | REACTOR COOLANT PUMP LOOP 2 (RCP) | EVR | R6
R322 | STEAM GENERATOR LOOP 2 (RCP) | EVR | R6
R323 | COMMON AREA LOOP 2 | EVR | R2
R330 | ANNULUS LOOP 3 | EVR | R2
R331 | REACTOR COOLANT PUMP LOOP 3 (RCP) | EVR | R6
R332 | STEAM GENERATOR LOOP 3 (RCP) | EVR | R6
R333 | COMMON AREA LOOP 3 | EVR | R2
R340 | REACTOR VESSEL ROOM (RCP) | EVC | R1
R341 | CONTAINMENT CLEAN-UP VENTILATIONS (EVF) | EVR | R2
R342 | VALVE ISOLATION 002BA | EVR | R2
R344 | RRA HEAT EXCHANGERS | EVR | R2
R345 | EXCESS LET DOWN HEAT EXCHANGER (RCV) | EVR | R2
R346 | SRR TANK | EVR | R2
R347 | STORAGE FOR REACTOR HEAD | EVR | R2
R348 | PRESSURIZER RELIEF TANK | EVR | R2
R350 | ANNULUS LOOP 1 | EVR | R2
R351 | REACTOR COOLANT PUMP LOOP 1 (RCP) | EVR | R6
R352 | STEAM GENERATOR LOOP 1 (RCP) | EVR | R6
R353 | COMMON AREA LOOP 1 | EVR | R2
R354 | SENSOR FLOW - 01PO SEAL LEAK WIDE RANGE | EVR | R2
R360 | ANNULUS LOOP 2 | EVR | R2
R361 | REACTOR COOLANT PUMP LOOP 2 (RCP) | EVR | R6
R362 | STEAM GENERATOR LOOP 2 (RCP) | EVR | R6
R363 | COMMON AREA LOOP 2 | EVR | R2
R370 | ANNULUS LOOP 3 | EVR | R2
R371 | REACTOR COOLANT PUMP LOOP 3 (RCP) | EVR | R6
R372 | STEAM GENERATOR LOOP 3 (RCP) | EVR | R6
R373 | COMMON AREA LOOP 3 | EVR | R2
R380 | REACTOR VESSEL ROOM (RCP) | EVC | R1
R381 | CONTAINMENT CLEAN-UP VENTILATIONS (EVF) | EVR | R2
R384 | RRA HEAT EXCHANGERS | EVR | R2
R385 | EXCESS LET DOWN HEAT EXCHANGER (RCV) | EVR | R2
R386 | SRR TANK | EVR | R2
R387 | STORAGE FOR REACTOR HEAD | EVR | R2
R388 | PRESSURIZER RELIEF TANK | EVR | R2
R410 | ANNULUS LOOP 1 | EVR | R3
R411 | REACTOR COOLANT PUMP LOOP 1 | EVR | R6
R412 | STEAM GENERATOR LOOP 1 | EVR | R6
R413 | COMMON SPACE LOOP 1 | EVR | R3
R420 | ANNULUS LOOP 2 | EVR | R3
R421 | REACTOR COOLANT PUMP LOOP 2 | EVR | R6
R422 | STEAM GENERATOR LOOP 2 | EVR | R6
R423 | COMMON SPACE LOOP 2 | EVR | R3
R430 | ANNALUS LOOP 3 | EVR | R3
R431 | REACTOR COOLANT PUMP LOOP 3 | EVR | R6
R432 | STEAM GENERATOR LOOP 3 | EVR | R6
R433 | COMMON SPACE LOOP 3 | EVR | R3
R440 | REACTOR VESSEL ROOM | EVC | R1
R441 | ELEVATOR | EVR | R3
R444 | RRA HEAT EXCHANGERS | EVR | R3
R445 | INTERNALS STORAGE PIT | EVR | R7
R447 | STORAGE FOR REACTOR HEAD | EVR | R3
R448 | PRESSURIZER HEATER ELEMENT ROOM (RCP) | EVR | R6
R450 | ANNULUS LOOP 1 | EVR | R3
R451 | REACTOR COOLANT PUMP LOOP 1 | EVR | R6
R452 | STEAM GENERATOR LOOP 1 | EVR | R6
R453 | COMMON SPACE LOOP 1 | EVR | R3
R460 | ANNULUS LOOP 2 | EVR | R3
R461 | REACTOR COOLANT PUMP LOOP 2 | EVR | R6
R462 | STEAM GENERATOR LOOP 2 | EVR | R6
R463 | COMMON SPACE LOOP 2 | EVR | R3
R470 | ANNALUS LOOP 3 | EVR | R3
R471 | REACTOR COOLANT PUMP LOOP 3 | EVR | R6
R472 | STEAM GENERATOR LOOP 3 | EVR | R6
R473 | COMMON SPACE LOOP 3 | EVR | R3
R480 | REACTOR VESSEL ROOM | EVC | R1
R481 | ELEVATOR | EVR | R3
R484 | RRA HEAT EXCHANGERS | EVR | R3
R485 | INTERNALS STORAGE PIT | EVR | R7
R487 | STORAGE FOR REACTOR HEAD | EVR | R3
R488 | PRESSURIZER HEATER ELEMENT ROOM (RCP) | EVR | R6
R510 | ANNULUS LOOP 1 | EVR | R3
R511 | REACTOR COOLANT PUMP LOOP 1 | EVR | R6
R512 | STEAM GENERATOR LOOP 1 | EVR | R6
R520 | ANNULUS LOOP 2 | EVR | R3
R521 | REACTOR COOLANT PUMP LOOP 2 | EVR | R6
R522 | STEAM GENERATOR LOOP 2 | EVR | R6
R530 | ANNULUS LOOP 3 AND RRM VENTILATION | EVR | R3
R531 | REACTOR COOLANT PUMP LOOP 3 | EVR | R6
R532 | STEAM GENERATOR LOOP 3 | EVR | R6
R540 | REACTOR CAVITY | RRM | R7
R541 | ELEVATOR | EVR | R3
R544 | RRA HEAT EXCHANGERS | EVR | R3
R545 | INTERNAL STORAGE PIT | EVR | R7
R547 | STORAGE FOR REACTOR HEAD | EVR | R3
R548 | PRESSUREIZER (RCP) | EVR | R6
R550 | ANNULUS LOOP 1 | EVR | R3
R551 | REACTOR COOLANT PUMP LOOP 1 | EVR | R6
R552 | STEAM GENERATOR LOOP 1 | EVR | R6
R560 | ANNULUS LOOP 2 | EVR | R3
R561 | REACTOR COOLANT PUMP LOOP 2 | EVR | R6
R562 | STEAM GENERATOR LOOP 2 | EVR | R6
R563 | 02RIS LINE NUMBER 028TY | EVR | R3
R570 | ANNULUS LOOP 3 AND RRM VENTILATION | EVR | R3
R571 | REACTOR COOLANT PUMP LOOP 3 | EVR | R6
R572 | STEAM GENERATOR LOOP 3 | EVR | R6
R573 | VALVE -LOOP 3 TEMP MEAS LINE DRAIN ISO | EVR | R3
R580 | REACTOR CAVITY | RRM | R7
R581 | ELEVATOR | EVR | R3
R584 | RRA HEAT EXCHANGERS | EVR | R3
R585 | INTERNAL STORAGE PIT | EVR | R7
R587 | STORAGE FOR REACTOR HEAD | EVR | R3
R588 | PRESSUREIZER (RCP) | EVR | R6
R610 | ANNULUS LOOP 1 | EVR | R3
R611 | PRIMARY MOTOR PUMP LOOP 1 | EVR | R6
R612 | STEAM GENERATOR LOOP 1 (RCP) | EVR | R6
R620 | ANNULUS LOOP 2 | EVR | R3
R621 | PRIMARY MOTOR PUMP LOOP 2 | EVR | R6
R622 | STEAM GENERATOR LOOP 2 (RCP) | EVR | R6
R623 | SKIMMING ROOM (PTR) | EVR | R3
R630 | ANNULUS LOOP 3 | EVR | R3
R631 | PRIMARY MOTOR PUMP LOOP 3 | EVR | R6
R632 | STEAM GENERATION LOOP 3 (RCP) | EVR | R6
R640 | REACTOR CAVITY (PTR) | RRM | R7
R641 | ELEVATOR | EVR | R3
R644 | RRA HEAT EXCHANGERS | EVR | R3
R645 | INTERNALS STORAGE PIT | EVR | R7
R647 | STORAGE FOR REACTOR HEAD | EVR | R3
R648 | PRESSURIZER (ACP) | EVR | R6
R650 | ANNULUS LOOP 1 | EVR | R3
R651 | PRIMARY MOTOR PUMP LOOP 1 | EVR | R6
R652 | STEAM GENERATOR LOOP 1 (RCP) | EVR | R6
R660 | ANNULUS LOOP 2 | EVR | R3
R661 | PRIMARY MOTOR PUMP LOOP 2 | EVR | R6
R662 | STEAM GENERATOR LOOP 2 (RCP) | EVR | R6
R663 | SKIMMING ROOM (PTR) | EVR | R3
R670 | ANNULUS LOOP 3 | EVR | R3
R671 | PRIMARY MOTOR PUMP LOOP 3 | EVR | R6
R672 | STEAM GENERATION LOOP 3 (RCP) | EVR | R6
R680 | REACTOR CAVITY (PTR) | RRM | R7
R681 | ELEVATOR | EVR | R3
R684 | RRA HEAT EXCHANGERS | EVR | R3
R685 | INTERNALS STORAGE PIT | EVR | R7
R687 | STORAGE FOR REACTOR HEAD | EVR | R3
R688 | PRESSURIZER (ACP) | EVR | R6
R710 | ANNULUS LOOP 1 | EVR | R3
R711 | PRIMARY MOTOR PUMP HATCH LOOP 1 | EVR | R3
R712 | STEAM GENERATOR LOOP 1 | EVR | R3
R713 | NIL | EVR | R3
R714 | NIL | EVR | R3
R716 | SERVICE DECK | EVR | R3
R718 | STAIRWAY ELEVATOR | EVR | R3
R720 | ANNULUS LOOP 2 | EVR | R3
R721 | PRIMARY MOTOR PUMP HATCH LOOP 2 | EVR | R3
R722 | STEAM GENERATOR LOOP 2 | EVR | R3
R723 | NEW UO2 FUEL INSPECTION POST HATCHES | EVR | R3
R727 | VALVE SG3 ARE SAMPLING TEST LINE ISOL | EVR | R3
R730 | ANNULUS LOOP 3 | EVR | R3
R731 | PRIMARY MOTOR PUMP HATCH LOOP 3 | EVR | R3
R732 | STEAM GENERATOR LOOP 3 | EVR | R3
R740 | REACTOR ZONE | EVR | R3
R741 | ELEVATOR | EVR | R3
R744 | RRA HEAT EXCHANGERS HATCH | EVR | R3
R745 | INTERNAL STORAGE PIT | EVR | R3
R747 | ACCESS ZONE FOR EQUIPMENT HATCH | EVR | R3
R748 | PRESSURIZER AREA (RCP) | EVR | R3
R749 | PRESSURIZER SPRAYING VALVE AREA (RCP) | EVR | R3
R750 | ANNULUS LOOP 1 | EVR | R3
R751 | PRIMARY MOTOR PUMP HATCH LOOP 1 | EVR | R3
R752 | STEAM GENERATOR LOOP 1 | EVR | R3
R753 | SPENT FUEL PIT | EVR | R3
R754 | TRANSFER FACILITY AREA | EVR | R3
R756 | SERVICE DECK | EVR | R3
R758 | STAIRWAY ELEVATOR | EVR | R3
R760 | ANNULUS LOOP 2 | EVR | R3
R761 | PRIMARY MOTOR PUMP HATCH LOOP 2 | EVR | R3
R762 | STEAM GENERATOR LOOP 2 | EVR | R3
R763 | NEW UO2 FUEL INSPECTION POST HATCHES | EVR | R3
R770 | ANNULUS LOOP 3 | EVR | R3
R771 | PRIMARY MOTOR PUMP HATCH LOOP 3 | EVR | R3
R772 | STEAM GENERATOR LOOP 3 | EVR | R3
R780 | REACTOR ZONE | EVR | R3
R781 | ELEVATOR | EVR | R3
R783 | SENSOR LEVEL MEAS 002GV NARROW RANGE | EVR | R3
R784 | RRA HEAT EXCHANGERS HATCH | EVR | R3
R785 | INTERNAL STORAGE PIT | EVR | R3
R787 | ACCESS ZONE FOR EQUIPMENT HATCH | EVR | R3
R788 | PRESSURIZER AREA (RCP) | EVR | R3
R789 | PRESSURIZER SPRAYING VALVE AREA (RCP) | EVR | R3
R800 | 20 PIN FEMALE CONNECTOR | EVR | R4
R810 | PASSIVE AUTOCATALYTIC RECOMBINER | EVR | R4
R812 | STAUBLI AUTO CLOSING FEMALE CONNECTION | EVR | R4
R822 | FAN - SUPPLY AIR R722 | EVR | R4
R832 | STAUBLI AUTO CLOSING FEMALE CONNECTION | EVR | R4
R840 | 20 PIN FEMALE CONNECTOR | EVR | R4
R848 | SENSOR TEMPERATURE PRESSURISER VES 001BA | EVR | R4
R849 | ROLLING BEAM PF/PR/CPP 1/2 TON VALVES RC | EVR | R4
R852 | STAUBLI AUTO CLOSING FEMALE CONNECTION | EVR | R4
R862 | STAUBLI AUTO CLOSING FEAMLE CONNECTION | EVR | R4
R872 | STAUBLI AUTO CLOSING FEMALE CONNECTION | EVR | R4
R888 | VALVE SAFETY RELIEF PRESSURISER VESSEL | EVR | R4
R889 | ROLLING BEAM PF/PR/CPP 1/2 TON VALVES RC | EVR | R4
R899 | VALVE PRESS REDUCING V/V SUPL RCP008VP | EVR | R4
R940 | SENSOR TEMPERATURE CONTAINMENT | ETY | R4
R980 | SENSOR TEMPERATURE CONTAINMENT | ETY | R4
D001 | ALARM AUDIBLE AND FLASHING |  | X1
D002 | VALVE ISOLN 09JPD SUPL TO DELG SYS |  | X1
D021 | ALARM AUDIBLE AND FLASHING |  | X1
D022 | VALVE ISOLN 09JPD SUPL TO DELG SYS |  | X1
D041 | ALARM AUDIBLE AND FLASHING |  | X1
D061 | ALARM AUDIBLE AND FLASHING |  | X1
D081 | VALVE ISOLATION 09JPD SUPPLY TO DLG SYS |  | X1
D084 | MOTOR BATTERY ROOM EXHAUST FAN 007ZV |  | X1
D101 | CABLING END BETWEEN DECK |  | X1
D102 | PIPES ROOM |  | X1
D103 | CABLES ROOM |  | X1
D121 | CABLING END BETWEEN DECK |  | X1
D122 | PIPES ROOM |  | X1
D123 | CABLES ROOM |  | X1
D201 | ELECTRICAL ROOM |  | X1
D202 | DIESEL ROOM |  | X1
D203 | STORAGE TANK ACCESSS |  | X1
D204 | AIR FILTER ROOM |  | X1
D221 | ELECTRICAL ROOM |  | X1
D222 | DIESEL ROOM |  | X1
D223 | STORAGE TANK ACCESSS |  | X1
D224 | AIR FILTER ROOM |  | X1
D241 | SWITCHBOARD - 380V AC ESSENTIAL |  | X1
D242 | ROLLING BEAM 2T CPE/PR/PE 1 LHQ D/ROOM |  | X1
D243 | PRIMING VALVE |  | X1
D261 | SWITCHBOARD - 380V AC ESSENTIAL |  | X1
D262 | ROLLING BEAM 2T CPE/PR/PE 2LHQ D/ROOM |  | X1
D263 | PRIMING VALVE |  | X1
D281 | BATTERY BANK - 125V DC |  | X1
D282 | VALVE - RELIEF TRANSFER PUMP 001PO |  | X1
D283 | PRIMING VALVE |  | X1
D301 | FUEL TANK ROOM |  | X1
D302 | OIL TANK ROOM |  | X1
D303 | SILENCER ROOM |  | X1
D321 | FUEL TANK ROOM |  | X1
D322 | OIL TANK ROOM |  | X1
D323 | SILENCER ROOM |  | X1
D401 | EXHAUST FAN |  | X1
D402 | EXHAUST FAN |  | X1
D403 | AIR COOLER |  | X1
D421 | EXHAUST FAN |  | X1
D422 | EXHAUST FAN |  | X1
D423 | AIR COOLER |  | X1
K010 | SPRAYING PUMP LINE A EAS | DVK | K1
K011 | SPRAYING PUMP LINE B EAS | DVK | K1
K012 | LOW HEAD SAFETY INJECTION PUMP LINE A (RIS) | DVK | K1
K013 | LOW HEAD SAFETY INJECTION PUMP LINE B (RIS) | DVK | K1
K014 | PIPING CHANNNEL RRI/RIS-CABLING-EMERGENCY LADDER | DVK | K2
K015 | CHEMICAL ADDICTIVE TANK (EAS) | DVK | K2
K016 | EAS HEAT EXCHANGERS | DVK | K2
K017 | REACTOR BUILDING CONNECTION ZONE | DVK | K2
K018 | STAIRWAY-ELEVATOR | DVK | K1
K026 | VALVE EAS 02RF RRI OUTLET RELIEF | DVK | K1
K050 | SPRAYING PUMP LINE A EAS | DVK | K1
K051 | SPRAYING PUMP LINE B EAS | DVK | K1
K052 | LOW HEAD SAFETY INJECTION PUMP LINE A (RIS) | DVK | K1
K053 | LOW HEAD SAFETY INJECTION PUMP LINE B (RIS) | DVK | K1
K054 | PIPING CHANNNEL RRI/RIS-CABLING-EMERGENCY LADDER | DVK | K2
K055 | CHEMICAL ADDICTIVE TANK (EAS) | DVK | K2
K056 | EAS HEAT EXCHANGERS | DVK | K2
K057 | REACTOR BUILDING CONNECTION ZONE | DVK | K2
K058 | STAIRWAY-ELEVATOR | DVK | K1
K081 | VALVE - DRAIN DRY RISER LINE 058 | DVK | K1
K110 | VALVE OPERATION AND MOTORS EAS LINE A | DVK | K1
K111 | VALVE OPERATION AND MOTORS EAS LINE B | DVK | K1
K112 | VALVE OPERATION AND MOTORS RIS (LHSI) LINE B | DVK | K1
K113 | VALVE OPERATION AND MOTORS RIS (LHSI) LINE B | DVK | K1
K115 | SEPARATOR 001BA CO2 SEPARATOR | DVK | K1
K117 | REACTOR BUILDING CONNECTION ZONE | DVK | K2
K118 | STAIRWAY ELEVATOR | DVK | K1
K130 | VALVE DRAIN WATER SPRAY LINE 008 | DVK | K1
K150 | VALVE OPERATION AND MOTORS EAS LINE A | DVK | K1
K151 | VALVE OPERATION AND MOTORS EAS LINE B | DVK | K1
K152 | VALVE OPERATION AND MOTORS RIS (LHSI) LINE B | DVK | K1
K153 | VALVE OPERATION AND MOTORS RIS (LHSI) LINE B | DVK | K1
K155 | VALVE-RAZ PRESURE CNTRL-ETY RECOMBINERS | DVK | K1
K157 | REACTOR BUILDING CONNECTION ZONE | DVK | K1
K158 | STAIRWAY ELEVATOR | DVK | K1
K210 | HANDLING AREA | DVK | K2
K212 | HANDLING HATCH FOR EAS HEAT EXCHANGERS | DVK | K2
K215 | PUSH BUTTON STOP 004PO | DVK | K1
K216 | RIS (LNSI) EAS PTR PUMPS HANDLING AREA | DVK | K2
K217 | ETY PIPING | DVW | W1
K218 | STAIRWAY ELEVATOR | DVK | K1
K219 | WEATHER LOUVRE INTAKE | DVK | K1
K250 | HANDLING AREA | DVK | K1
K252 | HANDLING HATCH FOR EAS HEAT EXCHANGERS | DVK | K1
K253 | 02RIS LINE NUMBER 084TY | DVK | K1
K254 | VOLTAGE MONITORING CIRCUIT | DVK | K1
K255 | FLOW METER RRA\PTR CROSS CONCT (LOCAL) | DVK | K1
K256 | RIS (LNSI) EAS PTR PUMPS HANDLING AREA | DVK | K1
K257 | ETY PIPING | DVW | W1
K258 | STAIRWAY ELEVATOR | DVK | K1
K259 | WEATHER LOUVRE INTAKE | DVK | K1
K310 | HANDLING HATCH | DVK | K2
K312 | CASK LOADING CELL | DVK | K4
K313 | SPENT FUEL PIT (PTR) | DVK | K4
K314 | TRANSFER FACILITY AREA | DVK | K4
K316 | PIT COOLING HEAT EXCHANGER (PTR) | DVK | K2
K317 | TRANSFER TUBE | DVK | K4
K318 | STAIRWAY ELEVATOR | DVK | K1
K350 | HANDLING HATCH | DVK | K2
K352 | CASK LOADING CELL | DVK | K4
K353 | SPENT FUEL PIT (PTR) | DVK | K4
K354 | TRANSFER FACILITY AREA | DVK | K4
K356 | PIT COOLING HEAT EXCHANGER (PTR) | DVK | K2
K357 | TRANSFER TUBE | DVK | K4
K358 | STAIRWAY ELEVATOR | DVK | K1
K410 | HANDLING HATCH | DVK | K2
K411 | FILTER ABSOLUTE | DVK | K2
K412 | CASK LOADING CELL | DVK | K4
K413 | SPENT FUEL PIT | DVK | K4
K414 | TRANSFER FACILITY AREA | DVK | K4
K415 | DEG MOTOR PUMP AND COMPRESSOR | DVK | K2
K416 | FUEL BUILDING VENTILATION (DVK) | DVK | K2
K418 | STAIRWY-ELEVATOR | DVK | K1
K446 | MOTOR - FOR 004ZV | DVK | K2
K450 | HANDLING HATCH | DVK | K2
K451 | FILTER IODINE | DVK | K2
K452 | CASK LOADING CELL | DVK | K4
K453 | SPENT FUEL PIT | DVK | K4
K454 | TRANSFER FACILITY AREA | DVK | K4
K455 | DEG MOTOR PUMP AND COMPRESSOR | DVK | K2
K456 | FUEL BUILDING VENTILATION (DVK) | DVK | K2
K458 | STAIRWY-ELEVATOR | DVK | K1
K507 | INTERMEDIATE RANGE I DBLING TIME <18 SEC | DVK | K2
K510 | HANDLING HATCH | DVK | K2
K511 | CASK CLEANING CELL | DVK | K2
K512 | CASK LOADING CELL | DVK | K4
K513 | SPENT FUEL PIT | DVK | K4
K514 | TRANSFER FACILITY AREA | DVK | K4
K516 | RECEPTION OF NEW FUEL ASSEMBLIES | DVK | K1
K518 | NIL | DVK | K1
K520 | STORAGE OF NEW FUEL ASSEMBLIES | DVK | K2
K521 | EXAMINATION STATION FOR NEW FUEL PU | DVK | K2
K522 | VALVE ROOM | DVK | K1
K523 | EXAMINATION STATION FOR NEW FUEL U 2 | DVK | K1
K524 | ACCESS AIRLOCK TO ROOM K516 | DVK | K2
K530 | DAMPER BALANCING | DVK | K2
K550 | HANDLING HATCH | DVK | K2
K551 | CASK CLEANING CELL | DVK | K2
K552 | CASK LOADING CELL | DVK | K4
K553 | SPENT FUEL PIT | DVK | K4
K554 | TRANSFER FACILITY AREA | DVK | K4
K556 | RECEPTION OF NEW FUEL ASSEMBLIES | DVK | K1
K558 | STAIRWAY-ELEVATOR | DVK | K1
K560 | STORAGE OF NEW FUEL ASSEMBLIES | DVK | K2
K561 | EXAMINATION STATION FOR NEW FUEL PU | DVK | K2
K562 | VALVE ROOM | DVK | K1
K563 | EXAMINATION STATION FOR NEW FUEL U 2 | DVK | K1
K564 | ACCESS AIRLOCK TO ROOM K516 | DVK | K2
K618 | LOCAL CABINET | DVK | K1
K710 | NIL | DVK | K2
K711 | RX MANUAL FUEL ASSEMBLY HANDLING TOOL | DVK | K2
K712 | SWITCH LOW LEVEL MEAS FUEL CASK COMPRT | DVK | K2
K713 | TEMP IND PIT HALL | DVK | K1
K714 | SWITCH TEMP PIT HALL | DVK | K1
K716 | ROLLING BEAM130T FUEL CASK HANDLG F/BLDG | DVK | K1
K718 | DAMPER BALANCING | DVK | K1
K720 | EXTERNAL CLAMP RESISTOR-UPENDER DRIVE | DVK | K1
K721 | NIL | DVK | K2
K723 | NIL | DVK | K2
K750 | NIL | DVK | K2
K751 | VALVE RELIEF TO TRANSFER COMPRT AIR SUP | DVK | K2
K752 | CONNECTOR FOR IAEA CAMERA TRAIN B | DVK | K2
K753 | TEMP IND PIT HALL | DVK | K1
K754 | SWITCH TEMP PIT HALL | DVK | K2
K756 | ROLLING BEAM130T FUEL CASK HANDLG F/BLDG | DVK | K1
K758 | DAMPER BALANCING | DVK | K1
K760 | TEMP SENSOR PIT HALL | DVK | K1
K761 | NIL | DVK | K2
K763 | NIL | DVK | K2
L001 | VENTILATION FILTER | DVL | L1
L002 | INDICATOR TEMPERATURE 002PO OUTLET | DVL | L1
L003 | COLD LABORATORY | DVL | L1
L004 | I & T WORKSHOP | DVL | L1
L005 | LABORATORIES FOREMAN OFFICE | DVL | L1
L006 | CHEMISTS OFFICE | DVL | L1
L007 | HOT LABORATORY AIRLOCK | DVL | L1
L008 | HOT LABORATORY | DVL | L1
L009 | I & T WORKSHOP | DVL | L1
L010 | COUNTING | DVL | L1
L011 | NIL | DVL | L1
L012 | COLD LABORATORY AIRLOCK | DVL | L1
L013 | STAIRWAY-ELEVATOR | DVL | L1
L015 | GALLERY LINE B | DVL | L1
L016 | GALLERY LINE A | DVL | L1
L017 | RRI-DVI CORRIDOR | DVL | L1
L018 | HOT LAUNDRY WASTE TANKS SRE | DVL | L1
L019 | DECONTAMINATION CHECK | DVL | L1
L020 | AIRLOCK WITH SHUTTER | DVL | L1
L021 | ELEVATOR CORRIDOR AND ACCESS | DVL | L1
L022 | HOT LAUNDRY WASHING AND DRYING | DVL | L1
L023 | SORTING | DVL | L1
L024 | MASKS CLEANING | DVL | L1
L025 | AIRLOCK | DVL | L1
L026 | SENSOR TEMP | DVL | L1
L027 | DETECTOR HEAT FIX TEMP KITCHEN | DVL | L1
L030 | DAMPER FIRE | DVL | L1
L031 | COIL COOLING | DVL | L1
L033 | VALVE PRESSURE RELIEF 004BA | DVL | L1
L034 | MOTOR FOR 006PO | DVL | L1
L035 | DETECTOR ION PASSAGE | DVL | L1
L036 | VALVE ISOLATION TO LINE DRAINING | DVL | L1
L041 | VENTILATION FILTER | DVL | L1
L053 | STAIRWAY-ELEVATOR | DVL | L1
L055 | GALLERY LINE B | DVL | L1
L056 | GALLERY LINE A | DVL | L1
L057 | RRI-DVI CORRIDOR | DVL | L1
L101 | CABLES GALLERY LINE A | DVL | L1
L102 | CABLES GALLERY LINE A | DVL | L1
L103 | CABLES GALLERY LINE A | DVL | L1
L104 | CABLES GALLERY LINE A | DVL | L1
L105 | CABLES GALLERY LINE A | DVL | L1
L106 | PIPES GALLERY LINE B | DVL | L1
L107 | PIPES GALLERY LINE B | DVL | L1
L108 | CABLES GALLERY LINE A | DVL | L1
L109 | CABLES GALLERY LINE A | DVL | L1
L110 | CABLES GALLERY LINE B | DVL | L1
L111 | PIPES GALLERY LINE B | DVL | L1
L112 | PIPES GALLERY LINE A | DVL | L1
L113 | STAIRWAY ELEVATOR | DVL | L1
L114 | NIL | DVL | L1
L115 | CABLES GALLERY | DVL | L1
L116 | AIRLOCK | DVL | L1
L117 | DETECTOR OPT LX / RX PERIPHERAL | DVL | L1
L128 | DETECTOR ION DVG VENT DUCTING | DVL | L1
L130 | DETECTOR ION ASG PIPE / DVG DUCTS | DVL | L1
L131 | DETECTOR ION ASG PIPING | DVL | L1
L132 | VALVE NON RETURN AFTER 257VE | DVL | L1
L134 | V/V SHUT OFF LINE VENTING STOR TNK 2 | DVL | L1
L141 | CABLES GALLERY LINE A | DVL | L1
L142 | CABLES GALLERY LINE A | DVL | L1
L143 | CABLES GALLERY LINE A | DVL | L1
L144 | CABLES GALLERY LINE A | DVL | L1
L145 | CABLES GALLERY LINE A | DVL | L1
L146 | PIPES GALLERY LINE B | DVL | L1
L147 | PIPES GALLERY LINE B | DVL | L1
L148 | CABLES GALLERY LINE A | DVL | L1
L149 | CABLES GALLERY LINE A | DVL | L1
L150 | CABLES GALLERY LINE B | DVL | L1
L151 | PIPES GALLERY LINE B | DVL | L1
L152 | PIPES GALLERY LINE A | DVL | L1
L153 | LOUD SPEAKER | DVL | L1
L201 | COMPRESSOR ROOM | DVL | L1
L202 | STAIRWAY ACCESS ELEVATOR | DVL | L1
L203 | PERSONNEL ACCESS | DVL | L1
L204 | CORRIDOR | DVL | L1
L205 | SAFETY AND FIRE | DVL | L1
L206 | NUCLEAR AUXILIARY BUILDING MATERIAL | DVL | L1
L207 | ACTIVE WORKSHOP | DVL | L1
L208 | TOOL SHOP | DVL | L1
L209 | CORRIDOR | DVL | L1
L210 | INSTRUMENTATION WORKSHOP | DVL | L1
L211 | VISITOR CHANGING ROOM | DVL | L1
L212 | SHIFT PERSONNEL CHANGING ROOM | DVL | L1
L213 | ACTIVE LABORATORY | DVL | L1
L214 | AIRLOCK | DVL | L1
L215 | 2ND CONTROL FOR L 211 | DVL | L1
L216 | 2ND CONTROL FOR L 212 | DVL | L1
L217 | RADIO PROTECTION ROOM | DVL | L1
L218 | CONTROL ROOM | DVL | L1
L219 | CORRIDOR | DVL | L1
L220 | SANITARIES | DVL | L1
L221 | SANITARIES | DVL | L1
L222 | HOT CHANGING ROOM | DVL | L1
L223 | HOT CHANGING ROOM | DVL | L1
L224 | AIRLOCK | DVL | L1
L226 | CONVENTIONAL CHANGING ROOM | DVL | L1
L227 | SANITARIES | DVL | L1
L228 | SANITARIES | DVL | L1
L229 | CONVENTIONAL CHANGING ROOM | DVL | L1
L241 | COMPRESSOR ROOM | DVL | L1
L242 | STAIRWAY ACCESS ELEVATOR | DVL | L1
L243 | PERSONNEL ACCESS | DVL | L1
L244 | CORRIDOR | DVL | L1
L246 | RELAY 13 POSITION STEPPING RELAY | DVL | L1
L301 | CABLING FLOOR LINE A | DVE | E1
L303 | STAIRWAY ACCESS ELEVATOR | DVE | E1
L304 | CABLING FLOOR LINE A | DVE | E1
L305 | SENSOR 01CS AERATED VENT TEMPERATURE | DVE | E1
L306 | CABLING FLOOR LINE A | DVE | E1
L307 | AIRLOCK LOCK | DVE | E1
L308 | CABLING FLOOR LINE B | DVE | E1
L310 | CABLING FLOOR COMMON | DVE | E1
L311 | BATTERY COMMON | DVE | E1
L312 | CABLING FLOOR COMMON | DVE | E1
L341 | CABLING FLOOR LINE A | DVE | E1
L343 | STAIRWAY ACCESS ELEVATOR | DVE | E1
L344 | CABLING FLOOR LINE A | DVE | E1
L345 | TERMINAL BLOCK | DVE | E1
L346 | CABLING FLOOR LINE A | DVE | E1
L347 | LOCAL CABINET | DVE | E1
L348 | CABLING FLOOR LINE B | DVE | E1
L401 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L402 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L403 | STAIRWAY ACCESS ELEVATOR | DVL | L1
L404 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L405 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L406 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L407 | AIRLOCK | DVL | L1
L408 | LV AND MV SWITCHBOARD LINE B | DVL | L1
L410 | LV AND MV SWITCHBOARD COMMON | DVL | L1
L411 | LV AND MV SWITCHBOARD COMMON | DVL | L1
L412 | LAMP INDICATOR REGULATOR FUSE FAIL | DVL | L1
L441 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L442 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L443 | STAIRWAY ACCESS ELEVATOR | DVL | L1
L444 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L445 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L446 | LV AND MV SWITCHBOARD LINE A | DVL | L1
L447 | AIR LOCK TESTS ROOM RESERVE TRANSFORMER | DVL | L1
L448 | LV AND MV SWITCHBOARD LINE B | DVL | L1
L449 | CONTROL MODULE | DVL | L1
L452 | TRANSFORMER - 6,6KV AC/380V AC | DVL | L1
L454 | LETDOWN LINE ISO KIT INPUT | DVL | L1
L456 | TEMP IND 001RE INLET | DVL | L1
L501 | STAIRWAY ELEVATOR ACCESS | DVL | L1
L503 | CONDENSOR SECTION OF ROOM SPLIT UNIT | DVL | L1
L504 | VENTILATION LINE A | DVL | L1
L505 | RELAYING LINE A | DVL | L1
L506 | RELAYING LINE A | DVL | L1
L507 | RELAYING LINE A | DVL | L1
L508 | AIR LOCK | DVL | L1
L509 | RELAYING LINE A | DVL | L1
L511 | RELAYING COMMON | DVL | L1
L514 | INSTRUMENT JUNCTION BOX | DVL | L1
L516 | TERMINAL BLOCK FOR PTR UP WIRING | DVL | L1
L541 | STAIRWAY ELEVATOR ACCESS | DVL | L1
L543 | INDICATOR LOCALIZED TEMP 006RF OUT | DVL | L1
L544 | REFRIGERATING ROOM | DVL | L1
L545 | RELAYING LINE A | DVL | L1
L546 | RELAYING LINE A | DVL | L1
L547 | RELAYING LINE A | DVL | L1
L548 | 48V CHANGEOVER SWITCH-U2 TRAIN A&B RELAY | DVL | L1
L549 | RELAYING LINE A | DVL | L1
L559 | LMK POWER DISTRIBUTION PANEL 11.5M | DVL | L1
L601 | STAIRWAY-ELEVATOR-ACCESS | DVC | C1
L603 | TELEPHONE ROOM | DVC | C1
L604 | TESTS ROOM | DVC | C1
L605 | CONTROL ROD DRIVE MECHANISM POSITION MEASURING | DVC | C1
L607 | REGULATION ROOM | DVC | C1
L608 | AIRLOCK | DVC | C1
L609 | REACTOR ANALOG CONTROL SYSTEM ROOM | DVC | C1
L610 | AMPLIFIER | DVC | C1
L645 | CONTROL ROD DRIVE MECHANISM POSITION MEASURING | DVC | C1
L647 | REGULATION ROOM | DVC | C1
L649 | REACTOR ANALOG CONTROL SYSTEM ROOM | DVC | C1
L650 | M.D.F | DVC | C1
L651 | ELEVATOR MACHINERY | DVC | C1
L652 | NIL | DVC | C1
L653 | STAIRWAY ACCESS | DVC | C1
L659 | MODULE ALARM THRESHOLD | DVC | C1
L680 | LAMP INDICATOR 117VA | DVC | C1
L701 | STAIRWAY ELEVATOR ACCESS | DVC | C1
L702 | CORRIDOR | DVC | C1
L703 | KITCHEN | DVC | C1
L704 | OFFICE | DVC | C1
L705 | CORRIDOR | DVC | C1
L706 | HALL | DVC | C1
L707 | CHIEF SUPERVISOR OFFICE | DVC | C1
L709 | COMPUTER ROOM | DVC | C1
L710 | CONTROL ROOM | DVC | C1
L711 | CONTROL ROOM COMMON | DVC | C1
L713 | SANITARY | DVC | C1
L714 | HALL | DVC | C1
L715 | SERVICE ROOM STORAGE | DVC | C1
L716 | WIRING PANEL ACCESS CORRIDOR | DVC | C1
L717 | CORRIDOR | DVC | C1
L718 | CORRIDOR | DVC | C1
L719 | CORRIDOR | DVC | C1
L740 | ALARM - GRATES OR FILTER BLOCKED | DVC | C1
L741 | CORRIDOR | DVC | C1
L742 | CORRIDOR | DVC | C1
L744 | COOLER CHILLED WATER | DVC | C1
L746 | DAMPER BALANCING | DVC | C1
L747 | CHIEF SUPERVISOR OFFICE | DVC | C1
L748 | INTERFACE CONTROLLER | DVC | C1
L749 | COMPUTER ROOM | DVC | C1
L750 | CONTROL ROOM | DVC | C1
L756 | WIRING PANEL ACCESS CORRIDOR | DVC | C1
L757 | CORRIDOR | DVC | C1
L800 | STAIRWAY ACCESS ELEVATOR | DVL | L1
L801 | VENTILATION LINE A-DVF Fan Room | DVL | L1
L802 | VENTILATION LINE B-DVF Fan Room | DVL | L1
L803 | SANITARIES | DVL | L1
L804 | SENSOR TEMP AMBIENT L804 | DVL | L1
L805 | PROJECTION ROOM | DVL | L1
L806 | CORRIDOR | DVL | L1
L807 | OFFICE | DVL | L1
L808 | OFFICE | DVL | L1
L809 | OFFICE | DVL | L1
L810 | AIR EXHAUST | DVL | L1
L811 | ELEVATOR MACHINERY | DVL | L1
L814 | DETECTOR ION | DVL | L1
L815 | NIL | DVE | E1
L816 | DIRECT CURRENT DISTRIBUTION | DVE | E1
L817 | BATTERY | DVE | E1
L818 | DAMPER NR EXHAUST L818 | DVL | L1
L841 | VENTILATION LINE A-DVF Fan Room | DVL | L1
L842 | VENTILATION LINE B-DVF Fan Room | DVL | L1
L847 | SENSOR TEMP AMBIENT L847 | DVL | L1
L858 | DIFF PRESS TRANSMITTER | DVL | L1
L860 | AIR INTAKE | DVL | L1
L901 | ELEVATOR MACHINERY | DVL | L1
N010 | RRI PUMPS LINE A | DVI | I1
N011 | RRI EXCHANGER LINE A | DVI | I1
N012 | RRI PUMPS LINE B | DVI | I1
N013 | PUMP - SUBMERSIBLE | DVN | N1
N014 | PUMP - 505MA | DVN | N1
N015 | ANTI-VORTEX DRAIN COVER | DVN | N1
N019 | DAMPER BALANCING | DVN | N1
N020 | DETECTOR SINTILLATOR DAL 10 | DVN | N1
N021 | COOLER RRI SEA WATER COOLED TRAIN A | DVN | N1
N022 | GAUGE 02PO DISCH PRESSURE | DVN | N1
N023 | PUMP - SUBMERSIBLE | DVN | N1
N024 | FAN ASSEMBLY - SUPPLY AIR NA024 | DVN | N1
N028 | SENSOR 04MO STATOR TEMPERATURE | DVN | N1
N030 | CONCRETE SETTING AREA TES | DVN | N1
N031 | CONCRETE DUMPER TES | DVN | N1
N032 | TES CONTROL ROOM/ PLUGGING FACILITY | DVN | N1
N033 | MANOMETER 102FI PRESS DIFF | DVN | N1
N034 | MANOMETER 101FI PRESS DIFF | DVN | N1
N040 | LOUD SPEAKER | DVN | N1
N050 | NIL | DVN | N1
N051 | PRESSURE SWITCH | DVN | N1
N067 | STAIRWAY | DVN | N1
N068 | STAIRWAY | DVN | N1
N069 | ELEVATOR | DVN | N1
N076 | STAIRWAY | DVN | N1
N077 | STAIRWAY | DVN | N1
N080 | GALLERY LINE B SEC-RRI | DVN | N1
N081 | GALLERY LINE A SEC-RRI | DVN | N1
N090 | GALLERY LINE B SEC-RRI | DVN | N1
N091 | GALLERY LINE A SEC-RRI | DVN | N1
N146 | UNIT POLARITY | DVN | N1
N154 | VALVE ISOLATION - VENT 002CO TO DVN | DVN | N1
N180 | PIPING CABLES GALLERY LINE B | DVN | N1
N181 | PIPING CABLES GALLERY LINE A | DVN | N1
N190 | PIPING CABLES GALLERY LINE B | DVN | N1
N191 | PIPING CABLES GALLERY LINE A | DVN | N1
N202 | ACTIVE PIPING TUNNEL SEE LEVEL +5.00 | DVN | N1
N203 | REA TANKS | DVN | N1
N204 | TEP TANKS | DVN | N1
N205 | SWITCH TEMPERATURE AMBIENT 041RS | DVN | N1
N206 | TRANSFER PUMP FOR TEU DISTILLATES NB 2 EVAP | DVN | N1
N207 | ACTIVE PIPING TUNNEL SEE LEVEL +5.00 | DVN | N1
N208 | ACTIVE PIPING TUNNEL SEE LEVEL +5.00 | DVN | N1
N209 | VALVE ISOL, RM ND209 FOR TEP351& 353VL | DVN | N1
N210 | ACTIVE PIPING TUNNEL SEE LEVEL +5.00 | DVN | N1
N211 | HHSI PUMPS PIPING TUNNEL | DVN | N1
N212 | CORRIDOR FUEL BUILDING | DVN | N1
N213 | REA BORIC ACID PUMPS | DVN | N1
N214 | ACTIVE PIPING TUNNEL | DVN | N1
N215 | HEAT EXCHANGER (RCV) | DVN | N1
N216 | GALLERY FOR HP PIPING (CHARGING PUMPS RCV) | DVN | N1
N217 | CHARGING PUMP RCV 01 PO | DVH | H1
N218 | CHARGING PUMP RCV 02 PO | DVH | H1
N219 | CHARGING PUMP RCV 03 PO | DVH | H1
N220 | VALVE TEST CONNECTION LINE 084TY. | DVN | N1
N221 | CHARGING PUMPS LP PIPING TUNNEL | DVN | N1
N222 | CORRIDOR FUEL BUILDING | DVN | N1
N223 | REA BORIC ACID PUMPS | DVN | N1
N224 | SENSOR PRESSURE - LETDOWN LINE PRESSURE | DVN | N1
N225 | HEAT EXCHANGER (RCV) | DVN | N1
N226 | VALVE ISOLATION - DISCHARGE 01PO | DVN | N1
N227 | CHARGING PUMP RCV 01 PO | DVH | H1
N228 | CHARGING PUMP RCV 02 PO | DVH | H1
N229 | ORIFICE F RESTRICTOR S/U G/BOX LUB OIL | DVN | N1
N230 | REA PUMPS | DVN | N1
N231 | TEP DEAERATING PUMP ROOM | DVN | N1
N232 | ACCESS TUNNEL TO TEU AND TEP PUMP ROOMS | DVN | N1
N233 | TEP MIXING AND EVAPORATOR SUPPLY PUMPS | DVN | N1
N234 | CENTRAL CIRCULATION TUNNEL | DVN | N1
N235 | TES DRUMMING FACILITY | DVN | N1
N236 | AIR HEATER CONDITIONER UNIT | DVN | N1
N237 | TEP DISTILLATES RECOVERY PUMPS DISTILLATE PUMP EVAPORATOR NO 1 | DVN | N1
N238 | DRAIN RECOVERY AND TRANSFER PUMPS FOR TEU DISTILLATE | DVN | N1
N239 | TEP CONCETRATE TANK AND EVACUATION PUMP | DVN | N1
N240 | TEU TANKS RESIDUAL DRAINS DECKS | DVN | N1
N241 | TEU PUMPS | DVN | N1
N242 | MOTOR - FOR 035ZV | DVN | N1
N243 | TEP HEAD PUMPS | DVN | N1
N244 | NIL | DVN | N1
N245 | SWITCHBOARD - 380V AC NON ESSENTIAL | DVN | N1
N246 | POLARITY UNIT | DVN | N1
N247 | MODULE ALARM THRESHOLD DISCHARGE FLOW | DVN | N1
N248 | ELECTRICAL ROOM -INVERTER LIGHTING | DVN | N1
N249 | ELECTRICAL ROOM -INVERTER LIGHTING | DVN | N1
N250 | ACCESS TUNNEL TO TEU AND TEP AUXILIARY ROOMS | DVN | N1
N251 | DISTILLATE PUMPS TEP NB 1 EVAPORATOR | DVN | N1
N252 | DISTILLATE PUMPS TEP NB 2 EVAPORATOR | DVN | N1
N253 | CONCETRATE RE-CIRCULATING PUMP TEU NB 1 EVAP | DVN | N1
N254 | VALVE CONTROL ROOM | DVN | N1
N255 | ACCESS STAIRWAY TO NC 254 | DVN | N1
N256 | CONCETRATE RE-CIRCULATING PUMP TEU NB 2 EVAP | DVN | N1
N257 | CONCETRATE RE-CIRCULATING PUMP TEU NB 3 EVAP | DVN | N1
N258 | DETECTOR ION DVH VENTILATION | DVN | N1
N259 | SWITCH TEMPERATURE FOR 153RS | DVN | N1
N260 | STAUBLI AIR SUPPLY POINT | DVN | N1
N263 | SINGLE LEAF DOOR 9NX/0.0/53 | DVN | N1
N264 | CENTRAL CIRCULATION TUNNEL | DVN | N1
N265 | ACCESS TO DRUMMING AND PLUGGING TES | DVN | N1
N266 | V/V ISOL DRAIN TUNDISH TEU 010+11PO | DVN | N1
N267 | ACCESS TO NF 230 NF 265 | DVN | N1
N268 | STAIRWAY | DVN | N1
N269 | ELEVATOR | DVN | N1
N270 | FIRE DAMPER (BIG LINK ) | DVN | N1
N275 | STAIRWAY | DVN | N1
N276 | ELEVATOR | DVN | N1
N277 | ELEVATOR | DVN | N1
N278 | STAIRWAY | DVN | N1
N280 | SVA ROOM PUMPS COOLANT | DVN | N1
N281 | RPE LIFT PUMPS ( ANCILLARY CHEMICAL RESIDUAL) | DVN | N1
N282 | ACCESS TO NB 283 | DVN | N1
N283 | RPE SUMPS (FLOOR DRAIN) | DVN | N1
N285 | LEVEL TRANSMITTER REA003BA | DVN | N1
N293 | REN SAMPLING ROOM | DVN | N1
N294 | APG SAMPLING ROOM | DVN | N1
N295 | ACCESS TO BORIC ACID AND CHARGING PUMPS UNIT 1 | DVN | N1
N296 | ACCESS TO NB281 294 223 | DVN | N1
N297 | ACCESS TO CHARGING PUMPS UNIT 2 | DVN | N1
N298 | SENSOR 014RF FLOW RATE REN SIDE | DVN | N1
N299 | COOLERS AND EXPANSION VALVES | DVN | N1
N300 | DE-AERATING TEP 01 DZ | DVN | N1
N301 | DE-AERATING TEP 02 DZ | DVN | N1
N302 | INACTIVE PIPING TUNNEL | DVN | N1
N304 | DETECTOR ION TEP STORAGE TANKS | DVN | N1
N305 | EVAPORATOR TEU 01 EV | DVN | N1
N306 | EVAPORATOR TEU 01 EV | DVN | N1
N307 | EVAPORATOR TEU 02 EV | DVN | N1
N308 | INACTIVE PIPING TUNNEL | DVN | N1
N309 | TES STAIRWAY | DVN | N1
N310 | EVAPORATOR TEU 02 EV | DVN | N1
N311 | ELECTRICAL AND NON-ACTIVE PIPING TUNNEL | DVN | N1
N312 | BORIC ACID TANK R15 | DVN | N1
N313 | ACTIVE TUNNEL TO RCV | DVN | N1
N314 | ELECTRICAL AND NON-ACTIVE PIPING TUNNEL | DVN | N1
N315 | VOLUME CONTROL TANK RCV | DVN | N1
N316 | HEAD TANKS TEP | DVN | N1
N317 | CIRCULATION TUNNEL- SAR TANK | DVN | N1
N318 | JPI TANKS UNIT 1 | DVN | N1
N321 | ELECTRICAL AND NON-ACTIVE PIPING TUNNEL | DVN | N1
N322 | BORIC ACID TANK R15 | DVN | N1
N323 | ACTIVE TUNNEL TO RCV | DVN | N1
N324 | ELECTRICAL AND NON-ACTIVE PIPING TUNNEL | DVN | N1
N325 | VOLUME CONTROL TANK RCV | DVN | N1
N326 | HEAD TANKS TEP | DVN | N1
N327 | CIRCULATION TUNNEL- SAR TANK | DVN | N1
N328 | JPI TANKS UNIT 2 | DVN | N1
N330 | ACCESS TRAP FOR FILTER AND DEMINERALIZERS | DVN | N1
N331 | SENSOR PRESSURE MEASUREMENT | DVN | N1
N333 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N334 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N335 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N336 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N337 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N338 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N339 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N340 | ACTIVE PIPING LAY-OUT ARRANGEMENT AREA | DVN | N1
N342 | ACCESS | DVN | N1
N343 | CENTRIFUGE | DVN | N1
N344 | CENTRIFUGATION SLUDGES | DVN | N1
N345 | SWITCH LIMIT 164VB | DVN | N1
N351 | TES PLATFORM | DVN | N1
N352 | ACCESS TO MIXER (TES) | DVN | N1
N353 | TES MIXER | DVN | N1
N354 | VALVE MANIFOLD | DVN | N1
N363 | GAUGE SUPPLY PRESS RCV VOLUME CTRL TANK | DVN | N1
N365 | TEU CONTROL TANKS | DVN | N1
N366 | NF 265 CRANE CONTROL ROOM | DVN | N1
N367 | GAUGE LEVEL - LOCAL 016BA | DVN | N1
N368 | GUAGE LEVEL - LOCAL 017BA | DVN | N1
N369 | DAMPER BALANCING | DVN | N1
N370 | 2"INTER-UNIT SUCTION MANUAL ISOL VLVE | DVN | N1
N371 | ACCESS TO NF 365 - NF 203 CIRCULATION TUNNEL | DVN | N1
N375 | STAIRWAY | DVN | N1
N376 | TRANSVERSAL PASSAGE WAY | DVN | N1
N377 | TRANSVERSAL PASSAGE WAY | DVN | N1
N378 | STAIRWAY | DVN | N1
N379 | NIL | DVN | N1
N380 | TEP DISTILLATE CONTROL | DVN | N1
N381 | INDICATOR, PRESSURE, 09TEG001BA | DVN | N1
N382 | TEU CHEMICAL EFFLUENT TANKS | DVN | N1
N383 | TEU SERVICE EFFLUENT TANKS | DVN | N1
N384 | PLATFORM | DVN | N1
N385 | VALVE ISOL TRANSFER 03BA TO 04BA UNIT 1 | DVN | N1
N386 | TEG DECAY TANKS | DVN | N1
N387 | TEG DECAY TANKS | DVN | N1
N388 | ADSORBERS TEG | DVN | N1
N389 | COOLER TEG | DVN | N1
N390 | TEG VALVE TUNNEL | DVN | N1
N391 | TEG VALVE CONTROL TUNNEL | DVN | N1
N392 | ACCESS PASSAGE TO THE TEG COMPRESSORS | DVN | N1
N393 | TEG COMPRESSORS | DVN | N1
N394 | TEG COMPRESSORS | DVN | N1
N395 | ELECTRICAL GALLERY | DVN | N1
N396 | TEST PUMP | DVN | N1
N397 | NIL | DVN | N1
N398 | NIL | DVN | N1
N401 | TES PLATFORM | DVN | N1
N402 | TES TRAP | DVN | N1
N403 | TES ROOM | DVN | N1
N404 | TES RESIN AND CONCENTRATE TANKS | DVN | N1
N405 | TES RESINS TANKS | DVN | N1
N406 | NIL | DVN | N1
N411 | NON-ACTIVE PIPING TUNNEL | DVN | N1
N412 | BORON RECIRC SURGE TANK - 021 BA. | DVN | N1
N413 | DETECTOR ION EBA VALVES | DVN | N1
N414 | DAMPER BALANCING | DVN | N1
N415 | BOX FOR 9JDT329CR AND 9JDT3016 - 3017UI | DVN | N1
N421 | VALVE RRI INLET TO T**/PTR | DVN | N1
N422 | RIS BORIC ACID TANK RECIRCULATING PUMPS | DVN | N1
N423 | CIRCULATION PLATFORM | DVN | N1
N424 | PLATFORM | DVN | N1
N425 | CIRCULATION TUNNEL | DVN | N1
N430 | DETECTOR IONIZATION CHAMBER DAR 30 | DVN | N1
N432 | LAMP INDICATOR RIS022PO | DVN | N1
N434 | 01RCV LINE NUMBER312TY | DVN | N1
N435 | GAUGE PRESSURE LOCAL 05FI DIFF PRESS | DVN | N1
N437 | 2PTR LINE NUMBER 012TY | DVN | N1
N440 | 9 PTR 04 FI | DVN | N1
N446 | FILTER HEAD | DVN | N1
N447 | FILTER RESIN RETENTION | DVN | N1
N448 | FILTER HEAD | DVN | N1
N449 | 9 TEP 04 FI | DVN | N1
N450 | FILTER EFFLEUENT FEED TO 02EV | DVN | N1
N451 | DAMPER BALANCING | DVN | N1
N455 | DEMINERALISER | DVN | N1
N457 | GAUGE PRESSURE DIFFERENTIAL 02DE | DVN | N1
N458 | DEMINERALISER MIXED BED | DVN | N1
N459 | 9 TEP 05 DE | DVN | N1
N461 | ACCESS TUNNEL TO VALVE MANIFOLDS | DVN | N1
N462 | ACCESS TUNNEL TO VALVE MANIFOLDS | DVN | N1
N463 | INDICATOR FLOW RATE | DVN | N1
N464 | VALVE ISOLATION - OUTLET 07FI | DVN | N1
N465 | VALVE ISOLATION DRAIN 03DE | DVN | N1
N466 | VALVE MANIFOLD FUNCTION 9 TEP | DVN | N1
N467 | VALVE MANIFOLD FUNCTION 9 TEU | DVN | N1
N468 | VALVE MANIFOLD FUNCTION 2 RCP | DVN | N1
N469 | VALVE FOR ASSEMBLY 314VP-SA | DVN | N1
N470 | ORIFICE PLATE FOR SENSOR 007MD | DVN | N1
N471 | VALVE - VENTING 003DE | DVN | N1
N472 | VALVE ISOLATION - SED SUPPLY 01DE INLET | DVN | N1
N475 | ELEVATOR | DVN | N1
N476 | STAIRWAY | DVN | N1
N477 | STAIRWAY | DVN | N1
N478 | ELEVATOR | DVN | N1
N479 | VALVE - ISOLATION AND HOSE REEL | DVN | N1
N480 | TEP DEAERATING VALVE ROOMS | DVN | N1
N481 | TEP DEAERATING VALVE ROOMS | DVN | N1
N482 | CONTROL TUNNEL FOR DEAERATING VALVES | DVN | N1
N483 | AIR TRAP-1 TEP 447,448VZ,2 TEP449 & 450V | DVN | N1
N485 | VALVE ISOLATION RAZ SUPL ISOL ON 04BA | DVN | N1
N486 | DAMPER FIRE 143 AR N395 | DVN | N1
N487 | SOLENOID VALVE BODY | DVN | N1
N488 | VALVE OPEN/CLOSE AFTER 005PO | DVN | N1
N489 | VALVE OPEN/CLOSED AFTER 006PO | DVN | N1
N490 | CONTROL CORRIDOR FOR EVAPORATOR VALVES | DVN | N1
N491 | TEU DEAERATING VALVES | DVN | N1
N492 | NON RETURN VALVE FOR 9 TEU 810VA | DVN | N1
N494 | DETECTOR ION ACT. PIPING GALLERY | DVN | N1
N495 | DETECTOR OPT TEG TANK ROOM | DVN | N1
N496 | SWITCH LEVEL - LOW 001BA | DVN | N1
N497 | ACCESS TO ACTIVE PIPING TUNNEL | DVN | N1
N498 | VALVE MANIFOLD ROOMS | DVN | N1
N499 | NIL | DVN | N1
N501 | CURCULATION TUNNEL | DVN | N1
N502 | CURCULATION TUNNEL | DVN | N1
N504 | TES ACCESS STAIRWAY | DVN | N1
N505 | TES PLATFORM | DVN | N1
N509 | ACCESS TUNNEL DVW EQUIPMENT | DVN | N1
N510 | EVAPORATOR Nb2 HANDLING AREA | DVN | N1
N511 | MACHINERY AREA LIFT ( SEE LEVEL +15.00) | DVN | N1
N512 | RIS ROOM UNIT 1 | DVN | N1
N513 | ACCESS TUNNEL RIS ROOM UNIT 1 | DVN | N1
N514 | DVW EQUIPMENT SPACE | DVN | N1
N515 | TRANSVERSAL CIRCULATION TUNNEL UNIT 1 SIDE | DVN | N1
N521 | DAMPER FIRE | DVN | N1
N522 | RIS ROOM UNIT 2 | DVN | N1
N523 | ACCESS TUNNEL R15 ROOM UNIT 2 | DVN | N1
N524 | CLEARING SIDE UNIT 2 | DVN | N1
N525 | TRANSVERSAL CIRCULATION TUNNEL UNIT 2 SIDE | DVN | N1
N530 | PREFILTER CELL 02 FI DVW | DVN | N1
N531 | ABSOLUTE FILTER 04 FI DVW | DVN | N1
N532 | NIL | DVN | N1
N533 | PREFILTER 01 FI DVW | DVN | N1
N534 | ABSOLUTE FILTER 03 FI DVW | DVN | N1
N535 | DVW COMPRESSION TRAP | DVN | N1
N536 | ACTIVE CARBON FILTER BY-PASS DUCT DVW | DVN | N1
N537 | ACTIVE CARBON FILTER ACCESS TRAP DVW | DVN | N1
N538 | INLET FOR ACTIVE CARBON FILTER DVN | DVN | N1
N539 | OUTLET ACTIVE CARBON FILTER DVW | DVN | N1
N541 | AIR DUCT DVW | DVN | N1
N542 | MOTOR - FOR 001ZV | DVN | N1
N543 | BLOWDOWN PLENUM EBA | DVN | N1
N544 | HEATING COIL CELL | DVN | N1
N545 | ACCESS TRAP BLOWDOWN DVN | DVN | N1
N546 | BLOW OUT PLENUM | DVN | N1
N547 | COOLING COIL CELL | DVN | N1
N548 | BLOW OUT FAN 01 2V DVN | DVN | N1
N549 | BLOW OUT FAN 02 2V DVN | DVN | N1
N550 | BLOW OUT FAN 03 2V DVN | DVN | N1
N551 | DAMPER RECYCLING | DVN | N1
N552 | HIGH EFFICIENCY FILTER CELLS | DVN | N1
N553 | COOLING COILS | DVN | N1
N554 | ACCESS AIR LOCK TO EXHAUST FANS DVN | DVN | N1
N555 | EXHAUST FAN 04 ZV DVN | DVN | N1
N556 | EXHAUST FAN 05 ZV DVN | DVN | N1
N557 | EXHAUST FAN 06 ZV DVN | DVN | N1
N558 | EXHAUST FANS OUTLET TUNNEL DVN | DVN | N1
N559 | EXHAUST FANS OUTLET AIRLOCK DVN | DVN | N1
N560 | EXHAUST DAMPER BY-PASS CELL DVN | DVN | N1
N562 | EXHAUST AIR INLET PLENUM DVN | DVN | N1
N563 | CLEANING | DVN | N1
N564 | FILTRATION EQUIPMENT ACESS TRAP DVN | DVN | N1
N565 | EXHAUST AIR DUCT DVN | DVN | N1
N566 | FILTER PRE | DVN | N1
N567 | PREFILTERS 04 FA DVN | DVN | N1
N568 | ABSOLUTE FILTERS 02 FA DVN | DVN | N1
N569 | PREFILTERS 02 PF DVN | DVN | N1
N570 | DEMINERALISER CATION BED | DVN | N1
N575 | ELEVATOR | DVN | N1
N576 | STAIRWAY SIDE UNIT 1 | DVN | N1
N577 | STAIRWAY SIDE UNIT 2 | DVN | N1
N578 | ELEVATOR | DVN | N1
N585 | TANK BORIC ACID BACHING | DVN | N1
N586 | TEG STACK 02 BA | DVN | N1
N587 | TEG STACK 03 BA | DVN | N1
N590 | AIR INLET CELL DVN | DVN | N1
N591 | VALVE CONTROL TUNNEL | DVN | N1
N601 | ENTRANCE PLATFORM AREA REA | DVN | N1
N602 | SWITCH TEMPERATURE - 02RS | DVN | N1
N604 | TEP VALVES FLOOR | DVN | N1
N606 | HOIST WAY | DVN | N1
N607 | ACCESS TUNNEL FOR DVW EQUIPMENT | DVN | N1
N613 | DAMPER BALANCING | DVN | N1
N614 | DVW EQUIPMENT CLEARING | DVN | N1
N615 | DVW BLOWING EQUIPMENT ROOF ACCESS CATWALK | DVN | N1
N616 | ORIFCE FLOW MEASUREMENT | DVN | N1
N624 | DAMPER BALANCING | DVN | N1
N625 | EXTRACTION VENTILATOR HANDLING BRIDGE | DVN | N1
N630 | DVW PREFILTER 02 FI | DVN | N1
N631 | DVW ABSOLUTE FILTER 04 FI | DVN | N1
N632 | MANOMETER 001FI PRESS DIFF | DVN | N1
N633 | PREFILTER 01 FI | DVN | N1
N634 | DVW ABSOLUTE FILTER 03 FI | DVN | N1
N635 | COMPRESSOR AIR LOCK | DVN | N1
N637 | ACCESS TRAP FOR ACTIVE CARBON FILTER BY-PASS DVW | DVN | N1
N638 | INLET CELL FOR ACTIVE CARBON FILTER DVW | DVN | N1
N639 | FILTER IODINE PROVISION FOR FUTURE FLTRS | DVN | N1
N642 | VENTILATION EQUIPMENT FOR DVW | DVN | N1
N645 | AIR DUCT | DVN | N1
N651 | FAN DISCHARGE CELL | DVN | N1
N652 | HIGH EFFICIENCY FILTERS | DVN | N1
N653 | COOLING COILS | DVN | N1
N655 | FILTERS PRE | DVN | N1
N661 | EXTRACTION VENTILATORS OUTLET TRAP 01 ZV | DVN | N1
N664 | DVW FILTRATION EQUIPMENT INLET TRAP | DVN | N1
N665 | AIR DUCT | DVN | N1
N666 | ABSOLUTE FILTER 03 FA CELL DVN | DVN | N1
N667 | PREFILTER 03 PF CELL DVN | DVN | N1
N668 | ABSOLUTE FILTER 01 FA CELL DVN | DVN | N1
N669 | PREFILTER 01 PF CELL DVN | DVN | N1
N670 | FILTRATION INLET TRAP | DVN | N1
N671 | PREFILTER PT CELL DVN | DVN | N1
N672 | ABSOLUTE FILTER 01 FA CELL DVN | DVN | N1
N673 | ACTIVE CARBON FILTER CELL 01 FI | DVN | N1
N674 | VENTILATORS 07 ZV | DVN | N1
N676 | ACTIVE CARBON FILTER ACCESS TRAP 01 FI | DVN | N1
N677 | ACTIVE CARBON FILTER INLET CELL 01 FI | DVN | N1
N678 | ACTIVE CARBON FILTER OUTLET CELL 01 FI | DVN | N1
N679 | ACTIVE CARBON FILTER ACCESS TRAP 02 FI | DVN | N1
N680 | ACTIVE CARBON FILTER OUTLET CELL 02 FI | DVN | N1
N681 | ACTIVE CARBON FILTER INLET CELL 02 FI | DVN | N1
N682 | EXTRACTION VENTILATORS OUTLET TRAP 02 2V | DVN | N1
N683 | VENTILATOR CELL 02 2V | DVN | N1
N684 | ACTIVE CARBON FILTER BY-PASS CELL 02 FI | DVN | N1
N685 | BORIC ACID PREPARATION | DVN | N1
N686 | FILTRATION INLET TRAP | DVN | N1
N687 | PREFILTER 02 PF | DVN | N1
N688 | AIR DUCT | DVN | N1
N689 | ABSOLUTE FILTER 02 FA | DVN | N1
N690 | AIR INLET CELLS DVN | DVN | N1
N691 | RRI EXPANSION TANK | DVN | N1
N692 | RRI EXPANSION TANK | DVN | N1
N693 | RRI EXPANSION TANK | DVN | N1
N694 | RRI EXPANSION TANK | DVN | N1
N700 | SENSOR LEVEL MEASUREMENT OF 001 BA | DVN | N1
N701 | DAMPER BALANCING UNIT 2 | DVN | N1
N702 | DAMPER BALANCING | DVN | N1
N706 | DAMPER FIRE | DVN | N1
N715 | DAMPER BALANCING (UNIT 1) | DVN | N1
N725 | DAMPER NON RETURN | DVN | N1
N730 | INSTRUMENT JUNCTION BOX | DVN | N1
N751 | DAMPER BALANCING | DVN | N1
N771 | SWITCH HUMIDISTAT | DVN | N1
N772 | DAMPER BALANCING | DVN | N1
N773 | DAMPER BALANCING | DVN | N1
N787 | SWITCH HUMIDISTAT | DVN | N1
N900 | GAUGE FLOW RATE MEASUREMENT | DVN | N1
NA013 | DAMPER FIRE EXHAUST | DVI | I1
NA014 | FAN - SUPPLY AIR | DVI | I1
NA209 | COOLERS AND EXPANSION VALVES | DVN | N1
NA224 | ACTIVE PIPING TUNNEL | DVN | N1
NA226 | GALLERY FOR HP PIPING (CHARGING PUMPS RCV) | DVN | N1
NA229 | CHARGING PUMP RCV 03 PO | DVH | H1
NA367 | RECOMBINER TEG | DVN | N1
NA368 | DECOMBINE TEG RECOMBINER | DVN | N1
NA369 | ANALYSER TEG | DVN | N1
NA379 | HYDROGEN DETECTOR CONTROLLER UNIT | DVN | N1
NA381 | ELECTRICAL CABINETS | DVN | N1
NA409 | TES STAIRWAY | DVN | N1
NA532 | ACCESS AIRLOCK DVW | DVN | N1
NA542 | FANS DVW | DVN | N1
NA551 | OUTLET TUNNEL FOR BLOWDOWN FAN | DVN | N1
NA561 | EXHAUST PLENUM DVN | DVN | N1
NA566 | ABSOLUTE FILTERS 04 FAN DVN | DVN | N1
NA632 | ACCESS AIRLOCK DVW | DVN | N1
NB023 | DAMPER FIRE EXHAUST | DVI | I1
NB024 | MOTOR - FOR 001ZV | DVI | I1
NB224 | RIS LEAK-OFF LINE VENT ISOLATION VALVE | DVN | N1
NB226 | GALLERY FOR HP PIPING RCV CHARGING PUMPS | DVN | N1
NB229 | CHARGING PUMP 2 RCV 03 PO | DVN | N1
NB246 | POLARITY UNIT | DVN | N1
NB331 | STAUBLI AIR SUPPLY POINT | DVN | N1
NB367 | TEG RECOMBINER | DVN | N1
NB368 | TEG RECOMBINER | DVN | N1
NB369 | TEG ANALYSER | DVN | N1
NB379 | TRANSVERSAL PASSAGE WAY | DVN | N1
NB381 | ANALYSER CHEMICAL - OXYGEN | DVN | N1
NB385 | BORIC ACID STORAGE TANKS (REA) | DVN | N1
NB532 | STAUBLI AIR SUPPLY POINT | DVN | N1
NB542 | VALVE - OUTLET 014BA | DVN | N1
NB551 | STAUBLI AIR SUPPLY POINT | DVN | N1
NB561 | STAUBLI AIR SUPPLY POINT | DVN | N1
NB566 | STAUBLI AIR SUPPLY POINT | DVN | N1
NB632 | STAUBLI AIR SUPPLY POINT | DVN | N1
NC013 | RRI EXCHANGER LINE B | DVI | I1
NC014 | DVI VENTILATION | DVI | I1
NC020 | RRI PUMPS LINE A | DVI | I1
NC021 | RRI EXCHANGER LINE A | DVI | I1
NC022 | RRI PUMPS LINE B | DVI | I1
NC023 | RRI EXCHANGER LINE B | DVI | I1
NC024 | DVI VENTILATION | DVI | I1
NC205 | CONCETRATION RECIRCULATING PUMP TEU NB 2 EVAP | DVN | N1
NC209 | TES STAIRWAY | DVN | N1
NC220 | ACTIVE PIPING TUNNEL SEE LEVEL +5.00 | DVN | N1
NC245 | ELECTRICAL ROOM - SWITCH BOARDS | DVN | N1
NC247 | TERMINAL BLOCK FOR 9LNF001TR | DVN | N1
NC270 | TRANSVERSE CIRCULATING TUNNEL | DVN | N1
NC331 | ELECTRO-PNEUMATIC CONVERTER | DVN | N1
NC370 | ELEVATOR | DVN | N1
NC421 | NON-ACTIVE PIPING TUNNEL | DVN | N1
NC430 | FILTER LETDOWN FLOW | DVN | N2
NC431 | FILTER LETDOWN FLOW | DVN | N2
NC432 | DEMINERALIZER - MIXED BED | DVN | N2
NC433 | DEMINERALIZER - MIXED BED | DVN | N2
NC434 | DEMINERALIZER - CATION BED | DVN | N2
NC435 | FILTER - RCP PUMP SEAL WATER RETURN | DVN | N2
NC436 | FILTER - PTR 001 AND 002PO | DVN | N2
NC437 | DEMINERALISER PTR FLOW | DVN | N2
NC438 | FILTER - PTR 001 AND 002PO | DVN | N2
NC439 | 9 PTR 03 FI | DVN | N2
NC441 | 1 APG 01 FI | DVN | N2
NC442 | 1 APG 02 FI | DVN | N2
NC443 | 1 APG 03 FI | DVN | N2
NC444 | 1 RCV 02 FI | DVN | N2
NC445 | 1 RCV 07 FI | DVN | N2
NC451 | 1 APG 01 DE | DVN | N2
NC452 | 1 APG 03 DE | DVN | N2
NC453 | 1 APG 02 DE | DVN | N2
NC454 | 1 APG 04 DE | DVN | N2
NC455 | 9 TEP 01 DE | DVN | N2
NC456 | 9 TEP 03 DE | DVN | N2
NC457 | 9 TEP 02 DE | DVN | N2
NC458 | 9 TEP 04 DE | DVN | N2
NC460 | VALVE MANIFOLD FUNCTION RCV | DVN | N1
NC463 | VALVE MANIFOLD FUNCTION 1 APG | DVN | N1
NC464 | VALVE MANIFOLD FUNCTION 2 ACV | DVN | N1
NC465 | VALVE ROOM | DVN | N1
NC469 | VALVE MANIFOLD FUNCTION 1 PTR | DVN | N1
NC470 | VALVE ROOM | DVN | N1
NC471 | VALVE CONTROL TUNNEL | DVN | N1
NC472 | VALVE CONTROL TUNNEL | DVN | N1
NC487 | TEU DEAERATING VALVES | DVN | N1
NC488 | TEP DEAERATING VALVES | DVN | N1
NC489 | TEP DEAERATING VALVES | DVN | N1
NC570 | FILTER AND DEMINERALIZATION BAY | DVN | N1
ND020 | SWITCH TEMP HI | DVI | I1
ND021 | DAMPER FIRE SUPPLY | DVI | I1
ND022 | DAMPER FIRE EXHAUST | DVI | I1
ND023 | SWITCH TEMP HI | DVI | I1
ND033 | LOUD SPEAKER | DVN | N1
ND236 | CONTROL CORRIDOR FOR TES DRUMMING | DVN | N1
ND245 | ELECTRICAL ROOM -POWER | DVN | N1
ND246 | ELECTRICAL ROOM -RELAYING | DVN | N1
ND247 | ELECTRICAL ROOM -INVERTING | DVN | N1
ND266 | DRUM WASHING | DVN | N1
ND270 | TRANSVERSE CIRCULATING TUNNEL | DVN | N1
ND331 | PASSAGE WAY AND INSTRUMENTATION TUNNEL | DVN | N1
ND370 | ELEVATOR | DVN | N1
ND409 | TES STAIRWAY | DVN | N1
ND421 | NON-ACTIVE PIPING TUNNEL | DVN | N1
ND430 | 2 RCV 01 FI | DVN | N2
ND431 | 2 RCV 06 FI | DVN | N2
ND432 | 2 RCV 01 DE | DVN | N2
ND433 | 2 RCV 02 DE | DVN | N2
ND434 | 2 RCV 03 DE | DVN | N2
ND435 | 2 RCV 05 FI | DVN | N2
ND436 | 2 PTR 02 FI | DVN | N2
ND437 | 2 PTR 01 FI | DVN | N2
ND438 | 2 PTR 01 DE | DVN | N2
ND439 | 9 TEP 07 DE | DVN | N2
ND441 | 2 APG 01 FI | DVN | N2
ND442 | 2 APG 02 FI | DVN | N2
ND443 | 2 APG 03 FI | DVN | N2
ND444 | 9 TEU 05 FI | DVN | N2
ND445 | 9 TEU 01 FI | DVN | N2
ND446 | 2 RCV 02 FI | DVN | N2
ND447 | 2 RCV 07 FI | DVN | N2
ND448 | 9 TEP 06 FI | DVN | N2
ND450 | KRT DETECTOR (9 TEU 006 FI) | DVN | N2
ND451 | 2 APG 01 DE | DVN | N2
ND452 | 2 APG 03 DE | DVN | N2
ND453 | 2 APG 02 DE | DVN | N2
ND454 | 2 APG 04 DE | DVN | N2
ND455 | 9 TEU 01 DE | DVN | N2
ND456 | 9 TEU 02 FI | DVN | N2
ND457 | 9 TEP 05 FI | DVN | N2
ND458 | 9 TEP 06 DE | DVN | N2
ND460 | VALVE MANIFOLD FUNCTION RCV | DVN | N1
ND463 | VALVE ROOM | DVN | N1
ND464 | VALVE MANIFOLD FUNCTION 1 RCV | DVN | N1
ND465 | VALVE MANIFOLD FUNCTION 9 TEP | DVN | N1
ND469 | VALVE MANIFOLD FUNCTION 9 TEP | DVN | N1
ND470 | VALVE MANIFOLD FUNCTION 2 PTR | DVN | N1
ND471 | VALVE CONTROL TUNNEL | DVN | N1
ND472 | VALVE CONTROL TUNNEL | DVN | N1
ND487 | TEU EVAPORATOR VALVE ROOM | DVN | N1
ND488 | TEU EVAPORATOR VALVE ROOM | DVN | N1
ND489 | TEU EVAPORATOR VALVE ROOM | DVN | N1
ND521 | MACHINERY AREA LIFT ( SEE LEVEL +15.00) | DVN | N1
ND570 | FILTER - SMPLNG SKID 036CQ - PIS FLTER 1 | DVN | N1
NE034 | TES COMPACTING PRESS | DVN | N1
NE442 | NIL | DVN | N1
NE443 | NIL | DVN | N1
NE444 | NIL | DVN | N1
NE445 | NIL | DVN | N1
NE446 | 9 TEP 01 FI | DVN | N2
NE447 | 9 TEP 03 FI | DVN | N2
NE448 | 9 TEP 02 FI | DVN | N2
NE450 | 9 TEP 06 FI | DVN | N2
NF033 | METAL DRUM STORAGE TES | DVN | N1
NF034 | LOW ACTIVING WASTE DRUMMING TES | DVN | N1
NF205 | PUSH BUTTON RESET DVN 041AE | DVN | N1
NF236 | TES CCTV PLUG FOR SYSTEM CNTRLER1 AREA 1 | DVN | N1
NF266 | TES CCTV LIGHT FOR CAMERA CT1- AREA 1 | DVN | N1
P200 | SEC PUMPHOUSE | DWS | X1
P250 | SEC PUMPHOUSE | DWS | X1
Q100 | LLW CASK STORAGE BUILDING | DWL | Q1
W017 | ACCELEROMETER FORCE BALANCE FBA3 | DVW | W1
W032 | 01RRI LINE NUMBER 963TY | DVW | W1
W035 | VALVE AIR ISOLATION TO PERSONNEL AIRLOCK | DVW | W1
W036 | GAUGE FOR BACKUP AIR SUPPLY TANK FOR ASG | DVW | W1
W037 | PUMP - SUBMERSIBLE PERIFERAL AREA | DVW | W1
W038 | PENDULUM (P1-A) | DVW | W1
W055 | PENDULUM (P2-A) | DVK | K3
W068 | DETECTOR ION RP STORAGE AREA | DVW | W1
W071 | VALVE ISOLN OF 9 TEU SUPPLY TO KER TANKS | DVK | K3
W072 | NIL | DVK | K2
W073 | TANK ADDITIONAL STORAGE | DVK | K1
W074 | MOTOR - FOR 014PO | DVK | K3
W076 | 02RRI LINE NUMBER 963TY | DVW | W1
W077 | GAUGE - PRESSURE LOCAL,DISCHARGE 025PO | DVW | W1
W079 | TANK NUCLEAR LIQUID WASTE STORAGE | DVK | K3
W080 | INDICATOR LEVEL 001BA | DVK | K2
W117 | PIPES DVW VENTILATION | DVW | W1
W128 | RRI PIPING TO DVG AND DVG VENTILATION: DUCTS | DVW | W1
W130 | DVG VENTILATION DUCTS AND ASG PIPES | DVW | W1
W131 | ASG PIPES | DVW | W1
W157 | PIPES DVW VENTILATION | DVK | K2
W168 | RRI PIPING TO DVG AND DVG VENTILATION: DUCTS | DVW | W1
W170 | DVG VENTILATION DUCTS AND ASG PIPES | DVW | W1
W171 | ASG PIPES | DVK | K1
W172 | TEU KER PIPES | DVW | W1
W177 | ASG PIPES | DVW | W1
W178 | ASG PIPES | DVW | W1
W211 | REFUELING WATER STORAGE TANK (PTR) | DVW | X1
W213 | RRI PIPING-PTR PUMP-SAT SAR RESEVOIR | DVW | W1
W215 | COLD PIPING PENETRATIONS | DVW | W1
W216 | ACCESS AREA | DVW | W1
W217 | ACTIVE PENETRATION AREA | DVW | W1
W218 | DVN VENTILATION | DVW | W1
W221 | VALVE - SHUT OFF TO STEAM TRAP 003PU | DVW | W1
W225 | CONTROL ROD DRIVE MECHANISM ELECTRICAL PENETRATION | DVW | W1
W226 | GAS PENETRATION CONTAINMENT ACTIVITY | DVW | W1
W227 | RGX RGL MOTOR GENERATOR SETS | DVG | G1
W228 | RGX RGL ROD DRIVE MECHANISM | DVG | G1
W229 | ASG MOTOR PUMPS | DVG | G1
W230 | HANDLING TUNNEL | DVW | W1
W231 | ASG REGULATION VALVES | DVW | W1
W232 | ASG TANK | DVW | W1
W233 | AIRLOCK | EPP | W1
W234 | AIRLOCK | EPP | W1
W236 | CABINET RLYNG FOR DOOR CTRL, ALMS & KIT | DVW | W1
W237 | ASG TURBO | DVW | W1
W238 | INTAKE WEATHER LOUVRE | DVW | W1
W243 | SWITCH PRESSURE 005PO NO WATER FLOW | DVW | W1
W247 | DETECTOR HEAT INT SAFE BAT RM TRN B | DVW | W1
W251 | REFUELING WATER STORAGE TANK (PTR) | DVW | X1
W253 | RRI PIPING-PTR PUMP-SAT SAR RESEVOIR | DVW | W1
W255 | COLD PIPING PENETRATIONS | DVW | W1
W256 | ACCESS AREA | DVW | W1
W257 | ACTIVE PENETRATION AREA | DVW | W1
W258 | DVN VENTILATION | DVW | W1
W260 | PIPEWORK / NUC COMPONENT COOLING SYS | DVW | W1
W265 | CONTROL ROD DRIVE MECHANISM ELECTRICAL PENETRATION | DVW | W1
W266 | GAS PENETRATION CONTAINMENT ACTIVITY | DVW | W1
W267 | RGX RGL MOTOR GENERATOR SETS | DVG | G1
W268 | RGX RGL ROD DRIVE MECHANISM | DVG | G1
W269 | ASG MOTOR PUMPS | DVG | G1
W270 | HANDLING TUNNEL | DVW | W1
W271 | ASG REGULATION VALVES | DVW | W1
W272 | ASG TANK | DVW | W1
W273 | AIRLOCK | EPP | W1
W274 | AIRLOCK | EPP | W1
W277 | ASG TURBO | DVW | W1
W278 | INTAKE WEATHER LOUVRE | DVW | W1
W299 | LOC PRESS MEAS AIR LOCK & PENETRATION SY | DVW | W1
W301 | CORRIDOR | DVW | W1
W302 | BATTERY LINE A | DVW | W1
W303 | BATTERY LINE A | DVW | W1
W304 | BATTERY LINE A | DVW | W1
W305 | BATTERY LINE B | DVW | W1
W307 | BATTERY LINE B | DVW | W1
W308 | BATTERY LINE B | DVW | W1
W309 | VALVE ISOLATION TO TURBINE BAT ROOM309 | DVW | W1
W310 | CORRIDOR | DVW | W1
W311 | VALVE ISOL TO TURBINE BATTERY ROOM 311 | DVW | W1
W313 | REN AREA | DVW | W1
W314 | VALVE AIR SUPPLY POINT (STAUBLI) | DVW | W1
W315 | APG ROOM | DVW | W1
W316 | ACCESS TO APG AREA | DVW | W1
W317 | ELECTRICAL PENTATION LINE B PENETRATION | DVW | W1
W325 | DAMPER FIRE (COMMON TO TRAIN AANDB) | DVW | W1
W326 | MV-LV ELECTRICAL PENETRATION AREA LINE B | DVW | W1
W330 | MV-LV ELECTRICAL PENETRATION AREA LINE A | DVW | W1
W341 | CORRIDOR | DVW | W1
W342 | BATTERY LINE A | DVW | W1
W343 | BATTERY LINE A | DVW | W1
W344 | BATTERY LINE A | DVW | W1
W345 | BATTERY LINE B | DVW | W1
W347 | BATTERY LINE B | DVW | W1
W348 | BATTERY LINE B | DVW | W1
W350 | CORRIDOR | DVW | W1
W353 | REN AREA | DVW | W1
W355 | APG ROOM | DVW | W1
W356 | ACCESS TO APG AREA | DVW | W1
W357 | ELECTRICAL PENTATION LINE B PENETRATION | DVW | W1
W360 | ELECTRICAL PENETRATION IN CORE RIC | DVW | W1
W365 | MV-LV ELECTRICAL PENETRATION AREA LINE B | DVW | W1
W370 | MV-LV ELECTRICAL PENETRATION AREA LINE A | DVW | W1
W401 | DIRECT CURRENT DISTRIBUTION LINE A | DVW | W1
W403 | DIRECT CURRENT DISTRIBUTION LINE B | DVW | W1
W410 | CHANGEOVER SWITCH FOR PANEL LBG002RD | DVW | W1
W413 | GAUGE SUPPLY PRESS DEG CHILLED WTR PROD | DVW | W1
W415 | MOTOR - FOR 005PO | DVW | W1
W416 | MANOMETER 001 & 002 FI PRESS DIF | DVW | W1
W417 | FLOW METER LOCAL | DVW | W1
W418 | AIRLOCK | DVW | W1
W425 | VENTILATION LINE B | DVW | W1
W431 | LV SWITCHBOARD LINE A | DVW | W1
W441 | DIRECT CURRENT DISTRIBUTION LINE A | DVW | W1
W443 | DIRECT CURRENT DISTRIBUTION LINE B | DVW | W1
W446 | CIRCUIT BRK 2KRG156AR LTG SUPPLY | DVW | W1
W451 | VENT SMOKE W441 | DVW | W1
W453 | VALVE AIR ISOLATION TO ROOM W453 | DVW | W1
W455 | SWITCH PRESS CHLD WTR FLOW IN EVAP 101EV | DVW | W1
W456 | MANOMETER 001 & 002 FI PRESS DIF | DVW | W1
W457 | ISOLATION VALVE - PENETRATION 407 | DVW | W1
W458 | AIRLOCK | DVW | W1
W465 | SWITCHBOARD - 380V AC ESSENTIAL | DVW | W1
W466 | LV SWITCHBOARD LINE A | DVW | W1
W471 | INDR FLOW SIGHT GLASS BEFORE 010VS | DVW | W1
W501 | REFRIGERATING ROOM | DVW | W1
W502 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP IV AND II | DVW | W1
W503 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP III AND I | DVW | W1
W504 | VENTILATION | DVW | W1
W505 | CORRRIDOR | DVW | W1
W506 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP IV AND II | DVW | W1
W507 | PENETRATIONS AREA | DVW | W1
W508 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP III AND I | DVW | W1
W513 | EBA VALVES | DVW | W1
W514 | DAMPER NON RETURN | DVW | W1
W515 | DEG. MOTOR PUMPS AND COMPRESSOR SETS | DVW | W1
W516 | NIL | DVW | W1
W517 | DAMPER BALANCING | DVW | W1
W530 | STEAM GENERATOR LOOP 2 WATER SUPPLY PIPING | DVW | V1
W531 | STEAM GENERATOR LOOP 1 WATER SUPPLY PIPING | DVW | V1
W532 | STEAM GENERATOR LOOP 3 WATER SUPPLY PIPING | DVW | V1
W541 | VENTILATION LINE A AND LINE B | DVW | W1
W542 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP IV AND II | DVW | W1
W543 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP III AND I | DVW | W1
W544 | VENTILATION | DVW | W1
W546 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP IV AND II | DVW | W1
W547 | PENETRATIONS AREA | DVW | W1
W548 | VITAL 220 V PRODUCTION AND DISTRIBUTION GROUP III AND I | DVW | W1
W551 | VALVE AIR SUPPLY POINT (STAUBLI) | DVW | W1
W553 | EBA VALVES | DVW | W1
W555 | DEG. MOTOR PUMPS AND COMPRESSOR SETS | DVW | W1
W556 | DAMPER BALANCING | DVW | W1
W557 | DAMPER BALANCING | DVW | W1
W570 | STEAM GENERATOR LOOP 2 WATER SUPPLY PIPING | DVW | V1
W571 | STEAM GENERATOR LOOP 1 WATER SUPPLY PIPING | DVW | V1
W572 | STEAM GENERATOR LOOP 3 WATER SUPPLY PIPING | DVW | V1
W601 | TELEPHONE ROOM | DVW | W1
W602 | PROTECTION INSTRUMENTION GROUP IV | DVW | W1
W603 | PROTECTION INSTRUMENTION GROUP III | DVW | W1
W604 | CABLING | DVW | W1
W605 | CORRIDOR | DVW | W1
W606 | NIL | DVW | W1
W607 | PROTECTION INSTRUMENTATION GROUP II | DVW | W1
W608 | PUSH BUTTON | DVW | W1
W609 | PROTECTION INSTURMENTATION GROUP I | DVW | W1
W630 | STEAM VALVE LOOP 2 (VVP) | DVW | V1
W631 | STEAM VALVE LOOP 1 (VVP) | DVW | V1
W632 | STEAM VALVE LOOP 3 (VVP) | DVW | V1
W633 | STEAM SAFETY VALVE LOOP 2 ( VVP-GCT) | DVW | V1
W634 | STEAM SAFETY VALVE LOOP 1 ( VVP-GCT) | DVW | V1
W635 | STEAM SAFETY VALVE LOOP 3 ( VVP-GCT) | DVW | V1
W636 | STEAM PIPES LOOP 2 | DVW | V1
W637 | STEAM PIPES LOOP 1 | DVW | V1
W638 | STEAM PIPES LOOP 3 | DVW | V1
W641 | BATTERY TO 402CC | DVW | W1
W642 | PROTECTION INSTRUMENTION GROUP IV | DVW | W1
W643 | PROTECTION INSTRUMENTION GROUP III | DVW | W1
W644 | CABLING | DVW | W1
W645 | CORRIDOR | DVW | W1
W647 | PROTECTION INSTRUMENTATION GROUP II | DVW | W1
W648 | PUSH BUTTON | DVW | W1
W649 | PROTECTION INSTURMENTATION GROUP I | DVW | W1
W652 | AIR EXHAUST | DVW | W1
W653 | AIR EXHAUST | DVW | W1
W670 | STEAM VALVE LOOP 2 (VVP) | DVW | V1
W671 | STEAM VALVE LOOP 1 (VVP) | DVW | V1
W672 | STEAM VALVE LOOP 3 (VVP) | DVW | V1
W673 | STEAM SAFETY VALVE LOOP 2 ( VVP-GCT) | DVW | V1
W674 | STEAM SAFETY VALVE LOOP 1 ( VVP-GCT) | DVW | V1
W675 | STEAM SAFETY VALVE LOOP 3 ( VVP-GCT) | DVW | V1
W676 | STEAM PIPES LOOP 2 | DVW | V1
W677 | STEAM PIPES LOOP 1 | DVW | V1
W678 | STEAM PIPES LOOP 3 | DVW | V1
W701 | CHANGING ROOM | DVW | W1
W702 | CORRIDOR | DVW | W1
W703 | HEATER ELECTRIC | DVW | W1
W704 | CONDITIONING ROOM | DVW | W1
W709 | DETECTOR ION 1RN004AR | DVW | W1
W730 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W731 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W732 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W733 | STEAM CUBICLE (VVP) | DVW | W1
W734 | STEAM CUBICLE (VVP) | DVW | W1
W735 | STEAM CUBICLE (VVP) | DVW | W1
W736 | ACCUMULATOR FOR GCT132VV | DVW | W1
W737 | ACCUMULATOR FOR GCT131VV | DVW | W1
W738 | ACCUMULATOR FOR GCT133VV | DVW | W1
W741 | PUSH BUTTON FOR TEST LAMP 005RS | DVW | W1
W744 | CONDITIONING ROOM | DVW | W1
W747 | LOCAL CABINETS | DVW | W1
W770 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W771 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W772 | STEAM SUPPLY VALVES FOR ASG TURBINE | DVW | W1
W773 | STEAM CUBICLE (VVP) | DVW | W1
W774 | STEAM CUBICLE (VVP) | DVW | W1
W775 | STEAM CUBICLE (VVP) | DVW | W1
W776 | ACCUMULATOR FOR GCT132VV | DVW | W1
W777 | ACCUMULATOR FOR GCT131VV | DVW | W1
W778 | ACCUMULATOR FOR GCT133VV | DVW | W1
W812 | AIR INTAKE | DVW | W1
W813 | AIR INTAKE | DVW | W1
W814 | AIR EXHAUST | DVW | W1
| SEC Plant, SEC Galleries, other corridors, tunnels, trenches SEVERE MARINE ENVIROMENTAL CONDITIONS |  | X2

## COMMODITY GROUP (hidden)
| COMMODITIES | Component Count
16 | Components_not_environmentally_qualified - Motor | 666
17 | Components_not_environmentally_qualified - Sensor | 1648
18 | Components_not_environmentally_qualified - Electronics | 14502
19 | Components_not_environmentally_qualified - Terminal Junction Box | 4515
20 | Components_not_environmentally_qualified - Relay ProtectionRelay | 4288
21 | Components_not_environmentally_qualified - Circuit Breaker Fuses | 4332
22 | Components_not_environmentally_qualified - MOVactuator | 757
23 | Components_not_environmentally_qualified - Transmitter | 1948
24 | Components_not_environmentally_qualified - Switches | 7466
25 | Components_not_environmentally_qualified - Panel Electrical Enclosures | 2904
26 | Components_not_environmentally_qualified - Battery Charger Inverters UPS | 96
51 | Components_not_environmentally_qualified - Cable Connection | 519
84 | Components_not_environmentally_qualified - Transformer | 176
85 | Components_not_environmentally_qualified - HighVoltageInsulator | 589
324 | Components_not_environmentally_qualified - Cable | 30089
334 | Components_not_environmentally_qualified - Electrical Penetration | 120
352 | Components_not_environmentally_qualified - Battery | 65
547 | Components_not_environmentally_qualified - Any | 18
699 | Components_not_environmentally_qualified - MOVactuator - Pneumatic Actuator / Booster | 1248
700 | Components_not_environmentally_qualified - MOVactuator - Electro Mechanical Actuator | 395
721 | Components_not_environmentally_qualified - Cable - Medium Voltage | 163
722 | Components_environmentally_qualified - MOVactuator | 106
723 | Components_environmentally_qualified - Electronics | 82
724 | Components_environmentally_qualified - Switches | 190
725 | Components_environmentally_qualified - Transmitter | 316
726 | Components_environmentally_qualified - Motor | 4
727 | Components_environmentally_qualified - MOVactuator - Electro Mechanical Actuator | 34
728 | Components_environmentally_qualified - Electrical Penetration | 40
729 | Components_environmentally_qualified - MOVactuator - Pneumatic Actuator / Booster | 6
730 | Components_environmentally_qualified - Cable | 754